2026-02 | 2026-02-27 | All Water System ROC General | ROC | STETBR, Tower Level Lo Alarm, Activated D1 STW2/3, Placed Wells 2/3 in man/on to help fill STETBR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043828 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | MKRSEM- Called Metro spoke with Paul to start 2 pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046874 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SHTP- Turbidity trends still abnormally high. Notified Benson S. Will attend site .Created CMU5 W11695345 NMTKKC- Ammonia P1 failed to start P2 started in its place. Reset alarm #CMU5 | FLAG | stage2_low_confidence | 0.012606 | ML: above threshold (no LLM available) — 0.013 | failed [equipment_failure]; alarm [control_system] | 0.012606 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | KSETDP - Outlet free chlorine Low alarm. Jackie S called yesterday from site and requested disregard chlorine residual alarms until Monday. Site offline and isolated until Monday. 11:50 KSETDP - verified with Stephen B , Outlet free chlorine residual low, slowly declining, ok to disregard. Not a distribution water residual. # Consult | FLAG | stage2_low_confidence | 0.013413 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.013413 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SHETCS- Post injection total Cl2 lo alarm came in. Checked trends residual lower than normal and is almost the same as inlet analyzer. Hypo pump 2 running and speed increasing. Continued to monitor for 10 mins no change. Rotated to hypo pump 1. Residual recovered after 3 mins alarms cleared . Placed P2 in man/off and emailed West Water team. | FLAG | stage2_low_confidence | 0.019801 | ML: above threshold (no LLM available) — 0.02 | alarm [control_system]; alarms [control_system] | 0.019801 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW5- Tim H called and requested a call if the low effluent switch alarm comes in at 0.4mg/L. Well currently man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069406 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | KSTP - Carbon Dioxide HiHi alarm. Stephen B called back and directed to activate the KSTP duty 1 high lift pump in manual. Activated high lift pump 4 in manual. Stephen B will attend site to inspect the CO2 system. Created CMU5#W11691423 #CMU5 | FLAG | stage2_low_confidence | 0.0091817 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0091817 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | ARPS- Benesh from OCWA called. Rotating pumps from pump 6 to pump 5. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050432 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | MAPS PD7 Placed P1/3 in man/off VNPS PD7- Placed P2/3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040437 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | KSTKWP- Tower hi level alarm came in notified Patrick F. Patrick F will make adjustments | FLAG | stage2_low_confidence | 0.0077711 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077711 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | MKRSEM - Request TO (Brent) to run 2 pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044736 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | STRS48- JOe M on site to test Cl2 leak alarms | FLAG | stage2_low_confidence | 0.0088853 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.0088853 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | GWTP, Parth P is on site at the low lift building, preforming annual calibrations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065904 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | NMETIB- Activated Duty 1 to offset with NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045413 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -5C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | GWTP - High lift header free chlorine hit 2.02mg/L. As per shift report notified Stephen B, no issues or change in Keswick or Sutton line free readings upstream. Okay to disregard for the night Consult | FLAG | stage2_low_confidence | 0.0074792 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074792 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AUPSWS, Jerry Z on site, testing temp/flood and running generator | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | MAPS PD7, Placed pumps 1/2/3 to man/off VNPS PD7, Placed pumps 2/3 to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035851 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | NMVCBA- Placed valve back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056242 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | BVPS - Activate duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040641 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Ethan U signing in Weather -4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | KSTP - CO2 Adjusted pH level LoLo alarm came in. Value turned normal on its own and alarm cleared. Will monitor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064847 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Carter D Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | NMETHW/NMETYS - Evgeny rebooting heartbeat alarm QVETQS/QVW12/QVW34/HLW/HLW2 - Kingsley M rebooting OIT for sites | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0056781 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NMW136, Eric S is leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041977 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | Carter D signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SHTP, Treated Water Turbidity Fault, Plant is shutting off/Tower is Draining, notified Cole W and West team before their morning meeting started, they will have someone look into it | FLAG | stage2_low_confidence | 0.017181 | ML: above threshold (no LLM available) — 0.017 | fault [equipment_failure] | 0.017181 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NMETIB - Deactivated duty 1 to maintain level offset from NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049338 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | VNP7 - Place pumps back man/off MAP7 - Place pump 2 & 3 auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040741 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | NMW15- Combined Cl2 lo alarm came in. Well in man/off no water directed to users | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058312 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NMVCBA- Placed valve in man/open at 40L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044166 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | NMETIB- Activated D1 at 49% to offset from NMETHW as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00502 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NMW15 - Dan B and Kyle R finished on site. Cleared alarms and placed the well in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0064893 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | KSTP - Jerry Z onsite, disregard any alarms coming in while contractors work on intake | FLAG | stage2_low_confidence | 0.0091699 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0091699 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | BVPS - Activated duty 1. MARS - low level alarm. BVPS activation will help to increase MARS level. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0044238 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from MAPS to VNPS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006037 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | SECC, Yash S on site, replacing OITs and working on system panel Wrong Book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044627 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | VNPS- Placed PD7 pump to man/off MAPS- Placed PD7 pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041236 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NMETIB- Activated D1 to offset from NMETHW as per shift report AURSBS- Cl2 iso valve failed to open alarm came in. Chemical system not being called for and alarm reset. AUW14- Joe D req wells to be running in manual for sampling later this morning. D1 just deactivated. NMTKBS- Activated D1. AUETOH- Activated D1 | FLAG | stage2_low_confidence | 0.0253 | ML: above threshold (no LLM available) — 0.025 | failed [equipment_failure]; alarm [control_system]; valve failed [infrastructure] | 0.0253 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | MKETFA - Toronto Water (Zoran) called and informed that they will be going back to normal operations | FLAG | stage2_low_confidence | 0.0076211 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076211 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | BLETNL, Phil D is on site, working on the analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057137 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | YWS + NYWS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038034 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | HLSSBS- Terry C and Bill V on site to work on P3 NMSSBP- Mech screen 1 overtorque alarm came in. Notified Kevin S closed gate 2 as 1 was still available. Will try to reset alarm and will escalate if alarm cannot be reset **WRONG BOOK** | FLAG | stage2_low_confidence | 0.0077959 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077959 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | ARPS- Peter from Peel called to notify ROC that they will be transferring from P7 to P5 STW12/3- Placed well 2/3 in man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055775 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AURSBS- Activated D1 HLETYS- Activated D1 as per Stephen B. Will be heading to HLW2 to trouble shoot ammonia pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051375 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | Ethan U signing in Weather: -2c | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003463 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | ARPS- Peter from OCWA called to notify that they are rotating pumps, from P5 to P6. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052414 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | MARS, Tim H on site, working on pump 4 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004121 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | STETBR - Tower low level alarm, Man/started STW12 pump 2 and STW3 to help with fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061663 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW5 - Jake M and Benson S on site to re-vamp the chlorination system. May see associated alarms. | FLAG | stage2_low_confidence | 0.011394 | ML: above threshold (no LLM available) — 0.011 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.011394 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | QVW12 - Donald M and Will M on site to complete maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045521 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | GWTP, Jack P on site with CMS, they are replacing a valve from the UV channel, directed to disregard Turbidity fault alarms at this current time, Plant is off at this time | FLAG | stage2_low_confidence | 0.021132 | ML: above threshold (no LLM available) — 0.021 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.021132 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | MTW12, Joe M/Travis W on site, Chemical system/inspection maint/silicate system inspection/Cl2 analyzer cleaning and injection cleaning and hi lo temp alarm are the alarms they will be working on | FLAG | stage2_low_confidence | 0.0093811 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0093811 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW2, John D on site, pulling cables 16:03, John D leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026771 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | GWTP, ZW6 Shutdown//BP Pump 1 flow lolo/Not available alarm, notified Dan Z, she will investigate consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0042743 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | Angelica Chepiga signing in,weather -7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NMW15- Placed well man/on for Dan B MAPS PD7- Chris I done on site P4 OOS KSTKWP- Tower level hihi alarm came in. Patrikc F still making adjustments to help KSETDP fill AUETFC- Kyle C on site STETTL- Lane from town of Stouffville is flushing in system | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW5, Kyle R on site, replacing generator battery | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004308 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NMW136 - Influent free chlorine hi and hihi alarm. Checked site, well recently activated. Trending shows a spike of the influent free chlorine reading which returned to normal range within two reading intervals. Reset alarms. | FLAG | stage2_low_confidence | 0.011442 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011442 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NMETHW - Activated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041172 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | HLETYS, Eric S on site, working on Chemical Transfusers on the tanks | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061982 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | MTW3 - Jack P & Jackie S onsite working on chlorine system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047811 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | Adam Button signing in -3C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004176 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NMW136 - Alex B finished and leaving site. NMW15 - Kyle R called and requested the pump be shut down so he and Dan B can complete some additional maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053166 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two MAPS pumps to one VNPS and one MAPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.007042 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | SHTP- Filter 3 Turbidity Hi Alarm. Backwash just completed. Disregard as per SCADA Report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0061155 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | MKPSSA - Combined chlorine lolo alarm. Station is currently offline as the Linear team has completed an isolation and the pipe the analyzer pulls from is currently empty. MKRSEM - Low level alarm. Called Toronto Water (Paul) and requested they activate two pumps to push flow to MKRSEM. | FLAG | stage2_low_confidence | 0.013928 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system] | 0.013928 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | MKRSEM- Reservoir hi level alarm came in. Called Metro spoke with Paul to stop pumps | FLAG | stage2_low_confidence | 0.0078545 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0078545 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | NMW12- Treated total/ Combined Cl2 lo alarm came in Well not active no water directed to users. Will continue to monitor 4:03-NMW12- Alarms cleared as residuals recovered. Wells were not called for while alarms were outstanding | FLAG | stage2_low_confidence | 0.00773 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.00773 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | VNRSKS - Swapped supply pump to one MAPS pump and one VNPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065472 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | HLETYS- Stephen B called and requested to deactivate duty at 55% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004915 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NBW3- Influent free CL2 lolo alarm came in interlocking well on start up. Well was running in manual. Notified Jordan B directed to clear alarms and restart well. Rotated hypo pump duty and restarted wells after clearing alarms | FLAG | stage2_low_confidence | 0.011242 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011242 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | KSSP, Phil from AB is on site wrong book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037971 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | AUW57 - Joe D finished on site, directed well 5 pump back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046813 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | MAP8 - Suct. header tot/free resid OOR. Analyzer isolated. Confirmed with Jacob M no flow to site and will be OOS/isolated for a few weeks. Disregard MAPS - Dwayne L took offline, until York peel feeder main returns | FLAG | stage2_low_confidence | 0.015027 | ML: above threshold (no LLM available) — 0.015 | oos [equipment_failure] | 0.015027 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | MTW12- Silicate P1/2 OOS. Notified Phil D will investigate on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SUETDR - Jackie S on site. Building Flood Alarm cleared. Jackie S leaving site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | KSETDP- Rick L on site for Cl2 analyzer commissioning | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043766 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | NMW12 - Eric S finished onsite, Replaced silicate pump 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047515 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | VNPS PD7- Placed P3 in man/off MAPS PD7 - Placed P3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040267 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | YWS+NYWS normal NMVCBA- Changed flow set point from 40l/s to 30L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040382 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SUETDR - Building flood alarm. Notifies Jackie S. She will attend site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | QVW34, Eric S on site, working on Total Cl2 analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043513 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | YWS + NYWS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004717 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | AUETFC - Deactivated duty 1 for tower sampling as per Joe D. STETBR - Tower level low alarm. Activated STW1 and STW3 in manual mode as per the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059357 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AURSBS, Yash S is finished with the network switch | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060871 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | VNPS PD7, Placed pump 2/3 man/off MAPS PD7, Placed 1/2/3 back to auto AUW57, Placed well 5 back to auto as per Joe D NMVCBA, Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.002481 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | QVW34 - Treated total chlorine Hi alarm, adjusted chlorinator 2 from 74 to 71%. Well 3 interlocked on Combine chlorine HiHi alarm shortly after. Well 3 pump was running in schedule mode. Notified William M. He will attend site . | FLAG | stage2_low_confidence | 0.011299 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011299 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | MKRSEM - Stephen B was able to clear Building smoke alarm. Leaving site. | FLAG | stage2_low_confidence | 0.014039 | ML: above threshold (no LLM available) — 0.014 | smoke [equipment_failure]; alarm [control_system] | 0.014039 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | TMC269- Pressure lolo alarm came in. Quick dip in trends and recovered. Cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005743 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | AUETFC- Kyle C done on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051406 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | HLW1 - Combine chlorine Low alarm, quick dip in trends. Value recovered in 5 minutes. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061729 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | Connor Smith signing in -8C cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00423 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | MAP8 - PD8 P3 VFD fault, VFD not ready, informed Jacob M. Will look into it with Tim H NMW15 - Yash S working on OIT | FLAG | stage2_low_confidence | 0.0084449 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0084449 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | NMETIB- Activated D1 to offset from NMETHW as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048489 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | MKMCLA- Comm Fail. Alarm cleared after about 45 minutes. Gap in trends. Will inform PCS and Linear. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | MARS - Called Toronto water( Mehdi) and requested to increase the flow. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066906 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | ARPS - Peter D informed they are doing a pump switch. Stopping pump 7 and putting pump 5 in duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058548 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | MAP7 - Place pump 1 & 2 man/off VNP7 - Place pump 3 auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040124 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two VNPS pumps to one VNPS pump and one MAPS pump to reduce the demand on RHRSTR. | FLAG | stage2_low_confidence | 0.008334 | ML: above threshold (no LLM available) — 0.008 |  | 0.008334 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | KSTKWP - Jerry Z on site for a chlorine leak test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | KSTP - Stephen B found CO2 levels coming down and speaking w Ben H will disregard for the night. Will monitor if continuous to go down and will place highlift pump 4 back in auto if trend continuous downward at request of Stephen B GWTP - Followed up with UV reactor 1 lamp #3 lo UV irradiance. Okay to disregard for the night. UV reactor 2 on duty 1 | FLAG | stage2_low_confidence | 0.015773 | ML: above threshold (no LLM available) — 0.016 |  | 0.015773 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | AUW57 - Joe D working on site, testing chlorine leak. Directed Well 5 pump man/off for the duration of the work. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | KSTP, Jerry Z on site testing the Cl2 leak alarm | FLAG | stage2_low_confidence | 0.0077821 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; leak [infrastructure] | 0.0077821 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | RHPSPA- Gen. Warning Alarm. Unable to clear. Emailed Jason G. and East Ops. | FLAG | stage2_low_confidence | 0.0075803 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075803 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | STPSMR, Sean P/Kyle R on site working on pump 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042952 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | VNPSAP - Joe W on site to complete a temperature alarm test and a flood alarm test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AURSBS, Notified Donald M that Yash S is finished with the network switch upgrades, Donald M is heading to site. Directed to leave the chemical system in man/off for the time being | FLAG | stage2_low_confidence | 0.01078 | ML: above threshold (no LLM available) — 0.011 |  | 0.01078 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | STW12- Hypo P1 Uncommanded stop alarm came in. Joe M on site working on pump | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054195 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | KCETDS - PAC communication failure, PAC comms failure. Hydro One restoring pole in area which is cause of initial power loss in area. Informed Yash S as critical alarm and site appears offline unable to see level. Last reading was around 66%. KCETFS still showing level KCPSDS - PAC communication failure. CMU = 11693012 3:11 - Power restored to site, Hydro One completed with work and power appears to be restored | FLAG | stage2_low_confidence | 0.025313 | ML: above threshold (no LLM available) — 0.025 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system]; comms failure [control_system] | 0.025313 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW2, Parth P on site, Duty is about to start for the tower and only one well is currently available, notified Parth P to get ahold of the operator to confirm that the tower will fill with 1 well | FLAG | stage2_low_confidence | 0.0083707 | ML: above threshold (no LLM available) — 0.008 |  | 0.0083707 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | STW12 - Man/start well 1 STW3 - Man/start well 3 STETBR - Low alarm did not come in. Change low alarm from 60 to 61% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.004686 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | HLW1 - Treated total chlorine Hi alarm. Effluent free chlorine residual higher than target. Adjusted chlorinator 1 dosage from 119 to 115%. | FLAG | stage2_low_confidence | 0.0076428 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076428 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | AUW57- Influent free cl2 hi alarm came in. Recovered after 3 mins cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055705 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | KSTP- Fin Water Fluoride Res Fault, Fin Water Tot CL2 Res Fault Alarms. Disregard as per SCADA Report. | FLAG | stage2_low_confidence | 0.012263 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.012263 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | MARS - Called Toronto water (Paul) and requested decrease flow. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064299 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NMPSKC- Talha H rebooting OIT disregard historian heartbeat alarm 13:35- NMPSKC- Talha H done rebooting OIT cleared historian heartbeat alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052194 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | KCETDS/KCPSDS, Aaron from PCS is done on site, trends looking normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061613 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | SHTP - Well pump 2 uncommanded start alarm. Checked site, plant is not active. Well pump 2 flow recently stopped. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070495 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | MKRSEM- Called Metro spoke with Brett to start two pumps to fill reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006803 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | NMW12, Alex B activated the duty of the site, if the lo/hi residual alarm comes in, Alex B would like ROC to contact Jason G. contacted Jason G but no response, will wait another 5 minutes then give him another call 14:04, Contacted Alex B as the residual is continuing to drop, Alex is on site watching and will react to the residual | FLAG | stage2_low_confidence | 0.010574 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010574 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | AURSBS - Chlorine GLCR 1 vlv fail to open. Able to clear. Reoccurring alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057357 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NMPSKC, Dan B on site, Working on pumps 5 and 6. Dan B will have to cut the power to the site. Power loss at NMPSKC will last for 30 minutes. Once power is restored, Pumps 5 and 6 will be OOS while pumps 1-4 will be available if needed | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | STPSMR - Kyle R & Sean P onsite working on valve replacement | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063798 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW2, Parth P/Rick L is finished on site, placed well back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046579 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | MARS, Contacted Toronto Operator Brent to increase the flow to the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066777 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | VNP7 - Suct Hdr free Cl2 hi, reaching hihi level and trends shows spike in reading after adjustment from today. Total also appears drop in reading. Informed Ben H. Okay to disregard hi/hihi header free. Consult | FLAG | stage2_low_confidence | 0.0080282 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080282 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Hub 1/Hub 2 Server/HLW12/HLETYS/STETTL/NMSSHS/STW12, Comm Fail alarms, contacted Yash S, he will look into it 09:24, Comms/Trends have been restored | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AUPSRR- Donald M on site to run generator test and test Cl2 leak detection alarms | FLAG | stage2_low_confidence | 0.010459 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.010459 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SUETDR, Building Flood Alarm, notified Jackie S, she will head to site to investigate the issue CMU5: W11694960 | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | RHRSTR - Deactivated D1 to maintain MARS level. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045414 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | AUW57, Joe D on site, working on the chemical analyzers and the turbidity analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050046 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | NRETCR, Jason G on site, testing Temp alarms, calibrating analyzers and doing valve testing | FLAG | stage2_low_confidence | 0.0087826 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0087826 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | QVW34 - Eric S finished on site. Placed pumps 3 and 4 back to auto as directed by Ben H. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052319 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | AURSBS- Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040024 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | VNRSKS - Deactivated duty due to lower levels at RHRSTR. Rotated pumps so that MAPS PD7 was in auto while all pumps at VNPS PD7 are man/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070503 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NRETCR, Activated D1 for Tim H | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042043 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AUW57- Joe D and Jay G on site to work on chlorinator 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044651 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | QVW12- Influent free Cl2 lo alarm came in. Slowly recovering alarm cleared after 6 mins | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060066 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NMW136- Influent free Cl2 hihi alarm came in recovered after 3 minas alarm cleared STETTL- STETTL to STW12 comm alarm. Cleared alarm trends okay GWTP- Cl tank 2 weight lo alarm disregard on shift report tank 1 full | FLAG | stage2_low_confidence | 0.0072334 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072334 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | STETBR- Tower level hi alarm STW12/3- Placed P2/3 in auto as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0047002 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | NMETHW, Evgeni S resetting OIT, directed to disregard Historian Heartbeat | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067297 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | GWTP, High Lift Free Cl2 hihi, Stephen B has reviewed the system and has directed to disregard the alarm at this time, If the residual on the analyzer hits 3.0mg/L or if the Keswick or Sutton line analyzers hit a hi/hihi alarm, Stephen B would like to be notified. consult | FLAG | stage2_low_confidence | 0.0097012 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0097012 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | Carter Dunn Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052492 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | HLETYS, Activated D1 for Jen S | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041983 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | HLETPR - Evgeny S rebooting OIT. Evgeny directed to disregard the associated Historian heartbeat alarm. | FLAG | stage2_low_confidence | 0.013964 | ML: above threshold (no LLM available) — 0.014 | sso [critical]; alarm [control_system] | 0.013964 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | AUMCBS - Rick L & Parth P onsite working on adjustment to flow meter | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066224 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | KSETDP, Junji from IAM is on site GWTP, Tyler Z on site, working on low lift pump 3 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035248 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS+NYWS Normal Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046111 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | MARS - Request TO (Mehdi) to drop to normal flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060077 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NBW3, Rashad R from Bosh Paladin Technology is on site, doing some test reports | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049421 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | QVW34, Parth P/Rick L on site, working on the total cl2 analyzer NMW15, Alex B on site, Repriming the silicate pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040698 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW5, Kyle R/Sean P leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042394 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | STW12- Placed well 1 back into auto STW3- Placed well back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041937 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NMETIB - Activated duty 1 to maintain level offset with NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048933 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated in schedule mode and then interlocked on the influent free chlorine lolo alarm. Influent free chlorine residual recovered, rotated the hypo pump duty back to pump 2 and cleared alarm. Monitored well start up. | FLAG | stage2_low_confidence | 0.014816 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.014816 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | AUW14- Placed P1 in man/on MKRSEM/MKRSMR- Peter from Metro called to notify ROC they will be running a generator from 8:30-9:30 on site and would like to activate MKRSMR D1 early. Notified Dan Z of plan and has no issues with this. Notified Peter from Metro there's no issue with generator run. | FLAG | stage2_low_confidence | 0.0091207 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091207 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | QVW34 - Eric S leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041568 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | MKRSEM - Request TO (Brent) to drop both pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059907 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | NMW12- Alex B on site to work on silicate system and NTU analyzer. Alex B is placing wells in man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054934 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | KSETDP - Rick L on site to complete analyzer calibrations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005926 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | KSETDP, Parth P is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005313 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | AUPSOH- Discharge flow lolo alarm came in. Flow with in range cleared alarm | FLAG | stage2_low_confidence | 0.0072338 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072338 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | MARS - Level Hi alarm. MAPS PD7 duty just activated. Will monitor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054873 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | MKMCLA - PAC communication failure. will monitor site and will inform PCS if does not clear by start of morning | FLAG | stage2_low_confidence | 0.019511 | ML: above threshold (no LLM available) — 0.02 | failure [equipment_failure]; communication failure [control_system] | 0.019511 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | HLW1 - Treated Free chlorine Hi alarm , value gradually increasing. Ammonia pump 1 running on duty 1, Stephen B was troubleshooting ammonia pump 1 earlier today. Notified Stephen B, he directed to switch ammonia pumps. Assigned ammonia pump 2 to duty 1 and placed ammonia pump 1 man/off. | FLAG | stage2_low_confidence | 0.014939 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.014939 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | GWTP, Parth P leaving site KSETDP, Jack P called to inform the ROC that they are testing the lo/lolo Level lit alarms on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0071967 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | KSETDP - Jackie S finished flushing chlorine analyzers and verified outlet chlorine analyzers. Requested disregard chlorine alarms, ET isolated until Monday. Jackie S leaving site shortly. | FLAG | stage2_low_confidence | 0.01465 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system]; alarms [control_system] | 0.01465 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NMW136- Combined/ treated total Cl2 lo alarms. Dip in trends. Recovered after 6 minutes, alarms cleared. | FLAG | stage2_low_confidence | 0.0075195 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0075195 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather +4C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | QVW34- Eric S on site to work on total Cl2 analyzer. Well is man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046947 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | STW12- Placed well 1 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042745 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | NMW15-Treated Total Cl2 residual low alarm. Well in man/off no water directed to users. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006002 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | AURSBS - Activated duty 1 in preparation for MAPS to JFRS feed run | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049728 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | MAPS- PD7 P2 Disch. Valve 1 Uncmd Close, Uncmd Stop. Pump 1 took over in duty 1. Cleared alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0070807 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | NMW15- Station Turbidity Hi Alarm. Rotated silicate pump duties so pump 1 in duty 1. Will monitor. 18:57- Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0047499 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | KCETDS - Aaron C working on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052512 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | QVW34, Eric S is on site, working on Cl2 analyzers AURSBS, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033195 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Connor Smith signing in -10C Windy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042119 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | KCETDS, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040402 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NBW5, Placed well back to auto as per Tim H | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044785 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NMW12 - Alex B on site to complete work orders including JHSC checks, ammonia system inspection, chlorin system inspection, flood alarm test, chlorine leak detection test, chlorine analyzer maintenance and if there is time a silicate system inspection. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | flood [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | MKPSSA - Total chlorine residual low and combined chlorine residual low alarms. Linear team is completing isolations around this station. Station is offline for the day and no water is being sent to distribution system. | FLAG | stage2_low_confidence | 0.016958 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system]; alarms [control_system] | 0.016958 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS + NYWS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004717 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | QVW12, Donald M is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040281 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | KCETDS- Aaron Carlo M on site to swap network from radio to cell connection. May lose comms for a minute or two but no other impacts expected | FLAG | stage2_low_confidence | 0.0087821 | ML: above threshold (no LLM available) — 0.009 |  | 0.0087821 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | KSETDP- Patrick F will be making adjustments to duty in system and filling tower. KSETWB will be isolated to help fill tower faster and all adjustments will be reverted once the tower reaches 95% and is isolated from system. Tower level high alarms will be expected but directed to disregard by Patrick F | FLAG | stage2_low_confidence | 0.019147 | ML: above threshold (no LLM available) — 0.019 | alarm [control_system]; alarms [control_system] | 0.019147 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | NMW136- Combined/ treated total Cl2 lo alarms came in. Looks like dip in trends. Recovered after 3 mins alarms cleared | FLAG | stage2_low_confidence | 0.0080319 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0080319 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AUW57, Joe D finished on site, will be placing the well back to auto once the cycle is done. Cl2 Pump 2/Booster 2 will be OOS for the night on site. If Cl2 Pump 1/Booster 1 has issues, contact on call | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | HLETPR - Rick L was on site for annual calibrations. Rick has completed the calibrations and is leaving site. | FLAG | stage2_low_confidence | 0.0075086 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075086 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | NMVCBA - Placed valve in man/open at 40 L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004472 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040295 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | NMETIB - Deactivated Duty 1 to offset with NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046096 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | RHRSWA- Dan B done on site both RSR MV1/2 back in local. Placed P1-4 at RHPSPA in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051597 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | MKETFA - Toronto Water (Zoran) called and informed that they will be shutting down the pump that is currently supplying MKETFA so they can test a PRV in their system. | FLAG | stage2_low_confidence | 0.010441 | ML: above threshold (no LLM available) — 0.01 |  | 0.010441 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | RHRSTR- Tim H called to req D1 activation for work on site. Activated D1 at 72% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049655 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AURSBS, Yash S is on site, switching the Network Switch, deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047484 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | AURSBS- CL2 iso valve 1 failed to open. Reset alarm | FLAG | stage2_low_confidence | 0.0097232 | ML: above threshold (no LLM available) — 0.01 | failed [equipment_failure]; alarm [control_system] | 0.0097232 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | KCPSDS- P2 failed to start alarm. Rotated Duty 1 to P1. Reset alarm | FLAG | stage2_low_confidence | 0.010506 | ML: above threshold (no LLM available) — 0.011 | failed [equipment_failure]; alarm [control_system] | 0.010506 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SHTP- Benson S called back and directed to placed filter 3 in backwash and monitor turbidity trends post backwash and to call back if they are still erratic AUW57- Influent free CL2 hihi alarm came in on well start up. Trends recovered after 3 mins cleared alarm | FLAG | stage2_low_confidence | 0.010904 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010904 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NMW15- Treated free hihi alarm came in. Well not active no water directed to users. Continue to monitor trends did not recover. Placed well in man/off emailed Central water team | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | STW12 - Place well 2 back in auto STW3 - Place well 3 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041998 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | KCETFS, aaron from PCS is on site, examining the network switch, not making any changes, just observing the switch 11:34, Aaron is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039379 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | KSETDP - Parth P finished and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058777 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | RHRSWA - Dan B on site to complete maintenance on one of the valve actuators. Dan B needs to complete a valve exercise test. Deactivated duty 1 for RHRSWA to shut down the RHPSPA pumps and placed all RHRSPA pumps in manual/off to prevent accidental activation. | FLAG | stage2_low_confidence | 0.011571 | ML: above threshold (no LLM available) — 0.012 |  | 0.011571 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | MKPSSA, Rob P called saying they are isolating that pumping station. That station cannot run while it is isolated. East operator are aware and also notified Travis W to confirm that it is now isolated | FLAG | stage2_low_confidence | 0.011915 | ML: above threshold (no LLM available) — 0.012 |  | 0.011915 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | AUW14- Building flood alarm came in. Notified Joe D on site will investigate | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NBW3, Influent Free Cl2 lolo, Influent dropped at start up, waited roughly 10 minutes for recovery however still residual remains lo. Placed well 3 man/off and notified Jordan B since it is his site | FLAG | stage2_low_confidence | 0.0089005 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089005 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -16C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046216 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | RHRSTR/VNPSCD - Johnathan from PS testing sprinkler alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069257 | 0 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | GWTP - Patrick F called to inform that the maintenance team will be on site to work on a valve in the UV system. GWTP will be offline during this work. Patrick will coordinate with Central Team to have KSTP active top fill the system during this time. Patrick will also check the Sutton Header pH high reading. | FLAG | stage2_low_confidence | 0.019164 | ML: above threshold (no LLM available) — 0.019 |  | 0.019164 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | NMW12,NMW136 - Kingsley M rebooting OIT QVW34 - Eric S finished at site, Ben H will return later to test run wells. Currently man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056384 | 0 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | MKRSEM - Building smoke alarm. Called Stephen B, no response. Will call again later. 16:00 Stephen B will attend site. # CMU5 W11695281 | FLAG | stage2_low_confidence | 0.010504 | ML: above threshold (no LLM available) — 0.011 | smoke [equipment_failure]; alarm [control_system] | 0.010504 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NMTKKC / NMETIB - Talha H completing work on the OIT's and directed to disregard associated historian heartbeat alarms. MAPS pD7 - Chris I on site to complete work on pump 4. | FLAG | stage2_low_confidence | 0.011327 | ML: above threshold (no LLM available) — 0.011 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.011327 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | NMTKKC- Chris S on site to work on UPS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054311 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | BVPS, Activated D1 for Tim H | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041642 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | NMTKKC, Chris S is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053095 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | Dialer/DMZ Reset. Kingsley M called, resetting System, Dialer/DMZ will be down for a few minutes, he will give a call back once he is finished on his end 12:04, DMZ SCADA is back to normal 12:16, Dialer is back to normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0052435 | 0 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | AUW14- Treated free Cl2 hihi alarm came in. Continued to monitor. Ammonia dosing slowly adjusting but increased flow and alarms cleared | FLAG | stage2_low_confidence | 0.0075145 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0075145 | 0 | 0
2026-02 | 2026-02-28 | All Water System ROC General | ROC | GWTP - High lift Free chlorine residual low alarm. Plant is off, High lift pumps not running, SUETDR line is active. Notified Stephen B. Requested disregard for now and monitor. Call back if receive clear wells chlorine residual alarms. Alarms will clear when duty activated. # Consult 17:38 High lift free chlorine residual low alarm cleared. | FLAG | stage2_low_confidence | 0.020943 | ML: above threshold (no LLM available) — 0.021 | not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.020943 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | STETBR - tower level hi alarm. Placed STW1 and STW3 in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005491 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | NMW15 - Noticed outstanding Station Turbidity Hi. Checked site. Noticed well is running in schedule mode. Trends indicate that turbidity levels have been higher through each run. Silicate pump 1 is currently running and the only one available. Placed well man/off and will send an email to central water team 21:50 - Called Jerry Z. to confirm compliance during this high turbidity level. Jerry directed to leave the well man/off for the remainder of the night #CONSULT | FLAG | stage2_low_confidence | 0.020032 | ML: above threshold (no LLM available) — 0.02 | compliance [regulatory] | 0.020032 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | KCETDS, Outlet Total Cl2 Res lolo, abnormal dip occurred, if residual doesn't recover, will contact operator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060276 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | GWTP, ZW6 Permeate Turbidity Fault/OOR Alarm, notified Jack P, Directed to place the filter off and Jack P will look into it consult | FLAG | stage2_low_confidence | 0.0095227 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; alarm [control_system] | 0.0095227 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | MKRSEM, Notified Paul from Toronto to start filling the res MARS, Notified Paul to go back to normal flow for the time being | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057815 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | STRS48 - High lift pump 1 fail to stop alarm. Checked site, SCADA shows the pump as active but no flow is registered on the flow meter. While monitoring the pump showed as deactivated. Able to clear alarm. Pump was re-assigned duty 1 automatically. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system] | scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | JFRS - Deactivated duty 2 and then duty 1 to keep reservoir level low for the Maple to jefferson feed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058927 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto, as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061178 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040295 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | NBW3 - Influent Free Chlorine Lo and LoLo switch alarm came in. Checked site. This occurred on duty activation. After a few minutes, influent levels went back to optimal range. Cleared alarms and interlock after 10 mins. Well started back up. Will monitor | FLAG | stage2_low_confidence | 0.012638 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012638 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | GWTP - ZW2 34.5 KPa MIT - Press Decay Test Failed and ZW2 Shutdown alarm came in. Checked site. Called Jack P. who directed to place the train off and then initiate MIT. Jack would like a call back if the train fails again 02:41 - ZW2 Test failed and MIT Sequence aborted alarms came in. Called Jack P. who directed to place train 2 off for the night and change the duty 1 flow setpoint from 180 L/s to 160 L/s #CONSULT | FLAG | stage2_low_confidence | 0.022397 | ML: above threshold (no LLM available) — 0.022 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.022397 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | GWTP - Make up air unit 1 coil low temperature alarm. Shift report states that this MUA coil alarm can be disregarded. Will send email to OCO to inform. | FLAG | stage2_low_confidence | 0.0082686 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0082686 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | NMTKBS, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004002 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Zoran) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069673 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | Carter Dunn Signing In, -15D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042054 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | GWTP - ZW4 Membrane Air Valve Failed, Membrane SetB Air Inlet Valve failed to close and train 4 shutdown alarms came in. Checked site. Plant is running. Called Jack P. who informed he will take a look on SCADA Jack informed that he has placed train 4 back online #CONSULT | FLAG | stage2_low_confidence | 0.024696 | ML: above threshold (no LLM available) — 0.025 | failed [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; valve failed [infrastructure] | 0.024696 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | KSTP - Carbon Dioxide HiHi alarm came in. Value went to normal and alarm cleared on its own | FLAG | stage2_low_confidence | 0.0077776 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077776 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | Terminating Maple to Jefferson feed and reverting changes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063162 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal ARPS, David from OCWA called, they are rotating pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004535 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | NBW5 - Turbidity Hi alarm came in. Checked site. Well is active. Rotated silicate pumps so that silicate pump 2 is in duty 1. Will monitor 19:20 - Turbidity levels came back to optimal range and alarm cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061768 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | NMTKKC - Outlet Total Chlorine LoLo alarms came in. Checked site. Duty is active. Level went back to optimal range right away. Alarm cleared right away | FLAG | stage2_low_confidence | 0.010689 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010689 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | MAP7 - PD7 P3 Discharge Valve 1 Uncommanded Close alarm came in. This occurred on duty activation. Duty rotated so that pump 1 and 2 are running in duty 1. Pump 3 is interlocked. 03:59 - Interlock cleared and pump 3 is now available again | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0072084 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | KSETWB -Evgeny S done reboot. Cleared historian heartbeat. Trends okay NMETIB- Both NMETHW and NMETIB draining. Notified Ben H for direction as per interim. Ben H directed to increase NMETIB D1 stop from 75 to 80 Percent and restart D1 | FLAG | stage2_low_confidence | 0.0087812 | ML: above threshold (no LLM available) — 0.009 |  | 0.0087812 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AUPSOH- Ben H done on site and has reverted all system changes | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060418 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | KSTKWP- Evgeny S rebooting OIT disregard historian heartbeat alarm until done | FLAG | stage2_low_confidence | 0.0076086 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076086 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | NMW15- Influent free Cl2 hi alarm came in on well start up. Cleared alarm after 3 mins as trends recovered | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063286 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | NMETIB- Total Cl2 hi/hihi and combined hi alarms came in. Tower fillings. Notified Jay G will head to site. Created CMU5 W11631082 ARPS- Sam from OCWA called back. P1 running in auto after issues with P8 were resolved #CMU5 | FLAG | stage2_low_confidence | 0.0093222 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0093222 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | VNRSKS - Activated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041091 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | SUETDR- Talha working on OIT. Disregard Heartbeat Alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068605 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | MKRSEM- Called Toronto (Poulan) and requested two pumps on. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063252 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AUPSRR- Ric L and Parth P finished onsite. Placed chlorinators and ammonia pumps back into auto. | FLAG | stage2_low_confidence | 0.0075304 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075304 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | KSETWB- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069695 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | GWTP- raw water total Cl2 res hihi alarm. Disregard on shift report as it recovered after 30mins cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064384 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | YWS + NYWS Normal RHRSTR, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.002943 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | SHTP- Reservoir Total Chlorine Lo Alarm. Notified Jacob M. He is onsite and just rotated reservoirs. | FLAG | stage2_low_confidence | 0.0082092 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0082092 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | AUW14, Placed wells 1/4 man/off so more water can be moved from AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050628 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | STW12- Placed well 2 man/on STW3- Placed well 3 man/on For STETBR Fill Cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036089 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | NBW5, Turbidity Hi alarm, well is currently off, tower is currently draining | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057462 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AURSBS- Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040024 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | AURSBS - Activated duty 1 to fill reservoir before the Maple to Jefferson feed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052512 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | MAPS PD7, Placed pumps 1/3 to auto VNPS PD7, Placed pumps 1/4 to man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035543 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | NMMCBS- Downstream Pressure LoLo Alarm NMMCAD- Upstream Press Lo Alarm. Justin Q called. Aware of alarms and addressing them | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0065679 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | ARPS- Sam from OCWA called. Having issues switching pumps over from pump 7 to 8. He will contact Peel SCADA team for assistance and inform us when pump back running. 11:02- Sam called. Pump 1 running in auto | FLAG | stage2_low_confidence | 0.00859 | ML: above threshold (no LLM available) — 0.009 | scada [control_system] | 0.00859 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | MTETNL- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069701 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | Connor Smith signing in -15C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042123 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AUPSRR- Rick L and Parth P. on site for calibrations. Notified Ben H of work on site. Directed to place chem system in man/off for duration of work. MAPS PD8- Dan B done work on P1 and moving to P2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070299 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AUPSOH- Justin Q and Ben H on site shutting down P3/4 for testing. Will call back when done testing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054631 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Mehdi) and requested they deactivate the pumps pushing flow to MKRSEM. | FLAG | stage2_low_confidence | 0.0076905 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076905 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | RHRSTR - Deactivated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041621 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | STW1/3, Placed wells 1/3 man/on MAPS PD7, Placed pumps 1/3 man/off VNPS PD7, Placed pumps 1/4 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0028154 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AUPSOH/NMTKBS- Ben H called. Running a test involving these sites in same pressure district. Requested a call for any pressure alarms in Aurora or Newmarket | FLAG | stage2_low_confidence | 0.012685 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012685 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | STPSMR- Travis W and Joe M on site for cylinder change ARPS- Sam from OCWA (Peel) is transferring to another pump NMW15- Alex B on site to respond to turbidity issues. Created CMU5 W11630987 #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005208 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | NMVCBA - Placed valve man/open at 40 L/s 00:57 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030115 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | NBW2- Eric S finished onsite. Placed well back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047392 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | MKRSEM, Notified Toronto operator Zoran to stop pumping to the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063719 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | GWTP- Train 4 membran air valve failed to open/ shutdown. Notified Patrick F. Will take a look on site | FLAG | stage2_low_confidence | 0.016126 | ML: above threshold (no LLM available) — 0.016 | failed [equipment_failure]; valve failed [infrastructure] | 0.016126 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AUPSRR- Gas chlorinators found in man/open. Notified Rick L. Rick L working on system no gas flow just working on position instruments MAPS PD8- Deactivated D1 for AURSBS and placed P2/3 in D1 to run as req by Dan B to ensure proper working order after PMs NBW2- Eric S on site to replace buttons on effluent free Cl2 analyzer. Placed well in man/off SUETDR- Talha H rebooting OIT Disregard historian Heartbeat alarm until done | FLAG | stage2_low_confidence | 0.015496 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.015496 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | Carter Dunn Signing In, -11D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042054 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | Initiating changes for Maple to Jefferson Feed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059768 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | BLETNL, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004003 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AUPSOH- Yash S working on OIT. Disregard Heartbeat Alarm. 14:50- Completed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0039688 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -11C and partly cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046527 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | QVETQS - System Pressure Lo alarm came in. Checked site. Duty for NMETHW just deactivated and QVW12 shut down. Trends indicate a quick dip and comes back to optimal range. Alarm cleared | FLAG | stage2_low_confidence | 0.0094985 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0094985 | 0 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | NMETHW, Activated D1 to help offset the towers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045202 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | HLW2 - Downstream Pressure Hi alarm came in. Checked site. Duty is still active. Lowered flow setpoint to 15 L/s as per shift report. Downstream pressure went back to optimal range and alarm cleared | FLAG | stage2_low_confidence | 0.010089 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010089 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | QVW12- William M onsite for chlorine cylinder change | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046363 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | MAPS PD8- Dan B on site for PMs req P1 in man/off. Placed P1 in man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048005 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | QVW12- Gerrick from Ferguson onsite for generator work. Disregard any generator alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0069386 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | KSETWB, KSETWP, MTETNL- Evegeny S working on OITs. Disregard Heartbeat Alarms. | FLAG | stage2_low_confidence | 0.0087902 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0087902 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | ANMCBL- Tyler Z on site for sump pump work | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055522 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | QVW34- Eric S onsite with William M working on treated analyzer. Wells are manual and local off 10:35- Finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044141 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | VNRSKS- Deactivated D1 MAPS PD7- Placed all pumps in man/off VNPS PD7- Placed P1/4 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038428 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | KSTKWP- Eric S onsite working on chlorinator 1. 11:27- Finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035296 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AURSBS- Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040024 | 0 | 0
2026-02 | 2026-02-02 | All Water System ROC General | ROC | AUPSRR- RSR outlet total/Combined Cl2 lo alarms outstanding. Notified Rick L. Should be in calibration mode. Rick L will look into it | FLAG | stage2_low_confidence | 0.0084159 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0084159 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NMETIB- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053242 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NMW136- Influent Free Chlorine HiHi. Value recovered. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052875 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | YWS + NYWS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038512 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | JFPS- VC UPS ATS Source S2 (Line), RES UPS ATS Source S2 (Line), WPS UPS ATS Source S2 Line) Not OK Alarm. Alarms Cleared. BVPS- Pump 4 Uncommaded Stop, Pump 4 Disch Vlv 1 Failed to Open, Pump 1 Disch Vlv 1 Failed to Open. Deactivated duty and cleared alarms. RHPSPA- Hydro Power Fail. Alarm cleared | FLAG | stage2_low_confidence | 0.021601 | ML: above threshold (no LLM available) — 0.022 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.021601 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | BLW34-Well 3 Percent Declined LoLo Alarm. Trending shows Well 3 Performance dropping to a negative value last several cycles. Placed well man/off. Alarm cleared on its own after well turned off. Will email Patrick F. 03:40- Influent Free CL2 Res LoLo. Interlocked Well. Well was already man/off | FLAG | stage2_low_confidence | 0.011043 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011043 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | SHTP- KMNO Pump 1 Leakage Alarm. Pump 1 Fault Alarm. Pump 2 rotating in and out of duty 1. Notified Cole W. He will take a look. 05:00- Cole W will attend site W11664772 CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | fault [equipment_failure]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AUW14 - Yash S. called back to inform that he will email Danielle M. of these missing trends but wanted to know if this can be resolved on Monday. Requested if Evgheny S. is able to backfill the data. Yash will speak to Evgheny | FLAG | stage2_low_confidence | 0.01057 | ML: above threshold (no LLM available) — 0.011 |  | 0.01057 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Zoran) and requested to start two pumps | FLAG | stage2_low_confidence | 0.0086027 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086027 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | MAP8 - Suction Header Free Chlorine Residual LoLo alarm. Dwyane L. informed that this alarm can be disregarded | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067301 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | NMETIB- Deactivated Duty 1 to offset with NMETHW NMVCBA/NMVCIB - Reverted flow setpoint changes | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047194 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMTKKC- Jay G placing staion back on utility power. Placing chem pumps in man/off andw ill be monitoring issues with comms to Newmarket wells. Jay G and Ian W will monitor the switchover. | FLAG | stage2_low_confidence | 0.01149 | ML: above threshold (no LLM available) — 0.011 |  | 0.01149 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MKRSEM, Notified Zoran to stop pumping to the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058961 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | NMETIB- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053242 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | STW12/3- Placed Well 2/3 in man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045616 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | HLW1/2- HLW1/2 to HLETYS comm alarm came in. Cleared upon acknowledgment. Trends okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059739 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | GWTP - Patrick F working on UV system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005739 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | VNRSKS - Deactivate duty 1 nearing stop VNP7 - Place pumps 2 & 3 back in man/off MAP7 - Place pumps 1-3 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044111 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMW136- Kyle R on site to disconnect well 13 motor. Alex B also on site to isolating well 13 ARPS- Martin from Peel called to notify ROC about PCS upgrades on their end | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061233 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW12 - Artour L on site, connecting generator, disregard alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0058802 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Paul) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069305 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | yws + nyws normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | VNPS- Pre injection total Cl2 hi alarm came in. Spike looks higher than normal and not recovering. Notified Tim H who will verify with grab TMC 317- Called Metro spoke with Mehdi to notify that ARPS is back online and returned flow to normal | FLAG | stage2_low_confidence | 0.010003 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010003 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW34- P4 VFD fault and Estop. Called Will M. Maintenance Ops on site replacing motor on P4 | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | MAP8- Suction header com. chlorine residual Hi alarm. As per Dwayne L and Tim H. Suction header is Isolated until further notice. Tim H requested disregard MAP8 Suction header CL2 and PIT alarms. # Consult | FLAG | stage2_low_confidence | 0.0087182 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0087182 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCPSDS- Comm fail. Ack/reset. Alarm cleared right away. Trends okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KSETDP - Tower outlet flow fault alarm, ET isolated, site offline. | FLAG | stage2_low_confidence | 0.013658 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system] | 0.013658 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHRSWA - Power restored, Historian Heartbeat- alarm notified Ian W, he will check SCADA. | FLAG | stage2_low_confidence | 0.007789 | ML: above threshold (no LLM available) — 0.008 | scada [control_system]; alarm [control_system] | 0.007789 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STPSMR, Pump 1/3 VFD Fault, Notified Dan Z, she is heading to site CMU5: W11674045 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure] | 0.0060544 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | MARS - High level alarm. Deactivated RHRSTR duty 1 to stop the BVPS flow. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0056819 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NMETIB - Activated D1 to offset with NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044833 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | JFRS - WPS Gen xfer switch to hydro power, ATS source not ok, RES UPS source 2, WPS 3 & 4 failed to start, able to reset alarms except pump 2 & 4 related alarms as they are unable to came back on. Generator not running. Informed Jerry Z, will head to site CMU = 11667801 RHPSPA - Hydro power failure, suction pressure hihi. Spike in pressure but came back within range. VNPSCD - Post-inj comb hihi, chlorine system failure. Alarms came in as BVPS shut down suddenly. Readings came back within range after spike. Informed Jerry Z as well as critical alarms and able to clear BVPS - pumps uncmd stop. Able to clear and after some time pumps able to run without issue. | FLAG | stage2_low_confidence | 0.091276 | ML: above threshold (no LLM available) — 0.091 | failed [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.091276 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | HLETYS - Post-injection combined chlorine lo. Value within range and alarm cleared | FLAG | stage2_low_confidence | 0.0077758 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077758 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | MTELNL - Outlet free chlorine hi, reached hihi level in reading. Sudden spike as earlier but no signs of reading coming back doen. Activated duty 1 to direct water to tower. Informed Patrick F, will look into issue Consult | FLAG | stage2_low_confidence | 0.0085034 | ML: above threshold (no LLM available) — 0.009 |  | 0.0085034 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MARS - Low level alarm. Called Toronto Water (Paul) and requested to increase flow to reservoir | FLAG | stage2_low_confidence | 0.0082542 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0082542 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | AURSBS - Deactivated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041392 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | JFPS- Tim H placed pump 2 into duty 1. Requested to switch pump 3 into duty 3 and back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058159 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | MAP8 - Suction Header combine chlorine residual HiHi alarm. Disregard alarm as per Tim H. Suction Header is isolated until further notice. | FLAG | stage2_low_confidence | 0.0076521 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076521 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | MKRSEM - Called Toronto water (Zoran) and requested stop filling Res. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066203 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | RHRSTR - Deactivated Duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041621 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | VNRSKS - Activated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041269 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to two MAPS pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060547 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | STETBR - Tower hi level alarm. Placed STW12 and STW3 in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055138 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | YWS + NYWS Normal Carter D Signing Ouit | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038009 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHPSWA - Power restored, cleared all alarms. | FLAG | stage2_low_confidence | 0.0072809 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0072809 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | STW12, STW3- Placed wells back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004411 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | STPSMR- Lo Cl2 effluent alarm came in on dialer. Travis W on site sampling and residual recovered. Notified Travis W no SCADA alarm came in for issue | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0070712 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | HLW2, Stephen B is leaving site, well 2 will be man/off for the night | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050322 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | SHTP- Cole W directed to placed sample pump 2 in man/on and will Cole W will clear alarm in a few minutes 12:35- SHTP- Cole W req CMU5 and will attend site later this afternoon. Analyzer still working correctly but fault will not clear. Created CMU5 W11667765 12:49- SHTP- Reservoir total Cl2 lolo alarm came in. Notified Cole W. Directed to swap sample pumps again and verify if dosing is in manual for chlorinators. Swapped sample pumps and dosing is in manual. Cole W ill atternd site #CMU5 | FLAG | stage2_low_confidence | 0.037349 | ML: above threshold (no LLM available) — 0.037 | fault [equipment_failure]; alarm [control_system] | 0.037349 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STW3 - Influent/effluent chlorine residual Hi alarms, Joe M will check SCADA. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0066239 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHMCMD- Valve 1/2 Fault outstanding. Valves in manual. Valve 1 is showing 3 percent open with normal flow. Notified Rob P of outstanding alarms after power fails across Richmond hill and Vaughan. Rob P will consult Linear team and notify ROC of further actions | FLAG | stage2_low_confidence | 0.024796 | ML: above threshold (no LLM available) — 0.025 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.024796 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | HLETYS - Stephen B requested to activate Duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045695 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | AUPSRR - Donald M performing w/o on site including: Chlorine analyzers maintenance, chem scan maintenance, testing ammonia flood alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | Connor Smith signing in 2C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041757 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047043 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NMW12 - Silicate Pump 1 Failed to Start alarm came in. Checked site. Wells are running. Silicate pump 2 rotated to duty 1. Alarm cleared. Will monitor | FLAG | stage2_low_confidence | 0.0153 | ML: above threshold (no LLM available) — 0.015 | failed [equipment_failure]; alarm [control_system] | 0.0153 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | AUW57- Influent Free Chlorine HiHi Alarm. Value recovered. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054165 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | STW12- Placed well 1 man/on STW3 - Placed Well 3 man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039332 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | 145 Harry Walker Parkway Server Room- Talha H accessing SCADA Server Room with badge and access code | FLAG | stage2_low_confidence | 0.0075024 | ML: above threshold (no LLM available) — 0.008 | scada [control_system] | 0.0075024 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | GWTP - Patrick F on site to complete a manual backwash of GAC 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046698 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | BLW34 -Kyle C and contractors finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042557 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | AUW57 - Station Turbidity Hi alarm came in. Turbidity levels kept rising after 12 mins. Rotated silicate pumps so that silicate pump 2 is in duty 1. Will monitor. 21:00 - Levels came back to optimal range and alarm cleared 02:23 - Station Turbidity Hi alarm came back in with silicate pump 1 in duty 1 again. Rotated silicate pumps so that pump 2 is in duty 1. Placed silicate pump 1 manual/off 05:15 -Station Turbidity HiHi alarm came in. Placed well man/off. Confirmed with Jerry Z. | FLAG | stage2_low_confidence | 0.010383 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010383 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHPSPA, JFPS, RHAMF - Site hydro power fail across these sites. Likely a blip as the generators did not run and alarms cleared right away RHAMF - Odour Control system offline alarm came in. Checked site. Both fans are still running. Alarms cleared after 2 mins | FLAG | stage2_low_confidence | 0.0090479 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0090479 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | JFPS- Lee F finished onsite. Requested to leave pump 2 man/off. Can run in emergency. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | MARS - Changed low level alarm setpoint from 60% to 55%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052528 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW12 - Artour L called, transferred site to station generator. Man/started Well 1 pump for test. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057198 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | STW12/STW3 - Place well 2 & 3 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044786 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | SHTP- Highlifts interlocked due to lolo reservoir level. High lifts were called for due to F2 backwash status drawing down high lifts. F2 coming out of backwash notified Jake M of interlock. Jake M cleared alarms on site. Plant will be shut down soon for PCS work | FLAG | stage2_low_confidence | 0.014085 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system]; alarms [control_system] | 0.014085 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | MKRSEM - Reservoir 1 Level Lo alarm came in. Called Toronto Water (Zoran) and requested 2 pumps on 04:37 - Called Toronto Water (Mehdi) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053553 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | VNRSKS - Dave T on site for flood alarm test and health and safety inspection. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | QVW12, Kyle R on site working on Well 2 failed to start issues | FLAG | stage2_low_confidence | 0.0084193 | ML: above threshold (no LLM available) — 0.008 | failed [equipment_failure] | 0.0084193 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | AUW14 - Joe D cleaning chlorine analyzers, turbidity meter and running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052989 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STETBR, Eric S on site working on the Cl2 analyzer KSTP, Jerry Z on site, cleaning the Cl2 analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003787 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMW15, Eric S is finished on site AUW14, Joe D is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032483 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | Angelica Chepiga signing in,weather +2C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | SHETCS - Eric S working in Hypo pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057711 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | AUW14 - Ammonia pump 1 fault alarm at duty stop. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | QVW34 - combined chlorine hihi, came back within range shortly | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004859 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | MARS - TO (Mehdi) pushing higher flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057377 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | NMTKKC - Ammonia Tank 2 Level HiHi alarm came in. Checked site. Noticed that the trends did not indicate any spike. Ammonia tank level back at optimal range and alarm cleared | FLAG | stage2_low_confidence | 0.0090744 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0090744 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | MAPS PD7 P2 disch valve uncomm close and P2 uncomnd stop alarms came in. Able to clear alarms VNPS- Post injection total Cl2 hi alarm came in. Reset after 3 mins after residuals recovered | FLAG | stage2_low_confidence | 0.0079932 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0079932 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | STW3- Joe M on site to work on analyzers. Lo/hi temp alarms. Will be testing Cl2 leak alarm later but will call back to confirm 10:59- STW3- Joe M testing Cl2 leak alarm | FLAG | stage2_low_confidence | 0.0095657 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.0095657 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | HLW2 - Treated total chlorine , combine chlorine residual low alarms. Well 2 duty not active, no water directed to users. Chlorine residual value recovered, alarms cleared. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | JFPS - Tim H headed to site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055125 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | QVW34- Tyler Z on site working on generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004181 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MAPS - Tim H and Dan B on site troubleshooting PD7 pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045017 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | VNRSKS- Lee F working on eyewash , disregard alarm for now. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070162 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | GWTP, Patrick F on site working on all Turbidity Analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059005 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | ARPS - David from OCWA notified OP performing maintenance on Total and free ammonia analyzers. | FLAG | stage2_low_confidence | 0.0072261 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072261 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | ARPS - David from OCWA called, rotating pumps from Pump 1 to Pump 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050525 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STW12, STW3 - Man/started pumps 1 and 3 for STETBR fill cycle. ok with Joe M | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052393 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NMETIB- Activated D2 to offset from NMETHW as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048519 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AUPSRR - Post injection free chlorine hihi alarm. Checked site, trending shows a spike of the post injection free chlorine reading which returned to normal range within one reading interval. reset alarm. SHTP - Well pump 2 uncommanded start alarm. Checked site, plant is not active. Well pump 2 flow recently stopped. Cleared alarm. NMETIB - Inlet flow hi alarm. Checked system, NMVCBA flow is above setpoint. Trending shows the valve tried to increase flow to reach the setpoint but opened too much. Will monitor valve to ensure it returns to the flow setpoint. | FLAG | stage2_low_confidence | 0.025531 | ML: above threshold (no LLM available) — 0.026 | alarm [control_system] | 0.025531 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 3 at MAPS 02:40 - Reverted all changes | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025324 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | AURSBS - Activated duty 1 YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029889 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | STRS48- Joe M on site to run generator and clean Cl2 analyzers NMW15- Yash S on site for network switch. Placed well in man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051432 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | NMVCBA - Flow setpoint from 40L/s to 80L/s to offset NMETIB/NMETHW NMVCIB - Flow setpoint from 80L/s to 40L/s to offset NMETIB/NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056453 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | NMW15 - Treated total chlorine residual Hi alarm. Adjusted chlorinator 1 dosing factor from 48 to 45%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064586 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | VNPS PD7 - Pump 3 man/stop MAPS PD7 - Pump 1 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039451 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NMW15, Alex B on site, testing Cl2 leak alarms MAPS PD7, Placed pumps 1/2 man/off VNPS PD7, Placed pumps 2/3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.0059646 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNETFD, Benson S on site doing health and safety checks and hooking up the portable generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069865 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KSTP- Eric S on site to work on Pre total Cl2 analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044166 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | QVW34- Tyler ZJ finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039887 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | NBW3- Influent free Cl2 lolo switch alarm , starting in schedule mode / wells interlocked. Influent free Cl2 residual to recovered , reset alarms and restarted P7 | FLAG | stage2_low_confidence | 0.0085426 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0085426 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: 0C and rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004415 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | HLETYS- Post injection combined lo alarm came in. Tower filling and dosing. Monitored for improvement as hypo system tends to slowly increase speed as fill cycle progresses. After 20 mins hypo pump increasing speed and Combined Residual not improving. Decreased max flow of P1 from 190 to 187. Slight improvement over 10 mins decreased max flow to 185. Continued to monitor | FLAG | stage2_low_confidence | 0.022981 | ML: above threshold (no LLM available) — 0.023 | alarm [control_system] | 0.022981 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | MKRSEM- Called Metro spoke with Pouran to start 2 pumps RHPSPA- Travis W on site to Gen test run, surge valve test and perform valve exercises AURSBS- CL2 iso valve1/2 failed to open. ack reset aalrms. Found Post total and free Cl2 analyzers in calibration mode. Notified Donald M. Directed to disable calibration mode on both analyzers. KSTP- Artour L on site to commission diesel tank LITs QVETQS- Jay G on site to clean outlet analyzer. Taking grab on site while working on analyzer. NMETIB- Deactivated at 72% NMETHW- Activated D1 at 48% AURSBS- Post injection free hihi switch alarm came in. Notified Donald M. Will attend site to 0 analyzer. Created CMU5 W11676555 SHTP-Jake M returned planet to normal Ops #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; alarm [control_system] | failed [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | SHETCS -Activated Duty 1 as per Memo | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043082 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STPSMR - Dan Z leaving site. QVW34 - Treated total and combine chlorine Hi alarms. Adjusted chlorinator 1 dosing factor from 77 to 72%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0060407 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NMTKKC - Ammonia pump 1 uncommanded stop alarm. Checked site, ammonia pump 2 rotated into duty 1 and is operating. Able to clear alarm. | FLAG | stage2_low_confidence | 0.007596 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.007596 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | COTFA - PD6 and PD5 Pressure LoLo alarm came in. Checked site. Trends indicate a dip but came back within 2 mins. Alarms cleared | FLAG | stage2_low_confidence | 0.0073177 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0073177 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AUW14- Yash S on site for network switch. Placed all wells man/off and will lose comms QVW34- Dan B on site for well 4 electrical work MKVCSA- PAC Control panel power fail MV general alarm and site power fail. Comms loss on site but valve in man open at 18% will continue to monitor and check for outage | FLAG | stage2_low_confidence | 0.010936 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010936 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BVPS - Ben H shutting down BVPS to save on diesel fuel during the ALectra utility network issues. | FLAG | stage2_low_confidence | 0.0075877 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075877 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | STW12- Placed Well 1 in man/on as per interim STW3- Placed Well 3 in man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046184 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | NMW15- Alex B onsite working on silicate injection points. Will have well Local off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053877 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | JFPS- Tim H going to placed site back on utility | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060412 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | HLW1 - Treated Free Chlorine Hi alarm came in. Checked site. Trends indicate a spike. but came back to optimal range. Alarm cleared after 5 mins | FLAG | stage2_low_confidence | 0.007838 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.007838 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCPSDS- Tim H able to reset VFD not ready alarm and is heading to KCETFS to investigate potential power outage on site | FLAG | stage2_low_confidence | 0.0083892 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0083892 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCETDS- Yash S able to restore comms. after network switch. KCPSDS- P2 VFD not ready aalrm KCETFS - Inlet valve fault alarm outstanding. Called Tim H. Will investigate both outstanding alarms | FLAG | stage2_low_confidence | 0.012793 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.012793 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | YWS+NYWS normal Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046111 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | VNETFD - Site hydro failure alarm. Checked site, tower is draining and there is no rechlorination or analyzers on site. Able to clear alarms. No power outage on the Alectra outage map for the local area. Likely a power blip. VNVCIA - Site power failure alarm. Valve was closed and duty off when alarms triggered. Able to clear alarm. No power outage on the Alectra outage map for the local area. Likely a power blip. KLMCHR - Site power failure alarm. Checked site, trending shows no impact to operations, able to clear alarm. No power outage on the Alectra outage map for the local area. Likely a power blip. | FLAG | stage2_low_confidence | 0.07514 | ML: above threshold (no LLM available) — 0.075 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.07514 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | COTFA - Communication failures to NRETBR, MKRSMR, MKRSEM, and STPSTL. Checked sites. After 5 mins, all alarms cleared and trending is okay 12:55 - Alarms came back in. After 5 mins, alarms cleared | FLAG | stage2_low_confidence | 0.012672 | ML: above threshold (no LLM available) — 0.013 | failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system] | 0.012672 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | NMVCBA- Placed valve back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056242 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMETIB - Combined chlorine, total chlorine hihi. Found reading spike up suddenly during drain cycle. Activated duty to direct water to tower. Informed Jerry Z, will head to site for a grab sample CMU = 11667856 3:37 - Jerry Z requested instrumentation assistance. Informed Parth P to follow-up with Jerry Z Consult 3:44 - Combined chlorine hihi (critical) Jerry Z onsite | FLAG | stage2_low_confidence | 0.014464 | ML: above threshold (no LLM available) — 0.014 | follow-up [maintenance_action] | 0.014464 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCETFS- Created CMU5 for Tim H W11679626 in response to power fail on site #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004396 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | HLW2 - Tim H. called to inform that he is finished on site and the well is back up and running. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053711 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | QVW12- Treated free Cl2 hihi alarm came in. Trends recovered after 6 mins alarms cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0060395 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | STW12 - Well 1 man/on STW3 - Place man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036867 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | STW3, Influent Free Cl2 hi alarm, adjusted Chlorinator 1 dosing factor from 288 to 260%, will continue to monitor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006803 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STETBR - Eric S finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052627 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AUW14- Missing trends during the network switch. Wells were ramping down while switch occurred. Notified Joe D. Joe D took grab at 11:45 today. Notified Yash S off missing trends. Yash S will email Danielle M to see if they can be backfilled. MAPS PD8- Dwayne L on site to work on PIT onPD8 suction | FLAG | stage2_low_confidence | 0.0094012 | ML: above threshold (no LLM available) — 0.009 |  | 0.0094012 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCETDS- Comm fail. Alarm cleared upon acknowledgement. Trends okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | VNP7 - Activate duty 1 as MARS level high | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044335 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | QVW34- Tyler ZJ on site to work on generator will not be transferring | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047382 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | NMETIB - Activated duty 1 to help offset with NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046546 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to MAPS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057695 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | KSTKWP - Total Chlorine Lo Lo switch alarm came in. Checked site. Tank is draining. Trends indicate a dip and then comes back to optimal range. Will monitor | FLAG | stage2_low_confidence | 0.010953 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010953 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | VNP7 - Place pump 3 auto MAP7 - Place pump 1 & 2 man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040124 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | GWTP - ZW2 34.5 KPa MIT - Press Decay Test Failed and ZW2 Shutdown alarms came in. Checked site. Duty is still active. Called Joe M. who directed to leave train off for the night and alarms can be disregarded 02:08 - Joe M. called back and directed to deactivate duty 02:09 - Hi Lift Pumps Exceeded Membrane Filter Flow limit alarm came in. Joe informed that this alarm will clear once the hi lift pump shuts down #CONSULT | FLAG | stage2_low_confidence | 0.015419 | ML: above threshold (no LLM available) — 0.015 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.015419 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | VNPS PD7 - Pump 2 man/sop. MARS PD7 - Pump 2 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039466 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NMVCBA - Placed back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054982 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | VNPS - Deactivated duty and switched from VNPS PD7 to MAPS PD7 as RHRSTR is low 20:49 - Placed pump 1 man/off at MAPS PD7 and Placed pump 2 at VNPS PD7 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045243 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHMCH7 - PAC Communication Failure alarm came in. Checked site. Trending had stopped at approximately 16:22. Checked Alectra Power which indicated a power outage still on going. ETA of restoration is approximately 19:00-21:00. Called Ian W. who informed that this PAC alarm came in due to the UPS on site running put. Ian informed that even after restoration, the alarm can be disregarded until tomorrow as this is a meter chamber #CONSULT | FLAG | stage2_low_confidence | 0.031798 | ML: above threshold (no LLM available) — 0.032 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.031798 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NMW136 - Alex B finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039987 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | GWTP - Jack P working on fluoride system. Disregard alarms for the duration of the work. | FLAG | stage2_low_confidence | 0.0092831 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0092831 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | AURSBS, Donald M on site, working on chemical analyzers and chemical pumps and dosing systems, testing leak alarms QVSSSC, Rick L/Parth P on site doing annual calibrations | FLAG | stage2_low_confidence | 0.014298 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.014298 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | STW3- Influent/Effluent Free Chlorine Hi Alarm. Adjusted chlorinator 1 dosing factor back down to 260% proposed setpoint. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00705 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | KCETDS- Combined Chlorine Lo Alarm. Analyzer back to normal next reading. Cleared alarm | FLAG | stage2_low_confidence | 0.0075663 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075663 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | ARPS, Hwy50 Total Cl2 Value, Residual had a bit of a dip but then recovered, Peter from OCWA called, confirm that everything is fine on their end, the slug was pushed through, most likely caused by putting the system back to normal operation | FLAG | stage2_low_confidence | 0.011202 | ML: above threshold (no LLM available) — 0.011 |  | 0.011202 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | STW12, STW3 - Placed to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041945 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | VNRSKS - Placed all pumps at VNPS PD7 man/off and placed pumps 1,2,3 at MAPS PD7 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055835 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | AUW14- Placed wells back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043099 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | BVPS - Activate duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040641 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MAPS PD7 - Dan B working on Pump 4. Will run pump 4 for test. VNPS PD7 Man/stopped Pump 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056158 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | MARS - Request TO (Zhoran) to go back to regular flow KCETDS - PAC communication failure. Alarm cleared quickly | FLAG | stage2_low_confidence | 0.014027 | ML: above threshold (no LLM available) — 0.014 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.014027 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMW136- Alex B on site to work on Cl2 and NTU analyzers as well as test Cl2 leak detection and valve work | FLAG | stage2_low_confidence | 0.0089276 | ML: above threshold (no LLM available) — 0.009 | leak [infrastructure] | 0.0089276 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | GWTP, ZW7 Neutralization Exceeded Dur Alarm and Tank Hi alarm, notified Joe M, he will look into it consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.004486 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | HLW1- Treated Free Chlorine Hi Alarm. Rotated Ammonia Pumps so that pump 2 in duty 1. Will Monitor. 23:02- Value went to normal range. Cleared alarm. Placed Ammonia Pump 1 into manual and will email West Ops | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070895 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | HLW2- Ammonia Pump 1 Fault Alarm. Ammonia Pump 2 took over in duty 1. Cleared alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMTKKC - Jason G testing flood alarm and performing chlorine and ammonia systems maintenance. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | MARS - Cell 1 Lo level alarm came in. Called Toronto Water (Zoran) and requested additional flow, as per interim procedure | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070832 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | Carter D Signing In, -6D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041513 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | QVW12, Artour L on site with contractors, will be testing generator alarms on site with the contractors | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0070586 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | NMW12 - Influent Free Chlorine Hi and HiHi alarms came in. After 7 mins, levels came down to optimal range and alarms cleared | FLAG | stage2_low_confidence | 0.0083313 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0083313 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | VNETFD - Tower low level alarm. Checked site, tower level is below duty start. The duty is active but flow from Toronto is not adequate to overcome system demand. Contacted Toronto Water who activated a pump to boost flow to the East Woodbridge PD4 West area. The tower is still draining however the outlet flow is greatly reduced, and the tower will fill once evening demand eases. | FLAG | stage2_low_confidence | 0.044536 | ML: above threshold (no LLM available) — 0.045 | oos [equipment_failure]; alarm [control_system] | 0.044536 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040295 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | MARS - Request TO (Mehdi) for max flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057737 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | VNPS PD7- Placed P2/3 in auto MAPS PD7- Placed P1-4 in man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040595 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | NBW2- Dave T onsite for work orders including silicate system, Cl system, Cl analyzers, turbidimeter, and Cl leak detection test. | FLAG | stage2_low_confidence | 0.018059 | ML: above threshold (no LLM available) — 0.018 | work order [maintenance_action]; leak [infrastructure] | 0.018059 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | NMVCBA- Placed valve manual 40L/s 00:52- Placed valve back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035042 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | ARPS- Airport Rd Discharge Flow LoLo MARS- Called Toronto (Mehdi) to decrease flow to Maple MKRSEM- Called Toronto (Mehdi) to turn off pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063992 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | MAPS/JFRS- Reverted Maple to Jefferson Feed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059146 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | VNMCBA, RHMCMD, MCMCCW,MKMCSA - Power blip, all alarms cleared. | FLAG | stage2_low_confidence | 0.0082363 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0082363 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MARS- Dave T on site for Cl2 analyzer maintenance, JHS inspections and to test flood alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMTKKC - Header ammonia LoLo, outlet total amonia LoLo alarms, Historian heartbeat alarm, called Jason G( running gen at NMPSKC). Jason G will check. NMW12 - interlocked on NMTKKC to NMW12 commfail. Alarm cleared. NMTKKC - Historian Heartbeat alarm. Notified Ian W, he will check. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | NMVCBA- Placed valve in manual 20L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043223 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NBW3- Influent Free Chlorine LoLo Alarm. Interlocked well on startup. Value recovered and cleared alarm. Well started back up in duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071993 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NMETIB- Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053728 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | Adam Button signing in -5C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004176 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | YWS + NWYS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050034 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW12 - Man/stopped well 1 pump, Artour L on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043404 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCETDS-Outlet total Cl2 res lolo alarm came in. Looks like analyzer dropped out but recovered after one reading alarm cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071666 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | AUETFC- Donald M called back tie valve is normally closed. Cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071646 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | AUETAD, Donald M on site, Testing temp and doing Cl2 analyzer main | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046589 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMW136, Influent Free Cl2 hihi, contacted Tyler Z who was talking to Ben H. Tyler Z will be back flushing the site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061972 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | SHTP- Jake M on site for step test | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053224 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | ARPS- Discharge flow hi alarm came in. Called Peel spoke with Jason. Peel tehcnicians are working on chemical quills causing flow meter readings as all pumps are currently off. Jason Notified they will be running a pump later today as per RFS | FLAG | stage2_low_confidence | 0.015947 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system] | 0.015947 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | STW3, Influent Free Cl2 hi, Adjusted dosing factor from 280 to 260, will continue to monitor site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005705 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | STW3- Historian heartbeat alarm came in interlocking well. Notified Chris S. Will take a look on SCADA | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0062832 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AURSBS - Ben H. is on site for work orders. This includes testing the eyewash. Ben directed to disregard all alarms until work is complete | FLAG | stage2_low_confidence | 0.020214 | ML: above threshold (no LLM available) — 0.02 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.020214 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NBW5- Influent Free CL2 Lo Alarm. Value recovered. Effluent Free CL2D Lo Alarm and Effluent Free Chlorine LoLo Switch alarm came in shortly after. Well interlocked. Notified Tim H. He will attend site. Tim H requested to change Influent Lo Alarm from 1.0 to 1.5 and Effluent Lo Alarm from 0.65 to 1.0 16:54- Tim H finished onsite. He will leave well man/off for the weekend. Requested a call if needed to run in emergency. W11679721 CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system] | emergency [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | AUPSOH- Jerry Z on site to run generator and test hi lo temp alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068638 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | ANW23 - Res inlet free chlorine Lolo alarm, quick dip, duty recently activated, Wells interlocked. Cleared alarms, wells 2&3 pumps restarted, Res free inlet chlorine residual normal. | FLAG | stage2_low_confidence | 0.008993 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.008993 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NMW15, Eric S on site, working on influent analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043363 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | KCPSDS - PAC Communication alarm came in and the value turned normal. Trending is okay | FLAG | stage2_low_confidence | 0.0078967 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0078967 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MMW1 - Well 8 and Well 13 hi level alarms came in. Likely due to the ongoing power issues in Richmond Hill/Vaughan. Checked site. Noticed all the wells man/off. Placed well 13 and well 8 man/on. Confirmed with Rob P. who informed well 13 should be opened at 21% and well 8 open at 42% #CONSULT | FLAG | stage2_low_confidence | 0.012791 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012791 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NRETCR - Deactivated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041464 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | VNPS- Utility source 1 not available came in. Notified Tim H. Tim H req Satnam M to call him for a consult. Notified Satnam M. Will update ROC KCETDS- Yash S changing switch | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066613 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMW12 - Influent Free Chlorine HiHi alarm came in. Checked site. Wells just activated 20:33 - Influent levels are back to optimal range and alarms cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0047509 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | SHETCS - Jacob M running generator, testing Hi/Low temp alarms, cleaning chlorine analyzers, inspecting hypo system. | FLAG | stage2_low_confidence | 0.010463 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010463 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | KCETFS - David T running generator, testing Hi/Low level and temp alarms, cleaning chlore analyzers. | FLAG | stage2_low_confidence | 0.0097319 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0097319 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | STETBR- Free Cl2 lo alarm came in. Notified Joe M. Will attend site to check MTETNL- Phil D on site to work on Cl2 analyzer. Directed to disregard alarms until done | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0065706 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -4C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MKRSEM - PAC control panel power fail alarm. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067606 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | MKPSSA, Travis W on site, Running generator/Testing pumps and testing flood alarms. notified Toronto of this work as well, they shouldn't be impacted | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | SHETCS - Activated Duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041251 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AUW14- Yash S done on site. Placed wells 2/3 in man/on. Trends okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046756 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AUW14 - Joe D. called to inform that Yash S. is still working on cable repairs and it may cause a communication loss. Joe will place well 2/3 man/off until the work is complete | FLAG | stage2_low_confidence | 0.014852 | ML: above threshold (no LLM available) — 0.015 | repair [maintenance_action] | 0.014852 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BVPS - Danielle Z leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055445 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to one MAPS and one VNPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064114 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather -12C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043332 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | HLW2 - Ammonia Pump 1 fault alarm, Cole W will attend site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NMW15, Placed back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041302 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | AUETFC, Joe D finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051866 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | MKRSEM - Request Mehdi (TO) to drop both pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059897 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MTW3 - Turbidity Fault alarm. Checked site, turbidity trending shows a small increase around the time of the fault but no abnormal trend lines. Attempted to reset alarm, will not reset. Placed well in manual/off. System has one well available to fill tower. Activated duty to determine if one well pump is sufficient. Placed well 3 manual/off. | FLAG | stage2_low_confidence | 0.037165 | ML: above threshold (no LLM available) — 0.037 | fault [equipment_failure]; alarm [control_system] | 0.037165 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | NMTKKC - Ammonia pump 1 uncommanded stop , Hypo pump 3 uncommanded stop alarms, PAC control panel door open alarm- Notified Jerry z and Ben H. As per Ben H- Ian W working on site. Called Ian W and Jason G, no response. Will call later. 13:15 Chris S working on UPS, Notified Jason G about outstanding alarms. Was able to clear alarms. | FLAG | stage2_low_confidence | 0.010296 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010296 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | NMETIB, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040018 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: 1C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | AUW57 - Influent Free Chlorine LoLo Switch alarm came in. Checked site. Influent level did not recover. Called Joe D. who will head to site. CMU5 Created W11664471 15:10 - Joe D. called back to inform that the chlorine cylinders were switching over and the regulator dropped. Joe D. will stay on site to monitor #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.007016 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | MKRSEM- Called Toronto (Mehdi) and requested pumps off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061833 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | STW12- Placed well 1 back into auto STW3- Placed well back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041937 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | KCETDS - Kyle R on site to complete work orders including a heat trace inspection, sump pump inspection and damper and exhaust fan inspections. | FLAG | stage2_low_confidence | 0.015822 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action] | 0.015822 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BVPS- Dan Z on site to work on analyzers and testing flood alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | VNRSKS - Deactivated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041452 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | MMW1, Well 8/13 hi alarm, notified Tyler Z, directed to place wells back to manual/on as a power outage occurred and knocked them man/off RHAMF1, Fan 1/2 Faulted, Notified Jimmy from NAC, he will send his team over to the site | FLAG | stage2_low_confidence | 0.014765 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] | 0.014765 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AURSBS- Cl2 valve 1/2 failed to open alarms came in. Reset | FLAG | stage2_low_confidence | 0.011568 | ML: above threshold (no LLM available) — 0.012 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011568 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | ARPS - Dereck from Peel informed they will rotate pump 1out and put pump 2 in auto duty 1. BLW3 - Duty running with well 3 active, well 3 percent declined lolo. Noticed on trend it occurs now with well 3 running reading goes into negative value | FLAG | stage2_low_confidence | 0.0095866 | ML: above threshold (no LLM available) — 0.01 |  | 0.0095866 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | STW12 - Well 1 running place man/on STW3 - Well 3 running, place in man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042846 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | MKRSEM - Request TO (Paul) to run 2 pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044544 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BVPS- Dan Z on site inquiring if D1 can be activated at RHRSTR as power has stabilized. Instrumentation working on chlorination system on site at RHRSTR/VNPS. Notified Dan Z D1 should not be activated until they are done | FLAG | stage2_low_confidence | 0.0092819 | ML: above threshold (no LLM available) — 0.009 |  | 0.0092819 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS+NYWS normal ARPS- Martin from Peel called to notify ROC that they will be transferring from P5 to P6 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047017 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | QVW12 - William M on site for turbidity meter maintenance and chlorine leak test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | NMVCBA - Placed valve man/open at 30 L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044121 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | STETBR- Joe M notified ROC that instrumentation was not able to attend site today and the Cl2 analyzer will be offline all night. Confirmed Joe M took a grab sample while attending earlier. | FLAG | stage2_low_confidence | 0.0085373 | ML: above threshold (no LLM available) — 0.009 |  | 0.0085373 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | Possible Main Break, Queensway and Bessborough, Abdula from Dispatched called saying there is a possible main break north of the intersection, after checking all pipes, the pipes belong to Georgina. Abdula informed the Georgina of their main break | FLAG | stage2_low_confidence | 0.014409 | ML: above threshold (no LLM available) — 0.014 |  | 0.014409 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | MAPS - Artour L. is on site for asset tagging | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055618 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | NMTKKC - Eyewash Flow alarms came in. Checked site. Jason G. on site flushing eyewash stations | FLAG | stage2_low_confidence | 0.0089039 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0089039 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | Ethan U signing in Weather -4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | NBW3- Influent free lolo switch alarm interlocked well. Continued to monitor reset after influent free Cl2 recovered. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069127 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | YWS + NYWS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038034 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | AUW14 - Placed pumps 3&4 and AUW5 pump back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046956 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | BLW3 - Patrick F finished at site. Leaving chlorinator 1 OOS for the weekend, disregard well 3 percent decline alarm. Will bring it up to team start of week | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | RHRSTR- Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053751 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | BVPS - Pump 1 & 4 uncmd stop again. Able to clear and reset after some time pumps gradually came back. Sudden drop caused VNPSCD chlorine system failure to occur with hihi post-inj chlorine total/combined VNPSCD - Chlorine system failure, combined/total post-inj hihi after BVPS sudden stop. Informed Jerry Z RHPSPA - suction pressure hihi, pump 4 inhibited as duty 1, disch valve partially closed. Rotated pump 3 to duty 1. | FLAG | stage2_low_confidence | 0.033032 | ML: above threshold (no LLM available) — 0.033 | failure [equipment_failure] | 0.033032 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW3 and STW1 back to auto as per inteirm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060694 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | MTW3 - Chlorine gas leak, scrubber running. Informed Patrick F, will head to site CMU = 11670914 | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; leak [infrastructure] | gas leak [critical]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | MKRSEM - Request TO (Brent) to run 2 pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044736 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | Connor Smith signing in -2 Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | AURSBS- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053256 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | QVW12- William M working on chlorine analyzers. Disregard related alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0064984 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | MAPS PD7, Placed pumps 2/3 auto VNPS PD7, Placed pumps 2/3 back to man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035841 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | SHTP, Deactivated D1 to help recover the res MKRSEM, Notified Toronto operator Zoran to start filling the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040852 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NRETCR, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040025 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MARS - Approaching high level. Called Toronto Water and requested they drop one pump. RHAMF - Generator running status alarm. Richmond Hill is suffering from power failures. Already contacted NAC regarding the VFD pump faults on site. Generator is on but the ATS is pointing to utility hydro. | FLAG | stage2_low_confidence | 0.040795 | ML: above threshold (no LLM available) — 0.041 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; pump fault [infrastructure] | 0.040795 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MMW1 - Well 8 and well 13 hi level alarms. Wells were knocked out during the most recent power blip in Richmond Hill. Activated well 8 and well 13 pumps in manual. | FLAG | stage2_low_confidence | 0.010072 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010072 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMPSKC - Jason G running generator, will attend NMTKKC re-chlor building after. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069453 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHPSPA- Placed all pumps in manual and started 1/2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046257 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MAPS PD7- Tim H on site to trouble shoot PD7 pump lo switch alarms issues from yesterday. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0066684 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | KSTP - CO2 adjusted pH lolo, status went to normal as reading went back within range Settl water cond level lolo. Found it dropped. Informed Patrick F, as both filters were in production at time. During call appears both fitlers changed to off. Patrick F will take a look Consult | FLAG | stage2_low_confidence | 0.0092662 | ML: above threshold (no LLM available) — 0.009 |  | 0.0092662 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | NMVCBA- Placed valve in manual 20L/s 23:58- Placed back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034568 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | VNRSKS to COTFA Comm Alarm COTFA to MARS Comm Fail COTFA to RHRSWA Comm Fail COTFA to ROYKS Comm Fail COTFA to VNETAG Comm Fail COTFA to VNPS7 Comm Fail COTFA to VNPS8 Comm Fail JFPS to COTFA Comm Fail NRETBR to COTFA Comm Fail RHPSWA to COTFA Comm Fail All alarms Cleared | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHPSPA- Activated and rotated duty and placed pumps back in auto. SHTP/ SHETCS- Power fail on both site. Notified Jacob M will check SCADA and reset alarms outstanding STPSTL- Joe M on site to run generator | FLAG | stage2_low_confidence | 0.01018 | ML: above threshold (no LLM available) — 0.01 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.01018 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | RHRSTR- Deactivate duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053649 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | ARPS- David from Peel notified ROC they are starting 1 pump in auto in pressure mode 12:40- ARPS- Peel ammonia analyzer a alarm came in. Called Peel about alarm spoke to Masoud. They are making adjustments on their end and trying to get the residuals to stabilize before making anymore adjustments. Masoud confirmed they have done the calculations themselves to ensure proper dosing and will have ops call back within a half hour with update. 13:00-ARPS- David from Peel called back. residuals stabilized cleared alarms and P5 running in auto | FLAG | stage2_low_confidence | 0.027586 | ML: above threshold (no LLM available) — 0.028 | alarm [control_system]; alarms [control_system] | 0.027586 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | HLW1 - Treated free chlorine hi, wells just activated, monitored site, well free reading dropped back down | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059368 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | MAPS PD7 - Pumps 2&3 man/off VNPS PD7 - Pumps 2&3 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040177 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | JFPS - Assigned P4 to Duty 1 and disabled Duty rotation. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047777 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | YWS + NYWS Normal NMVCBA - Adjusted flow setpoint from 40L/s to 80L/s to maintain NMETIB/NMETHW offset. NMVCIB - Adjusted flow setpoint from 80L/s to 40L/s to maintain NMETIB/NMETHW offset. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041673 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | NBW3 - Influent free chlorine lolo alarm. Checked site, well just activated to fill system. Trending shows the influent free chlorine dipped on well start. Rotated chlorine pump duty and waited for the influent free chlorine reading to rebound. Then placed well in auto and cleared alarms. Monitored start up. | FLAG | stage2_low_confidence | 0.016326 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system]; alarms [control_system] | 0.016326 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | VNPSCD - Pre - injection total chlorine and combined chlorine lolo. Checked site, chemical system is currently active as RHRSTR is filling. trending shows a sudden drop of the total and combined chlorine values. Contacted Jerry Z who directed to disable to chemical system and will attend site to check the analyzer. Created CMU5#W11664539 23:28 - VNPSCD - Jerry Z called to inform he needs the assistance of on call instrumentation. Called Parth P to inform, Parth will attend site to assist Jerry. Created CMU5#W11664549 #consult #CMU5 | FLAG | stage2_low_confidence | 0.01904 | ML: above threshold (no LLM available) — 0.019 |  | 0.01904 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | VNPSCD - Parth P on site and requested that the duty be deactivated. Deactivated duty 1 for RHRSTR. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054335 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | VNETFD- Site Hydro Power Failure Alarm, Isolation Valve General Alarm. Alarms cleared KLMCHR- Site Power Failure Alarm. Alarm cleared | FLAG | stage2_low_confidence | 0.015375 | ML: above threshold (no LLM available) — 0.015 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.015375 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | VNETFD- Control Panel Power Failure Alarm, Isolation Valve General Alarm. Alarms cleared. | FLAG | stage2_low_confidence | 0.015111 | ML: above threshold (no LLM available) — 0.015 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.015111 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | MAPS PD7- Placed P2/3 in man/off VNPS PD7- Placed P2/3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040649 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | QVW34, Will M is on site, testing Cl2 analyzers/leak/temp alarms, directed to disregard alarms | FLAG | stage2_low_confidence | 0.010868 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.010868 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STPSMR - Travis W working on site, deactivating duty , testing chlorine leak alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | GWTP - Patrick F backwashing GAC3. NRETBR - Jason G cleaning chlorine analyzers, testing temp alarms and eyewash alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0040255 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | MKRSEM- Called Toronto water (Poulin) requested stop filling res. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064858 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | Carter D Signing In, -3D/Snowing YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030615 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather -9C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | ARPS - David from OCWA called, rotating pumps from Pump 5 to Pump 6. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050525 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | 13:50 BLW12 - Kyle C restarting OIT, Disregard Historian Heartbeat alarm. 14:14 Kyle C completed work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0045348 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMTKKC - Jason G and Ian W working on site, requested Man/off all chemical pumps. Disregard alarms. | FLAG | stage2_low_confidence | 0.0091185 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0091185 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | KSTP- Eric S onsite for turbidimeter troubleshooting. 14:24- Finished onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003619 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | KCETDS- Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040054 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | AUW57- John D rebooting OIT. Disregard Heartbeat Alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051928 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | VNPS PD7 - Pumps 2&3 to auto. MAPS PD7 - Pumps 1&2 man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040164 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHRSWA- Pac Panel died on site lossing comms. RHPSPA interlocked due to comm fail/ Notified Tim H. Time H req consult with Ian W to troubleshoot. Notified Ian W to call Tim H. MKRSMR- Called Metro spoke with Pouria activated D1 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | KCETDS- Outlet Total CL2 Res LoLo Alarm. Recovered next reading. Cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055588 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | ARPS - Peel informed they are rotating pump 4 off and placing pump 5 auto duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053697 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | QVW12, Influent Free Cl2 hihi alarm, abnormal spike occurred. After 1 reading, residual came back down to normal levels | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069613 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | QVW34, Ben H is heading to site to reset the wells CMU: W11674030 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003631 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NMW136 - Alex B and Christian B on site, working on silicate and ammonia systems, disregard alarms for the duration of the work. | FLAG | stage2_low_confidence | 0.0079675 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0079675 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | RHRSTR, MKRSMR, MKRSEM - not trending. Notified Chris S. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060806 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMETHW - Deactivate duty 1 as Ivsbridge remains active and keep offset | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050739 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMETIB- Parth P done on site Cl2 analyzer reading properly | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044762 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | GWTP- Patrick F on site to test chemical leak alarms and flood alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | flood [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMW15 - PAC commfail. PCS working on NMETYS to NMW15 communication as per Alex B. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | ANW23 - Pre-Inj free chlorine lo. Noticed trend dropping in reading slowly. Informed Cole W, will head to site CMU = W11664823 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005737 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | BVPS 1 & 4 uncmd stop came back in with power blip in area. Able to clear alarm and pumps were able to gradually come back in service JFRS - VC UPS ATS source and source S2 line not okay related alarms came back in. RES/PS UPS ATS source 2. RES CP PWR failure. Alarms able to clear but pumps remain unable to run RHPSWA - Control panel power failure RHPSPA - Suction pressure hihi, able to clear after spike VNVCIA - PAC control panel power failure, Chris S called back informing AUMCBR will remain outstanding over night. VNVCIA is on battery power and will lose comms within 4 hours as power failure remains outstanding. Infomred Harsh P as well of scenario, will leave for morning Consult | FLAG | stage2_low_confidence | 0.075031 | ML: above threshold (no LLM available) — 0.075 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.075031 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | SHTP- Changed duty setpoints from 15/45% to 30/80% Interim Procedure | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034695 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MKRSMR- Called Metro spoke with Peter to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065477 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | McCowan Road and 14th Avenue - Dwayne L. called to inform that he will be responding to a potential watermain break and requested a CMU5. Harsh P. and Peter T. will also be responding. CMU5 Created W11664363 #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.007202 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | MARS- Called Toronto (Mehdi) and requested increase flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062362 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | VNPS- Ric L and Parth P onsite for annual calibrations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062275 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | AUW14, Treated Free Cl2 hihi alarm, trends show an abnormal spike occurred, if recovery doesn't happen within 2 readings, will take further action | FLAG | stage2_low_confidence | 0.0079493 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079493 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | GWTP- ZW3 memb tank level hi alarm came in. Notified Patrick F. Directed to disregard as tank should drain after a few mins but call for hihi #consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065824 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | VNRSKS- Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040006 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | MKRSEM- Called Toronto (Mehdi) and requested pumps on. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061774 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | Richmond Hill - Followed up with Joanna from Alectra regarding power blips in area. Still no update of restoration as crew continues to work on resolving issue | FLAG | stage2_low_confidence | 0.010115 | ML: above threshold (no LLM available) — 0.01 |  | 0.010115 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | SHTP - Reservoir level hi alarm. Activated SHETCS duty 1 to draw down the reservoir. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059856 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Paul) and requested they deactivate the pumps pushing flow to MKRSEM. MTETNL - Site to site communications fail with MTW12. The alarmn ahs interlocked MTW2 which was active when the alarm triggered. Placed MTW2 in manual to prevent immediate start up when alarm clears. Alarms reset. Will place the well in auto in ten minutes. | FLAG | stage2_low_confidence | 0.014791 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system]; alarms [control_system] | 0.014791 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | KSTP - Raw water turbidity fault alarm. Checked site, plant is not active at the moment. No flow being generated by low lift pumps. Disregard alarm as per the shift report. | FLAG | stage2_low_confidence | 0.022292 | ML: above threshold (no LLM available) — 0.022 | fault [equipment_failure]; alarm [control_system] | 0.022292 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMTKKC - Sean P on site to cut power to the re-chlor facility on site to complete maintenance on the header system. | FLAG | stage2_low_confidence | 0.0077656 | ML: above threshold (no LLM available) — 0.008 |  | 0.0077656 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | AURSBS - Activated duty 1 to draw down MARS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044915 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | SHTP- Placed well 2 in man/off as per interim. Confirmed with Tim H before shutting down | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054813 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | ARPS, David from OCWA called, he is switching their D1 pump from pump 4 to pump 5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053639 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMW12- Christian B and Alex B is on site to work on silicate system and backflush VNPS- Rick L and Parth P done on site STETBR- Joe M was not able to get analyzer back online and Instrumentation will be attending site to trouble shoot | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071058 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | SHTP- Treated Water Turbidity Fault. Notified Cole W. Can disregard for the night. Requested a call if it stops trending. CONSULT | FLAG | stage2_low_confidence | 0.0093481 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure] | 0.0093481 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | AUMCBR - PAC communication failure. Loss of trends high priority. Informed Chris S who will look into it CMU = 11667808 | FLAG | stage2_low_confidence | 0.012823 | ML: above threshold (no LLM available) — 0.013 | failure [equipment_failure]; communication failure [control_system] | 0.012823 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BLETNL - Activate duty 1 YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029731 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STW12 - Place well 1 back in auto STW3 - Place well 3 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041998 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | BLW12 - Phil D cleaning chlorine analyzers and turbidity meter, cleaning injection points and running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061369 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | SHETCS, Kevin W doing a network switch, once tower hits D1 stop, he will do his work. Notified Darrick Simm will attend site if issues arise. 12:08, Kevin W is finished his work 12:09, Adjusted D1 start from 45% to 60% and D1 stop from 15 to 20% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045225 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | ARPS - Airport rd pressure LoLo alarm, confirmed all pumps Local/off for ARPS shutdown. | FLAG | stage2_low_confidence | 0.0080139 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080139 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | STPSMR- Travis W on site for Cl2 analyzer maintenance | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043758 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | JFRS - VC UPS ATS source S2 (line, UPS ATS source S2, WPS Gen xfer switch hydro power. Alarm status switched to normal and alarms cleared. No pumps running at the time. | FLAG | stage2_low_confidence | 0.0085753 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0085753 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NBW5- Turbidity hi outstanding. Rotated from silicate P 1 to silicate P2. Will monitor for improvement Placed silicate P 1 in man/off and disabled all stop duty rotation | FLAG | stage2_low_confidence | 0.0079862 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079862 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | ARPS - David from OCWA called, rotating pumps from Pump 6 to Pump 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050525 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MKRSEM, Notified Toronto operator Zoran to start filling the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063119 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMTKKC - Ammonia pump 1failed to start, notified Jason G. He is on site, will check. | FLAG | stage2_low_confidence | 0.0090458 | ML: above threshold (no LLM available) — 0.009 | failed [equipment_failure] | 0.0090458 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | Ethan U signing in Weather 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | JFRS - Jerry Z finished at site and able to reset pumps. GWTP - Train 5 membrane pressure lo, value went back to normal and cleared upon acknowledging alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066867 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | QVW34- Treated total and / combined Cl2 lo alarms came in. Wells not active Checked trends looks like analyzer dropped out. Continued to monitor and cleared alarms as residuals recovered after 6 mins no water directed to users | FLAG | stage2_low_confidence | 0.012746 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012746 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | AUETFC- Tie valve uncommanded close alarm came in. Notified Donald M. Will investigate and update ROC | FLAG | stage2_low_confidence | 0.0082637 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0082637 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | STW12- Comm alarm to STETTL. Trends okay cleared alarm ANW23- RSVR inlet free Cl2 lolo alarm came in. Checked trends. Residual dropped suddenly. Reset alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.006942 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNPS PD7, Placed pumps 2/3 man/on VNPS PD8, Placed pumps 2/3 man/on Lee F Preforming Pump vibration testing on pumps 2/3 at VNPS PD7/PD8 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | vibration [equipment_failure] | 0.006062 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | YWS + NYWS Normal MKRSEM - Called Toronto Water (Paul) and requested they deactivate the pumps pushing flow to MKRSEM. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056543 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | AURSBS - Activated duty 1 to draw down MARS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044915 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -15C and sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044737 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | VNP7 - Man/stop pupmp 2 MAP7 - Place pump 2 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040022 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | SUSP- Satnam M done on site. Notified Satnam M barscreen and vortex/ dewatering screws are not in auto. Will place back in auto 11:56- Satnam M confirmed with Ops headworks is normally in local but runs in auto **WRONG BOOK** | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055707 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | JFRS - Followed up with Alectra as constant power interruption occur. Nothing reported on the outage map but they confirmed they are aware of the situation across Richmond Hill and Vaughan area being impacted with power loss and interruptions. They have no further updates on estimated time of restoration and sounds like there team is still searching for cause of these faults as they believe these interruptions could be cause from tree contact or wildlife. With them actively investigating they have no further updates at this time. Informed Jerry Z of situation and will remain on site for some time to see any further issues before running generator | FLAG | stage2_low_confidence | 0.15721 | ML: above threshold (no LLM available) — 0.157 | fault [equipment_failure] | 0.15721 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | ANW23- Deactivated Duty and reactivated to get wells to start up. MARS- Called Metro spoke with Mehdi to reduce flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052141 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | NMETIB- Deactivated D1 to offset from NMETHW as per shift report AUPSRR- Post injection free Cl2 hihi alarm came in. Reset as trends recovered after 3 mins | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068633 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | AUW57- turbidity hihi alarms outstanding. Turbidity recovered. Cleared alarms and will continue to monitor well run | FLAG | stage2_low_confidence | 0.007619 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.007619 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMTKKC- Sean P done on site site back to normal and all alarms cleared | FLAG | stage2_low_confidence | 0.0076858 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0076858 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | STPSTL - Dan Z. called and directed to place the duty start for STETBR back to 60% as the deep cycling of the tower is complete. Dan also directed to place the low level alarm at STETBR back to 60 % | FLAG | stage2_low_confidence | 0.010345 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010345 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | NBW5 - Silicate Pump 1 failed to stop alarm came in. Checked site. Well is running. Silicate pump 2 rotated to duty 1 but silicate pump 1 was still running. Called Jordan B. who is not on site but informed this is okay | FLAG | stage2_low_confidence | 0.020111 | ML: above threshold (no LLM available) — 0.02 | failed [equipment_failure]; alarm [control_system] | 0.020111 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | VNPS- Tim H confirmed Line 1 became available alarms cleared on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0060455 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | SHTP, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039621 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | yws + nyws normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | KCETDS, Activated D! | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052961 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | VNETFD- Deactivated D1 to help the tower cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004521 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | AUW5 - Joe D requested to place well 5 pump to Duty 1 and leave running in manual mode for now. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057386 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MARS- Called Metro spoke with Poulan to increase flow to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065422 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | HLW2- Stephen B heading to site for workorders | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004514 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MARS- Called Metro spoke with Zorhan to reduce flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006111 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMW136, Placed well 16 man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041899 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | AUW14/5, Placed wells 2/3/5 in man/off so more water can be taken from AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005219 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | VNRSKS - Switched feed from VNPS PD7 to MAPS PD7 In preparation to chem scan calibration at RHRSTR/VNPS re-chlor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061757 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | Carter D Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | SHETCS - Common in/out Total chlorine LoLo alarm, Jacob M working on Hypo system, no water to analyzers, Jacob M collected grab sample. 14:05 Jacob M called Eric S. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060119 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NMPSKC- Aaron Carlos from Networking is done work on site QVW12- jerry Z on site to work on treated total Cl2 analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049262 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MMW1- Power blip, Well 8 and well 13 High level. All wells interlocked. Cleared alarms and restarted Well 13 pump @ 20% and well 8 @ 41%. Verified with Rob P. High level alarms cleared. | FLAG | stage2_low_confidence | 0.010695 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010695 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | GWTP- Train two TMP lo. Cleared upon acknowledgement YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053502 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | VNRSKS - Deactivated duty due to low levels at MARS YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045093 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | STW12 - Place well 1 man/on STW3 - Place well 3 man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039297 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | SHTP, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040013 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | STW12/3- Placed P2/3 in auto as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044611 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | SHETCS - Eric S leaving site. Hypo Pump 2 man/off, can run if needed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050518 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NBW3- Influent free Cl2 lolo switch alarm came in while starting up in schedule mode interlocking wells. Waited for Influent free Cl2 residual to recover and reset alarms | FLAG | stage2_low_confidence | 0.008849 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.008849 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KSETDP - Dan Z. called to inform that the outlet chlorine analyzer is reading system water and tower remains isolated. Dan directed to disregard low chlorine alarms after hours | FLAG | stage2_low_confidence | 0.013805 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system]; alarms [control_system] | 0.013805 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | SHTP - Yash S completed Network switch replacement, all alarms cleared. Jacob M will start the plant. | FLAG | stage2_low_confidence | 0.0098682 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0098682 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | RHRSTR- Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040026 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | QVW34- Tyler ZJ onsite with William M for generator maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004918 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | AUW14, AUW5 - Placed back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042904 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMTKKC - Historian Heartbeat alarm. Notified Ian W, he is on site. Jason G on site, monitoring. | FLAG | stage2_low_confidence | 0.0075456 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075456 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | Adam Button signing in -6C Snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042225 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | JFPS- Power fail on site generator running RHRSWA- Power fail on site RHPSPA- Power failure on site power blip pumps running okay BVPS- P1/3 uncomammnded stop alarm. P1 discharge valve failed to open. Deactivated D1 reset alarms Will continue to monitor power fails on other sites | FLAG | stage2_low_confidence | 0.020483 | ML: above threshold (no LLM available) — 0.02 | failed [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system]; valve failed [infrastructure] | 0.020483 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RMMCMD- Rob P notified ROC that there is no response at this time as there is still no power to site. Once power is restored faults can be reset. | FLAG | stage2_low_confidence | 0.016401 | ML: above threshold (no LLM available) — 0.016 | fault [equipment_failure] | 0.016401 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | KSTP- Fin Water Fluoride Res Fault, Fin Water Tot CL2 Res Fault Alarms. Disregard as per SCADA Report. | FLAG | stage2_low_confidence | 0.012263 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.012263 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | STW12, STW3 - Man/start for STETBR fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045302 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MTW3, Chlorinator 1 Vacuum Switch, Patrick F on site working on the Cl2 leak | FLAG | stage2_low_confidence | 0.0077143 | ML: above threshold (no LLM available) — 0.008 | leak [infrastructure] | 0.0077143 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | GWTP, ZW6 Recovery over extended, notified Patrick F, as calling, the alarm cleared, Patrick F directed to disregard at this time however if it start coming in multiple times, he would like a call | FLAG | stage2_low_confidence | 0.0098119 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0098119 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MAPS PD7 - Pump 4 off for the night as per Tim H. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046499 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | RHRSTR, Deactivated D1 NRETCR, Deactivated D1 JFRS, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0023808 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | ARPS, Peter from OCWA called, Peter confirmed OCWA will not be running any pumps tonight | FLAG | stage2_low_confidence | 0.0072634 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072634 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | STETBR- Tower level lo STW12/3- Placed well 2/3 in man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042258 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NBW3- influent free Cl2 lolo alarm came in interlocking well on start up. Residuals recovered reset alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0065829 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | STPSMR - Travis W. is on site and will be completing a hard reset on the effluent analyzer. Travis will be stopping the pumps | FLAG | stage2_low_confidence | 0.0080906 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080906 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCETFS - Control Panel Power Failure alarm came in. Outage reported on hydro one outage map. ETA of restoration is 1900 16:51 - Tim called back to inform that he is finished on site and power has been restored | FLAG | stage2_low_confidence | 0.011097 | ML: above threshold (no LLM available) — 0.011 | failure [equipment_failure]; alarm [control_system] | 0.011097 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | QVW34- Tyler ZJ finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042325 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | QVW34 - Treated combined chlorine hihi alarm. Well pump was running in manual for sampling. Will M was in site. Will contact Will to inform if changes are not observed on SCADA. 13"50 - QVW34 - Will M is on site and managing the situation. | FLAG | stage2_low_confidence | 0.0080568 | ML: above threshold (no LLM available) — 0.008 | scada [control_system]; alarm [control_system] | 0.0080568 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -2C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMVCBA - Placed valve in manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055732 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | VNPSCD - Tim H. is on site with Parth P. and Art P. who will be taking the chem scan offline for about 10-15 mins. 11:25 - Parth P. and Art P. are finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043566 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW34 - Treated Total chlorine Low alarm, Ben H on site monitoring. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051601 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | VNETAG- Yash S working on OIT disregard historian heartbeat alarm until done 11:47-VNETAG- Yash S done working on OIT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.004849 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | BLW3 - Phil D running generator and testing low temp alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053238 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | VNPS - Rick L on site for calibration. Deactivated RHRSTR duty and placed BVPS pumps man/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069364 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | KBPS27 - Benson S cleaning chlorine analyzers, exercising valves, PRV and temp alarms test and health and safety inspection. | FLAG | stage2_low_confidence | 0.0082938 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0082938 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | NMETIB - Activate duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040962 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | KSTP- Jerry Z called and requested CMU5 for Eric S for turbidimeter. W11658745 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032703 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MKETFA - Travis W testing Hi/Lo level and Hi/Lo temp alarms, inspecting and exercising altitude valve, cleaning chlorine analyzers. | FLAG | stage2_low_confidence | 0.011254 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011254 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | KSTP - Raw water turbidity fault alarm. Disregard as per the shift report. | FLAG | stage2_low_confidence | 0.014128 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system] | 0.014128 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | RHPSPA RHMCMD RHRSWA JFPS, AUMCBS RHPSWA VNMCBA - Power blip. Cleared all alarms. | FLAG | stage2_low_confidence | 0.0086371 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0086371 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | STW12, STW3 - placed back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004292 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: 1C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | STW2 / STW3 - Activated these well pumps in manual mode as directed by Joe M. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005256 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | STPSTL- Discharge Flow FWD LoLo Alarm. Pump shut down and Pump 1 went into duty 1. STW12- Placed pump 1 man/on STW3- Placed well man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052846 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NMW12- Silicate Pump 1 Uncommanded Stop Alarm. Silicate Pump 2 took over in duty 1. Cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006124 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | VNPS- Placed PD7 Pump 2 man/off MAPS- Placed PD7 pump 2 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041083 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MARS - Low level alarm, activated RHRSTR Duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005054 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | STW3 - Effluent free chlorine hi alarm. Checked site, influent and effluent values are nigher than normal. Checked the chlorinator dosing setpoints and noted that the dosing setpoint of the active chlorinator has climbed higher than the initial setpoint. Re-applied the initial setpoint and monitored. Tyler ZJ on site to complete a station disconnect. Will see alarms related to generator disconnection. | FLAG | stage2_low_confidence | 0.020925 | ML: above threshold (no LLM available) — 0.021 | alarm [control_system]; alarms [control_system] | 0.020925 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMETHW- Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040398 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | MTW3, Patrick F on site, resetting well 3 and also working on the silicate injection point | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052136 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NMW12, Eric S is on site working on Silicate pump 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043584 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNPS PD7- Placed P3 in man/off and Placed P2/3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047001 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNPSPD7/8 - RHRSTR, Benson S on site, testing health and safety alarms | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0060754 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | NMETIB- Activated D1 at 55% to offset from NMETHW as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00502 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | STW12- Placed Well 1 in man/off and rotated D1 to P2 due to VFD speed fluctuations over past 5 days. Emailed East water team about potential issue | FLAG | stage2_low_confidence | 0.0072263 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072263 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | Ethan U signing in Weather -4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal ARPS - Peel informed they will switch active pump 6 to pump 7 to duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045463 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | NMW12 Silicate pump 1 failed to start. Issue that occurred throughout the weekend. Emailed central team regarding issue. Placed silicate pump 1 man/off | FLAG | stage2_low_confidence | 0.013468 | ML: above threshold (no LLM available) — 0.013 | failed [equipment_failure] | 0.013468 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NMETIB, Deactivated D1 NMVCIB, Reverted flow back to 80L/sec NMVCBA, Reverted flow back to 40L/sec | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0027662 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NMVCBA, Placed valve in manual and set flow to 40L/sec | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047058 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | QVW12 - Jerry Z on site, requested to disregard chlorine room gas leak alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | VNPSCD - Parth P finished his work on the pre-injection chlorine analyzer. Placed the chemical system in auto mode and monitored. Chemical system activated and within five minutes the combined chlorine residual triggered a hihi alarm. Parth P collecting a grab sample. 01:42 - VNPSCD - Grab sample was below the hihi alarm setpoint. When the chemical system activates the post injection combined reading will likely hit the same value. Contacted Jerry Z who directed to try again. Parth P standing by with a grab sample to determine if the reading is accurate. 01:50 - VNPSCD - Alarms returned on second attempt to activate chemical system. Parth P collected a grab sample and confirmed that the post injection analyzer is reading accurately. Called Jerry Z to inform that the system is not operating as expected. Jerry Z informed that the combined chlorine average is what controls the dosing setpoints and this analyzer is currently reading low. Jerry stated that if the twenty minute average analyzer reading does not update then PCS should be contacted. 02:13 - VNPSCD - The twenty minute average combined chlorine reading has not updated after forty minutes. Contacted Chris S who walked through the process of completing a combined chlorine average reading reset. Completed the combined chlorine average reading reset at the request of Chris S and the combined chlorine average value matched the current pre-injection combined chlorine reading. Returned the chemical system to auto and monitored the post injection values. The post injection readings stabilized within normal range indicating that dosing is normal and the issue has been resolved. Will monitor site closely. Created CMU5#W11664563 for Chris S. #consult #CMU5 | FLAG | stage2_classifier | 0.75265 | ML classifier: high issue probability (0.753) | alarm [control_system]; alarms [control_system] | 0.75265 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | GWTP- Pre Chlor booster P1 overload alarm came in. P2 in man/off. Notified Patrick F. Patrick F reset alarms and pump restarted. Directed to disregard if alarms come back in as prechlor is not required #consult | FLAG | stage2_low_confidence | 0.016312 | ML: above threshold (no LLM available) — 0.016 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.016312 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | SHTP- Reservoir total Cl2 fault alarm came in. Notified Cole W. Will take a look on SCADA #consult | FLAG | stage2_low_confidence | 0.0097355 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.0097355 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | SHTP- Cole W was able to reset alarm. Cole W rotated sample pumps. and Directed to do so if alarm comes back in 11:51- SHTP- Total Cl2 fault came back in. Rotated sample pumps from P2 to P1. cleared alarm 11:59- SHTP- Total Cl2 fault came in again. Notified Cole W. Will check SCADA and reach out if he will attend site | FLAG | stage2_low_confidence | 0.019359 | ML: above threshold (no LLM available) — 0.019 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.019359 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | NMVCBA- Placed valve in manual open at 40L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044988 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | KCETDS- total/combined Cl2 alarms came in. Looks like analyzer dropped out and recovered after 3 mins alarms cleared | FLAG | stage2_low_confidence | 0.0079285 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0079285 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | MAP7 - Place pump 2 back in auto VNP7 - Place pump 3 back man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041793 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -1C and flurries | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045056 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | GWTP - ZW3 Membrane Tank Level Switch LoLo alarm came in. Value turned normal and alarm cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060078 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | AUW57, Placed well 5 man/off to help take more flow from AURSBS AUW14, once contact tank has been cleared, will be placing wells 2/3 man/off to allow more water to be taken from AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059711 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal RHRSTR - Activated duty 1 to fill the reservoir. NMETIB - Deactivated duty 1. NMVCBA/NMVSIB - Reverted flow setpoint changes made earlier. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0024657 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | YWS+NYWS normal AUPSRR- Post injection free Cl2 hihi/ combined lo alarms came in. Reset as residuals recovered VNPS- Free amm hi alarm came in. Looks like residuals higher than normal after adjustments on site. Will continue to monitor. | FLAG | stage2_low_confidence | 0.0076947 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0076947 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | AURSBS - Activated reservoir in preparation for MAPS to JFRS Feed run | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066306 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | BLW34 - Kyle C with contractor working on site. Well 3 pump man/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047117 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NBW2 - Parth P, Rick L and Art on site rebuilding chlorinator. Cole W on site to assist. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051932 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040295 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | HLW2 - Ammonia pump 1 fault. Pump 2 able to run. Able to clear pump 1 fault | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STRS48 - Joe M cleaning chlorine analyzers. NMW15 - Alex B called, well 15 pump man/off for now, chlorine analyzer issue, Eric S will attend site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004969 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNETFD- Angelica C and Tim H on site to test hi lo temp and flood alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNPS PD8, Placed pumps back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043128 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033588 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | VNRSKS - Placed all MAPS PD7 pumps man/off and placed pump 2 and 3 at VNPS into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054467 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | MKRSEM - High level alarm setpoint from 75 to 70% as per Patrick F. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055405 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | MTW3 - Chlorine Gas Leak alarm came in. Well was not running. Called Dan Z. who will attend site. CMU5 Created W11679951 23:26 - Dan Z. called back to inform that MTW3 will be OOS for the night as a minor leak has been identified. Both cylinders are now closed. #CONSULT #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; oos [equipment_failure]; not running [equipment_failure]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; oos [equipment_failure]; not running [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | YWS + NWYS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050034 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | STPSMR - Discharge pressure hi alarm. Checked site, pumps are active and system is close to duty 1 stop setpoint. Will monitor site and deactivate duty 1 if the discharge pressure continues to increase | FLAG | stage2_low_confidence | 0.010279 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010279 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | JFPS - Called back Alectra, speaking with Jill. Confirmed cause of power blips and faults in area of Vaughan & Richmond hill are due to drastic temperature increasing from below negative to above 0 quickly in area which caused salt and moisture going airborne causing flashover and temporary faults in line and dips in voltage. As well as ice shedding in areas. No concrete time of restoration but said it could be at least 12h to a day or two for these power blips in area. Informed Jerry Z of situation and he will head home. JFPS & BVPS remain on generator power to prevent continues drop in pumps due to power blips. Outage map does not reflect these areas of concern and faults as its dips in voltage but Alectra team is aware of the heavy power blips caused in areas and are actively responding and cleaning lines. They suggesting calling back in the morning for another update on situation | FLAG | stage2_low_confidence | 0.31295 | ML: above threshold (no LLM available) — 0.313 | fault [equipment_failure] | 0.31295 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMETIB - Deactivate duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041346 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | KLPSWL - Pump 3 & 4 hi temp, able to clear alarms right away. Pumps were not running at time MTELNL - Outlet free chlorine spike in reading, came back within range shortly and able to clear | FLAG | stage2_low_confidence | 0.017942 | ML: above threshold (no LLM available) — 0.018 | not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.017942 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | STW1/3, Placed wells 1/3 man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042107 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KSTP- Jerry Z req ROC to create CMU5 for Eric S for a total Cl2 analyzer fault. Created CMU5 W11679195 #CMU5 | FLAG | stage2_low_confidence | 0.0084637 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0084637 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | MTW3 - Chlorine Gas Leak alarm came in. Called Phil D. who will head to site. CMU5 Created W11679209 #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | Connor Smith signing in -1 Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | MAPS/JFRS- Initiated Maple to Jefferson Feed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059425 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMPSKC, NMTKKC, NMMCWA - Kevin W switching from Radio to cellular APN. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066741 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -4C and snow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045642 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | YWS + NYWS Normal QVW34 - Treated total chlorine hihi alarm. Checked site, well is off no water being directed to users. Reset alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0048898 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | SHTP - Made changes for the interim procedure. Noted that there is a "well raw water tank level override stop" setpoint that is currently set to a level that is lower than the new Raw water tank level stop setpoint. Contacted Tim H to ask if this override stop setpoint will interlock the well pump if it is below the target stop setpoint for the raw water tank. Tim will check SCADA and call back. 21:22 - SHTP - Tim H called back and directed to change the well water tank level override stop alarm to 5.30m, from 5.10m. Tim also adjusted the manual speed setpoint for well #2 from 70% to 92% because the well was only producing 15L/s but the interim requires 17L/s. Tim also adjusted the reservoir high level alarm to 85% which will trigger if the reservoir fills and the plant stops. At this time Tim H requested that the SHETCS duty be activated to ensure the raw water well 2 does not stop. #consult | FLAG | stage2_low_confidence | 0.10582 | ML: above threshold (no LLM available) — 0.106 | scada [control_system]; alarm [control_system] | 0.10582 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | MKRSMR- Pouran from Metro called wanting to test P10 for 30 mins | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049202 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | MAPSN1 - Communication Failure alarm came in for various sites on the server. After 5 mins, all communications alarms cleared and trending is okay 12:44 - MAPSN1 Server communications alarm came in again. Called Yash S. who will take a look 12:58 - Yash S. called back to inform that the server is back online and that he is finished the KCETFS and KCETDS upgrades. Alarms cleared and trending is okay 13:!3 - PAC communication alarms for KCETDS and KCETFS came in again. Called Yash S. who is looking into it. Also informed Yash about the outstanding ANMCBL - PAC Communication Alarms | FLAG | stage2_low_confidence | 0.032062 | ML: above threshold (no LLM available) — 0.032 | failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system] | 0.032062 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | AUW14, Joe D on site, testing cl2 leak alarm | FLAG | stage2_low_confidence | 0.0076232 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; leak [infrastructure] | 0.0076232 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | MAPS- Placed PD7 pumps to manual VNPS- Placed PD7 duty 1 pumps into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042767 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | BLW3 - Patrick F attending site CMU = 11664802 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037856 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MAPS PD7 - Dan B called, P4 will remain man/off, Pumps 1,2,3 back to normal. VNPS PD7 - placed Pump 2 back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052144 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMW15 - Eric S working on total chlorine analyzer. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045684 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | SHTP - Filter 1 and 3 Turbidity Hi alarm came in. Checked site. Filter 2 just came out of backwash. Spoke to Derrick S. and Jacob M. Jacob M. directed to Ack/reset alarms | FLAG | stage2_low_confidence | 0.008945 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.008945 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | HLW2 - Stephen B leaving site to grab supplies from HLW1 and will be back to change cylinders at HLW2 with Jacob M STPS48- Lee F on site to work on high lift P2 NMTKKC- Ian W and Jay G done on site. Jay G will activate D1 with chem system off and place back in auto once flow stabilizes. NMPSKC- Pac Comm fail came in on site. Notified Jay G who will consult with Ian W | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | NMETIB - Total Chlorine Hi alarm came in. Checked site. Tower is filling. Will continue to monitor site 04:58 - Combined Chlorine Hi alarm came in. Trends indicate an increase of total and combined levels over the past day. Called Jerry Z. who informed if the combined level goes above 3.7, he will attend site. | FLAG | stage2_low_confidence | 0.0099087 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0099087 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | MAPS PD8- Placed all pumps in man/off. Placed P2/4 in D1 and started both for Lee F. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054073 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | Adam Button signing in in -3C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042347 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | STW3 - Influent Free chlorine residual Hi, Effluent Free chlorine residua Hi alarms at duty start. Value back to normal, cleared alarms. | FLAG | stage2_low_confidence | 0.0083069 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0083069 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNRSKS - Activated duty 1 to draw down MARS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044928 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | JFPS- WPS P2 failed to start and MV2 failed to close alarms came in as power transferred back to utility cleared alarms KSETDP- Jackie P on site to test lo temp, Cl2 leak alarms and perform JHS inspections AUW57- Joe D on site to get well back on line. MAPS- Dave T on site to test lo temp, Gas leak alarms and perform JHS HVAC inspections BLW3- Phil D on site to work on silicate and Cl2 systems. Dan Z also on site to test alarms on site and directed to disregard all alarms on site until done | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; failed [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | gas leak [critical]; failed [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | MAPS- Lee F called and requested to run PD7 pumps 1,3. Placed VNPS duty 1 pumps man/off and MAPS PD7 pumps 1,3 into auto. 10:05- Pump 1 shut down on Pressure Switch Low Alarm. Notified Lee F. Cleared alarm and placed back into duty 1. 10:15- Pump 2 shut down on same alarm, Lee F will inform Tyler ZJ. 10:20- Lee F requested pumps 2,4 in duty 1. 11:10- Lee F finished. Placed Maple PD7 pumps in manual. Placed VNPS PD7 Duty 1 pumps into auto | FLAG | stage2_low_confidence | 0.012204 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.012204 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NMETYS- Yash working on comms network. Will lose comms to towers valves and meter chambers in system but no impact expected AURSBS- Donald M done on site QVW12- Artour done commissioning diesel LIT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059422 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | VNPS PD7 - Pumps 2&3 to auto. MAPS PD7 - Pumps 1&2 man/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040328 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | AUMCBS - Power blip, cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060445 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW12 - Artour L working on OIT, disregard Historian Heartbeat alarm. Placed Well pumps 1&2 man/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063961 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | QVW12 - Influent free chlorine hihi. Checked site, wells are running in manual mode. Trending shows a sudden spike of the influent free chlorine reading which returned to normal range within one reading interval. Reset alarm. | FLAG | stage2_low_confidence | 0.011438 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011438 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | SHTP, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039621 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW12 - Garrick from Ferguson electric disconnecting portable generator and connecting to station generator, may send alarms. | FLAG | stage2_low_confidence | 0.00829 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.00829 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | QVETQS - System pressure lo alarm came in when QVW12 deactivated. Pressure took a dip and came back immediately. Alarm cleared NMVCBA - Placed valve back to auto NMETIB - Activated duty to help offset with NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051743 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | JFPS- WPS P2 failed to start/ MV2 failed to open alarm came in. Came in yesterday as well. Notified Tim H heading to site | FLAG | stage2_low_confidence | 0.013135 | ML: above threshold (no LLM available) — 0.013 | failed [equipment_failure]; alarm [control_system] | 0.013135 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MAPS PD7, Placed pumps 2/3 man/off VNPS PD7, Placed pumps 2/3 in auto RHRSTR, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026746 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BVPS - Diesel delivery on its way, informed Jerry Z to meet Consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054917 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMETIB - activated D1 to offset with NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044833 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MKMCLA - Power blip, alarms cleared | FLAG | stage2_low_confidence | 0.0072651 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0072651 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MAPS- Tim H on site to run generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053699 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | NMTKKC-Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039756 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | MKRSEM - Noted that the trendline appears flatlined. Level value changes slightly over time. Reservoir is draining and flatline level is abnormal during reservoir draining. MKRSMR is currently filling, backflow down to MKRSEM is possible. Will monitor situation. 20:58 - MKRSEM - Reservoir has begun filling with no duty active. This abnormal fill/drain trend could be related to an ongoing watermain break in Markham. If valves are being turned in Markham it would be affecting flow pathways. No York Region operators are in the field at the moment but CPD is investigating and trying to determine who has ownership of the break. If ownership has been claimed and they are working on the fix, valving has likely influenced the fill cycle. | FLAG | stage2_low_confidence | 0.066867 | ML: above threshold (no LLM available) — 0.067 |  | 0.066867 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MKETFA/MKRSEM/MKRSMR- Poulan from Metro called to inform ROC that we will lose comms for pumps supplying storages. Pumps that are active currently will remain on but Metro is working on software updates for pumps in this area | FLAG | stage2_low_confidence | 0.01371 | ML: above threshold (no LLM available) — 0.014 |  | 0.01371 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMETIB- Parth P on site to work on Cl2 analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042768 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMETIB - Free chlorine hi. Checked site, trending shows the free chlorine reading is climbing following a visit from instrumentation and operations. Called Joe W who will return to site to check the analyzer. | FLAG | stage2_low_confidence | 0.01258 | ML: above threshold (no LLM available) — 0.013 |  | 0.01258 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | ARPS, David from OCWA called, Rotating pumps from pump 2 to pump 4 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049982 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | Adeela Khan signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052739 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | STW12 - Joe M performing w/o including: generator run, chlorine analyzers maintenance, health and safety inspection. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062703 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NBW56 - Jordan B on site, cleaning chlorine analyzers and testing chlorine leak alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | SHTP - Kevin W on site for network upgrades. Jacob M on site to assist | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062875 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NBW3- Influent free Cl2 lolo switch. Called Jordan B. Directed to reset and allow well to run in schedule mode | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060793 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | STW12, STW3 - man/start for STETBR fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045302 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BVPS - Dan Z on site to swap the station back to utility power and shut down the generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069635 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | SHTP - Well 2 pump uncommanded start alarm. Checked site, flow recently stopped as the reservoir is full. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067745 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMETIB - Activate duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040962 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | GWTP- Joe M notified ROC ZW7 neutralization exceeded dur and recirc inlet V failed to close alarm will remain outstanding for night | FLAG | stage2_low_confidence | 0.013672 | ML: above threshold (no LLM available) — 0.014 | failed [equipment_failure]; alarm [control_system] | 0.013672 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | Bathurst and North of Shaw - Karen from Roads dispatch called to inform that there has been a report of a watermain break at this intersection. After checking this location on all pipes, york region does not have any watermains in this area. Karen will contact the city of richmond hill. Karen will also give the ROC a call back with any new information | FLAG | stage2_low_confidence | 0.024936 | ML: above threshold (no LLM available) — 0.025 |  | 0.024936 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | ARPS - Clarified from Peter (OCWA) that flow registered between 13:44-14:16 is a result of service water flow through chemical quill during maintenance work on injection system. Flow through FIT34310 not a result of pump run. Notified Jeremy H. | FLAG | stage2_low_confidence | 0.0093616 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093616 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | AUW57 - Influent Free chlorine LoLo interlock on duty start. Placed man/off. Notified Joe D. 15:00 Jerry Z will attend site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043821 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | RHRSTR - Tim H and Carter D on site. Tim requested that the VNPS PD8 pumps be activated. Activated duty 1 and then duty 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060888 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | SHTP- Backwash high lift required alarm came in. Notified Jake M. Jake M reset alarms high lifts back in auto. | FLAG | stage2_low_confidence | 0.0086583 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0086583 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | NMETHW - Deactivated duty to keep level offset from NMETIB. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063191 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | BVPS- Peter from Metro notified ROC they are having a technician work on software updates at bayview reservoir and will lose comms for 10 mins RHRSWA- Tim H heading to site with portable generator created CMU5 #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066965 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | HLW2- Station Turbidity Fault. Interlocked well. Notified Tim. H. Can disregard. Increased HLW2 VC from 20L/s to 40L/s. 15:10- Tim H will attend site after attending NBW5 W11679730 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure] | 0.0056014 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Zoran) and requested two pumps on 03:00 - Called Toronto Water (Zoran) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053524 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | NMVCBA - Placed valve in manual at 40 L/s 01:59 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030365 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | STETBR- Tower level hi STW12/3- Placed P1/3 back in auto as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042265 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | HLW2- Treated Total and Combined Cl2 lo alarms came in. Well not active no water directed to users and alarm cleared after 3 mins | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | NMW12- Influent free Cl2 lo alarm came in on well start up cleared after 3 mins | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058254 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MAPS PD7 - Tim H and Dan B finished on site. Pump 4 man/off until further notice. MAPS PD7 pumps 1,2,3 man/off VNPS PD7 Pumps 2 and 3 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046857 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NMVCIB, changed flow setpoint from 80 to 40L/sec NMVCBA, Changed flow setpoint from 40 to 80L/sec 22:05, Reverted changes | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025886 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MKPSSA - Garrick from Ferguson electric running generator and testing containment foods. 09:40 All alarms cleared, Garrick leaving site. | FLAG | stage2_low_confidence | 0.0094585 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system]; containment [safety] | 0.0094585 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | Carter Dunn Signing In, -2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | GWTP- Jackie S on site backwashing GAC 3 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041396 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | AUETFC, Joe D on site, working on the health and safety alarms//temp alarms and working on the analyzers on site | FLAG | stage2_low_confidence | 0.0097139 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0097139 | 0 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | TMC317, Forward Flow Lo, Valve shows no flow going to MARS, contacted Zoran from Toronto, he is rotating pumps which caused the flow to drop. will continue to monitor the until it is back to normal range | FLAG | stage2_low_confidence | 0.0093713 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093713 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NMVCBA - Placed valve in man at 30 L/s 01:30 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029913 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | VNRSKS - Deactivated duty 1 and switched all VNPS PD7 pumps man/off and placed pumps 1,2,3 at MAPS PD7 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061062 | 0 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | HLETYS - Stephen B testing temp alarms and cleaning chlorine analyzers. | FLAG | stage2_low_confidence | 0.008525 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.008525 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | HLW2- Treated free Cl2 hihi alarm came in. Rotated ammonia pumps and notified Stephen B. Stephen B on site working on ammonia system MKRSEM- Called Metro spoke with Poulin to start 2 pumps to reservoir QVW34- Donny M on site to work on analyzer sand get the well back up and running | FLAG | stage2_low_confidence | 0.009532 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.009532 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | JFRS - WPS pump 3 & 4 failed to start. Reoccurring issue with iste. WPS MV#3 & 4 failed to close. Informed Jerry Z again of situation. Unable to clear on my end, Jerry will go back to site | FLAG | stage2_low_confidence | 0.016372 | ML: above threshold (no LLM available) — 0.016 | failed [equipment_failure] | 0.016372 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | JFPS - Pump 3 & 4 uncmd stop on power trip. WPS pump 3 faile to start, pump 4 MV#4 failed to close. Generator running No update from Alectra (Kevin) when called for update. Was informed no news or anything concrete to share at this time. Still investigating. BVPS - Pump 1 & 4 multilin trip/warning. Unable to clear alarm. Informed Jerry Z again of issue and will try and run generator at BVPS VNPSCD - Post-inj free/comb hihi due to BVPS shutting down and readings spike. RHPSPA - Surge valve 2 open | FLAG | stage2_low_confidence | 0.045485 | ML: above threshold (no LLM available) — 0.045 | failed [equipment_failure]; trip [equipment_failure]; alarm [control_system] | 0.045485 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | ARPS - Martin from Peel/OCWA called to inform they are completing a pump duty rotation. | FLAG | stage2_low_confidence | 0.0072345 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072345 | 0 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | GWTP - Backpulse Tank 2 Level HiHi and Backpulse Tank Level Hi alarm came in. Checked site. Spoke to Jackie S. who will take a look | FLAG | stage2_low_confidence | 0.0074664 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0074664 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | AURSOH, Deactivated D1 AURSBS, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031127 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | GWTP- MAU 1 coil lo temp alarm came in. Notified Jackie P. Will try to clear after chem delivery is completed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065469 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNPS- Tim H on site to work on post injection hi ammonia residual analyzer. Req RHRSTR D1 be activated RHRSTR- Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050376 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BLW12- Tyler Z restored power to site and req D1 activation to ensure wells running okay after work. Activated D1 for BLETNL 17:29- BLW12- VFD Fault alarm came in. Notified Tyler Z. Will go back to site and check VFD 17:40- BLW12- Tyler Z cleared VFD alarm well started up okay 17:48-BLW12- Notified Patrick F that Well is back up and running #consult | FLAG | stage2_low_confidence | 0.015287 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system] | 0.015287 | 0 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW3 and STW1 back to auto, as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060923 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | VNPS - Rick L completed work on site, Placed BVPS pumps back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062614 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | SHTP- Cole W done on site directed to clear alarms. All alarms cleared trends okay AUW57- influent free Cl2 hihi alarm came in on well start up cleared after 3 mins | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0067736 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | NMMCBA - Parth P on site to complete a flowmeter calibration. *wrong book* | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044524 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | Adam Button signing in 3C Foggy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041576 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | RHPSWPA, Travis W on site, testing flood alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW12- Artour L done testing on generator. Placed Well 1 back in auto. KLET27- Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046676 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | STETBR - tower level hi alarm. Placed STW1 and STW3 in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005491 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | STW12- Placed well 1 back into auto STW3- Placed well back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041937 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | Carter D Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | MARS- Called Metro spoke with Pouran to increase flow to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065422 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | BLW34 - Kyle C restarting OIT for updates, disregard Heartbeat Alarm until further notice. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061462 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NMPSKC - Aaron M making network changes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058312 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | QVETQS, Jason G is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053162 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMETIB, Changed D1 stop back to 75% from 85% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044781 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MKRSEM -low level alarm. Called Toronto Water (Paul) and requested they activate two pumps to push flow. | FLAG | stage2_low_confidence | 0.0086239 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086239 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | VNP8 - Proc sump pump 1 & 2 fault, able to clear RHRSTR - Site power failure, able to clear as site continuous to run on generator | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure] | fault [equipment_failure]; failure [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | MKRSEM -Request TO (Brent) to drop both pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059547 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | GWTP-CIP feed water flow hi alarm came in. Cleared upon acknowledgement | FLAG | stage2_low_confidence | 0.0073716 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073716 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | MKRSEM- Called Metro spoke with Paul to start two pumps to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066178 | 0 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | NMVCBA- Placed valve back inauto NMETHW- Activated D1 at 43% to offset from NMETIB as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048576 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BVPS- Notified Dan Z that instrumentation is done work at VNPS and pumps can go back into auto. Notified Tim H that we will be activating D1 at RHRSTR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071905 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | Ethan U signing in Weather 0. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMTKKC - Ammonia tank 2 hihi. Able to clear, level within range | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049062 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather -2C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | ARPS- Martin from Peel called to notify ROC they will be transferring from P5 to P6 KCETDS- Activated D1 as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051345 | 0 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | 9255 Jane St- Kai Ming C. from Access York (Customer Relations) notified ROC of ongoing leak in Vaughan that was called in by Property manager. City of Vaughan was first point of contact claiming it is not their infrastructure. Checked all pipes. No York Region infrastructure in area. Complex being fed by Vaughan main and most likely private connection to complex. Emailed Access York explaining that this location does not have York region infrastructure in area of leak and followed up with Nolan from City of Vaughan. (416-550-8419). #Accessyork | FLAG | stage2_low_confidence | 0.050652 | ML: above threshold (no LLM available) — 0.051 | leak [infrastructure] | 0.050652 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | MAP7 - Place pumps man/off. VNP7 - Place pump 2 & 3 auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039939 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | STW3- Chris S cleared historian heartbeat. Placed well 2 in man/on trends okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052145 | 0 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | VNPS- Rick L on site for chlorination system calibrations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058843 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | ARPS - Peel ammonia analyzer B airport Rd discharge. Ammonia level/readings within normal range. Called Peel, no response 16:17 - Called back and spoke with Bineesh. Said Readings are okay on their end, they received same alarm but analyzer B is their spare and all ammonia and related alarms are in good standing | FLAG | stage2_low_confidence | 0.012081 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012081 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | Ethan U signing in Weather -1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMW15, Alex B/Christian are on site, doing site PMS, working on the chemical analyzers/turbidity analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055903 | 0 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | NBET27 - Jordan B running generator, testing Hi/Low level and temperature alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0067675 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | NMETIB - Deactivate duty 1 MAP7 - Place pump 3 man/off VNP7 - Place pump 3 auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037018 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | NMW136 - Influent free chlorine hihi, Came in during startup of well. Monitored site and reading came down within range | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062924 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | NBW3 - Influent free chlorine lolo on startup for schedule mode. Able to reset alarm next couple reading | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065381 | 0 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | YWS + NYWS Normal NMETIB - Activate duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035532 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060929 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | NBW5 - Turbidity Hi alarm came in. Checked site. Well is running but duty is 2% from deactivating. Trends indicate turbidity was high during the day. Rotated silicate pumps. Will continue to monitor 18:55 - After about 20 mins, turbidity did not come down. Placed well man/off and will send an email to Jacob M. 19:09 - Spoke to Jacob M. instead. Jacob directed to prime both silicate pumps. Started with silicate pump 1 and placed it in manual with 100% setpoint and started the pump. After about a minute, placed silicate pump 1 man/off and then started priming silicate pump 2. Jacob also directed to place the well and all pumps back to auto once duty deactivates #CONSULT | FLAG | stage2_low_confidence | 0.026177 | ML: above threshold (no LLM available) — 0.026 | alarm [control_system] | 0.026177 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | ARPS - Peel OCWA (David) called to inform he is rotating duty 1 pump at ARPS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052443 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | QVW34- Yash S finished with work. Wells are back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004765 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | HLW2- Combined Chlorine HiHi Alarm. Interlocked well. Notified Stephen B. He will take a look. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060516 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | VNPS PD7- Placed duty 1 pumps in auto MAPS PD7- Placed duty 1 pumps in manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043886 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | QVW12 - Influent Free Chlorine Hi alarm came in. Checked site. Influent Free levels are just below the target level. Will monitor | FLAG | stage2_low_confidence | 0.0072756 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072756 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | SCADA server - Evgheny S. called to inform he will be rebooting remote SCADA. Lose access for 20 Seconds 21:25 - Server Restart complete | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0061438 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NMW12 - Treated Total Chlorine Lo and Combined Chlorine Lo alarms came in. Wells are not running and water is not being directed to users | FLAG | stage2_low_confidence | 0.016651 | ML: above threshold (no LLM available) — 0.017 | not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.016651 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | GWTP - Make Up Air Unit 1 Coil Low Temp alarm came in. Critical alarm. Shift report directs to disregard the MAU fault, not the low temp. Called Joe M. who directed to disregard alarm for the rest of the weekend #CONSULT | FLAG | stage2_low_confidence | 0.014846 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system] | 0.014846 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | VNPS/RHRSTR - Yash S. completed planned network work. Placed BVPS and VNP8 back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055097 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | GWTP, Sutton/Keswick Header Fluoride Lo alarm, Notified Patrick F, Jack P is currently working on the analyzers | FLAG | stage2_low_confidence | 0.0086508 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086508 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | VNVCIA - Site Power Fail alarm came in. Checked site. Valve was closing and in local. After about 5 mins, valve went back to auto and alarm cleared. | FLAG | stage2_low_confidence | 0.0080607 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080607 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | NMVCBA - Placed valve in manual at 30 L/s 04:15 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030365 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | QVW34 - Well producing less flow than normal. Placed well manual/off and sent email to area operators to have it inspected. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064672 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | GWTP - ZW2 recovery exceeded recovery setpoint. Alarm status changed to normal while navigating to site. Alarm cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.0073236 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073236 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | NBW37- Jordan B onsite working on Cl analyzers and Turbidimeter as well as running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055964 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | AUPSWS- Sean P onsite running generator. 09:40- Sean P finished with generator run. Lee F onsite working on pump 4 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043284 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | AUW57- CT Not Achieved Alarm. Called Joe D. Notified that William M is onsite running well to waste for sample | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063089 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | NBW5, Turbidity Hi Alarm, Placed well man/off for the time being | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054424 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | AUW14 - Placed wells2 and 3 pumps back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045696 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | Carter D signing in, -9D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041513 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | VNPS PD7, Placed pumps 1/4 man/off MAPS PD7, Placed pumps 1/3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035046 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | ARPS-Martin from OCWA (Peel) is switching pumps. P5 has a leak on the gasket. Martin will start pump 8. | FLAG | stage2_low_confidence | 0.0093677 | ML: above threshold (no LLM available) — 0.009 | leak [infrastructure] | 0.0093677 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | MARS, Notified Toronto operator Zoran to go back down to normal flow MKRSEM, Notified Toronto Operator Zoran to stop pumping to the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060742 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | GWTP, Backpulse Tank 2 Level hi alarm trends show the level higher than normal, Shift report doesn't say to disregard, notified Jack P as RO doesn't have OIC for site, Notified Jack P, directed to disregard for the night consult | FLAG | stage2_low_confidence | 0.0078463 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0078463 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | JFPS - David T. testing flood alarm ANW23 - Stephen B. working on NTU analyzer | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | AUPSOH - Inlet Pipe Heat Trace Fault alarm came in. Called Jason G. who directed to disregard alarm as he will take a look later on in the day #CONSULT | FLAG | stage2_low_confidence | 0.014186 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system] | 0.014186 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | RHMCMD - Closed valve to help RHRSTR fill for the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066203 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | Adeela Khan Signing in. Weather: -18C and clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044683 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | HLW1 - Ian W working on OIT, disregard Historian Heartbeat alarm. 13:00 Ian W completed work on OIT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0044818 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | NMETHW- Deactivated duty to keep offset with NMETIB | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060931 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | NMTKKC- Jason G onsite for work orders. May receive hi sanitary pit, flood alarm, hi/low temp, process room flood. Will also be working on chlorine analyzers later on | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NMW15 - Combined Chlorine Lo alarm came in. Checked site. Well is running in schedule mode. Trends indicate a dip in combined levels but came back to optimal range within 2 mins. Alarm cleared | FLAG | stage2_low_confidence | 0.0098229 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0098229 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NRETCR - Deactivated duty in preparation for interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061263 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NBW5 - Effluent Free Chlorine Lo alarm came in. Checked site. Well is active. Monitored site for 10 minutes and effluent free chlorine levels did not recover. Influent levels are within range, but lower than usual. Switched chlorinators so that chlorinator 2 is in duty 1. Will continue to monitor 21:24 - Effluent Free Chlorine LoLo switch alarm came in. Checked site. Effluent chlorine levels did not hi lolo levels. Placed well man/off. Called Jacob M. who will take a look on SCADA. 21:50 - Jacob M. called back to inform he is headed to site. CMU5 Created W11646068 23:30 - Jacob called back to inform that he is finished on site. Jake informed he backflushed well 5 with system water and then restarted the well. Chlorinator 2 has been put back into duty 1. Jake informed this may trigger a hi influent due to this but will readjust shortly. Jake also informed that a turbidity hi may come in due to the backflushing and starting and stopping the well. If a high turbidity occurs and lasts more than an hour, Jake directed to prime each silicate pump. 23:34 - Turbidity Hi alarm came in. Will monitor 00:07 - Placed well back to auto. Turbidity levels have gone back to optimal range and alarm cleared #CONSULT #CMU5 | FLAG | stage2_low_confidence | 0.073702 | ML: above threshold (no LLM available) — 0.074 | scada [control_system]; alarm [control_system] | 0.073702 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | ARPS - David from OCWA Called to inform that he is shutting down pump 2 and will have no flow, as per ARPS Shutdown Interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064993 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal RHMCMD - Placed valve man/open as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043562 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | HLPSYS - Tim H running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005621 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | SHTP- Jacob M onsite for work orders. UV reactor check, Chlorine and turbidity analyzer cleaning, KNMO system inspection. | FLAG | stage2_low_confidence | 0.014073 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action] | 0.014073 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | VNETAG- Aaron C switching over network. May receive communication alarms. 11:39- Work is complete | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0051214 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | GWTP, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003958 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | NMETHW- Combined, Total Chlorine HiHi Alarms. Called Jason G. No answer. Will try again 09:26- Jason G called back. He will look into it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0061492 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | MKRSEM - Called Toronto water (Zoran) and requested start filling Res with 2 pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053665 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | HLW2 - Eric S finished and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044016 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | STW12- Placed in auto STW3- Placed in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003715 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | NMETHW- Ben H called to request a CMU for Eric S to troubleshoot chlorine analyzer W11634388 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034784 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | GWTP - CIP inlet valve failed to open alarm. Patrick F requested reset alarm. | FLAG | stage2_low_confidence | 0.023575 | ML: above threshold (no LLM available) — 0.024 | failed [equipment_failure]; alarm [control_system]; valve failed [infrastructure] | 0.023575 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | BLW12- Joe M onsite with contractors for electrical upgrades. Wells will be Local off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005453 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | AUPSRR- Ric L finished onsite. Placed chemical pumps back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00661 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | JFPS - Multiple power related alarms came in. Value immediately turned normal. Generator is not running and site is still connected to generator power. Trending is okay. Will continue to monitor | FLAG | stage2_low_confidence | 0.028145 | ML: above threshold (no LLM available) — 0.028 | not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.028145 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | MARS- Ric L onsite for calibrations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056812 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | KSETDP, BLETNL - Talha H working on OIT, disregard Historian Heartbeat alarms. | FLAG | stage2_low_confidence | 0.0088118 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0088118 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | KLW34- Eric S onsite working on turbidimeter. 11:46- finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034945 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | SHETCS - Eric S on site, working on Hypo tank level and Hypo pump 2. 13:58 Eric S leaving site and heading to NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041583 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | AUW14 - Placed well 1 and 4 in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044514 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | JFRS - Activated Duty 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040872 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | HLW2- Eric S onsite working on effluent, treated and total chlorine analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051801 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Linear- Rob P called the ROC for an update on the main break in EG. No one called ROC with update. Rob P will call Ryan from EG and update ROC | FLAG | stage2_low_confidence | 0.009464 | ML: above threshold (no LLM available) — 0.009 |  | 0.009464 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | VNETAG - Yash S. on site for planned network work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057255 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | STPSMR- Travis W onsite running generator. He will place pumps man/off then back on when generator starts up. | FLAG | stage2_low_confidence | 0.0079508 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079508 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | RHRSTR - Activated duty 1 to help push more water into MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048168 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | KSETWB - Jackie S on site performing w/o, including - Chlorine gas leak test, chlorine analyzer maintenance, recirculation pump run, valves exercising. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; leak [infrastructure] | gas leak [critical]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | HLW1 - Stephen B on site for chlorine leak alarm test, chlorine analyzers maintenance. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | YWS+NYWS normal 22:10-Linear- Cory from GIP (416-677-7682) req York Region OPs to attend site to throttle down main to complete repair. Notified Rob P who will head to site. Notified Cory that Rob P will be on site within the hour 22:10-GWTP- Back pulse tank fill failed to close alarm. Valve showing closed and tank not filling,. Reset alarm. | FLAG | stage2_low_confidence | 0.036163 | ML: above threshold (no LLM available) — 0.036 | failed [equipment_failure]; repair [maintenance_action]; alarm [control_system] | 0.036163 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NMMCBR- Upstream pressure lolo alarm came in. Called Rob P to confirm it was caused by work going on to fix main. ROB P closed valve in area to help EG repair main. #consult | FLAG | stage2_low_confidence | 0.01851 | ML: above threshold (no LLM available) — 0.019 | repair [maintenance_action]; alarm [control_system] | 0.01851 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | NMTKKC- Ammonia P1 failed to start alarm. reset alarm | FLAG | stage2_low_confidence | 0.0097821 | ML: above threshold (no LLM available) — 0.01 | failed [equipment_failure]; alarm [control_system] | 0.0097821 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | ARPS - Peel Ammonia analyzer airport road discharge free ammonia fault alarm came in. Called Peel spoke with Bineesh. No issues with ammonia system cleared alarm | FLAG | stage2_low_confidence | 0.020947 | ML: above threshold (no LLM available) — 0.021 | fault [equipment_failure]; alarm [control_system] | 0.020947 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | MAP8 - Rick L. doing annual calibrations. Duty just deactivated, placed pumps man/off AUW14 - AU central just activated, will place W2 and 3 man/on. Notified Joe D. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063159 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | GWTP - Keswick and Sutton Header Fluoride Lo alarms came in. Disregarded as per Joe M. | FLAG | stage2_low_confidence | 0.0091788 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0091788 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | GWTP - Pressurized Vestibule Lo Temp alarm came in. Higher priority alarm. Called Joe M. who directed to disregard alarm for the night #CONSULT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071194 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -22C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046216 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | VNRSKS - Activated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041269 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | GWTP - Sutton Header fluoride low. Value is not recovering as expected, fluoride pump 1 still pushing flow at the same interval. Called Joe M who directed to increase the fluoride pump 1 dosing factor from 1.00 to 1.05 and wait one hour. If the value does not recover Joe would like to be contacted. #consult | FLAG | stage2_low_confidence | 0.010679 | ML: above threshold (no LLM available) — 0.011 |  | 0.010679 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | ARPS- Peter from OCWA called and is rotating pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061118 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | SHTP - Jacob M working on chlorine system, testing chlorine leak alarm and running generator. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | HLW2 - Ian W working on OIT, disregard Historian Heartbeat alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054597 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | GRTPLL - Raw water total chlorine Res HiHi alarm, value back to normal. Cleared alarm. Disregard as per shift report. | FLAG | stage2_low_confidence | 0.0086938 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086938 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | ARPS- Peter from OCWA called.. Working on Free and Total Ammonia analyzers. Will return to normal shortly | FLAG | stage2_low_confidence | 0.0077746 | ML: above threshold (no LLM available) — 0.008 |  | 0.0077746 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | AUPSRR - Post injection free chlorine hihi. Checked site, trending shows a spike of the post injection free chlorine reading which dropped to normal range within one reading interval. Reset alarm. | FLAG | stage2_low_confidence | 0.013175 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.013175 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | AUETFC - Joe D headed to site for sampling. Joe D directed to deactivate the duty so the tower is draining. | FLAG | stage2_low_confidence | 0.0079308 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079308 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | STW3 - Influent and Effluent Free chlorine Hi alarm came in. Monitored site for 15 mins. Levels kept rising. Lowered Chlorinator 1 dosing factor to 260. Will monitor | FLAG | stage2_low_confidence | 0.0086375 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086375 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | STRS48 - High lift pump 1 failed to stop alarm at duty stop. Cleared alarm. | FLAG | stage2_low_confidence | 0.010931 | ML: above threshold (no LLM available) — 0.011 | failed [equipment_failure]; alarm [control_system] | 0.010931 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | ARPS- Peter from OCWA called. Pump 5 shutdown. Working on getting another pump going. 14:45- Peter called back. Pump 4 running in auto. Back to normal operations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054004 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | QVW34- Yash S onsite. Disregard comm fails. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044605 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | QVW3, Tyler Z on site, doing some well maint, Will M has talked with Tyler Z on running the well in man/on. Tyler Z will call when he is finished working on the site | FLAG | stage2_low_confidence | 0.0074445 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074445 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | RHPSWA - Karen from property services called to inform that security has received several security intrusion alarms from site. Karen stated that there is a door that is usually held closed by a key padlock and latch however half of the latch is missing and can no longer be locked. Karen requested that area operations be consulted to determine Contacted Jacob M who was unfamiliar with why the latch would be missing its connection. Karen stated that directing security to disregard the security intrusion alarm is an option. Jacob was not able to make that decision and requested that the situation be escalated to water on call management. Contacted Aaron W who directed to have the area ops on call operator attend site to determine if they can prop the door shut to complete a tight seal and prevent the security intrusion alarms from triggering. If that fails Aaron W wants on call mechanical to attend site to replace the broken latch. Contacted Joe D to dispatch. Created CMU5#W11645836 #consult #CMU5 | FLAG | stage2_low_confidence | 0.26185 | ML: above threshold (no LLM available) — 0.262 | alarm [control_system]; alarms [control_system] | 0.26185 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | GWTP - Sutton header fluoride low. Called Joe M who directed to leave the dosing where it is for the weekend. #consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005804 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | RHPSWA - Joe D leaving site. Joe worked with Security to secure the location and prevent further intrusion alarms from triggering. Joe stated that with this door secured if any more security intrusion alarms trigger security should attend site. | FLAG | stage2_low_confidence | 0.019116 | ML: above threshold (no LLM available) — 0.019 | alarm [control_system]; alarms [control_system] | 0.019116 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | STW3 - Influent Free Chlorine Hi alarm came in. Checked site. Duty recently activated. Level is just above the hi level. Will continue to monitor site 02:13 - Both Effluent Free Chlorine Hi and Influent Free Chlorine Hi alarms came in. Checked site. After 15 mins, levels came back to optimal range and alarms cleared | FLAG | stage2_low_confidence | 0.010159 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010159 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | AURSBS - Activated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041071 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | KSTKWP, Jerry Z on site working on the Cl2 analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043651 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | QVW34- Historian Heartbeat Alarm. Notified Ian W. He will take a look. Spoke with Tyler ZJ. Well 3 can go back into auto and well 4 to remain man/off | FLAG | stage2_low_confidence | 0.0079152 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079152 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | MARS - Level low alarm. Activated BVPS and swapped supply pumps to VNRSKS to VNPS. | FLAG | stage2_low_confidence | 0.0078152 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0078152 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated for schedule mode. Trending shows the influent free chlorine reading dropped on start up. Placed well in manual mode. Monitoring site to determine if the influent reading will recover. 13:13 - NBW37 - Influent free chlorine reading has recovered. Able to clear alarms. Placed hypo pump 2 back in duty 1 and activated the well. Monitored start up. | FLAG | stage2_low_confidence | 0.017042 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system]; alarms [control_system] | 0.017042 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | QVW12 - Treated free chlorine hihi alarm. Checked site, well recently activated to fill system. Trending shows a spike of the treated free chlorine residual. Rotated ammonia pump duty and monitored. | FLAG | stage2_low_confidence | 0.01009 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.01009 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NMW136 - Well 16 pump fault alarm. Checked site, unable to clear alarm. Rotated duty 1 to pump 16. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; pump fault [infrastructure] | fault [equipment_failure]; alarm [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | STW1 - Placed well pump in auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042743 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | MKRSEM - Low level alarm. Called Toronto Water (Brett) and requested they activate two pumps to push flow to MKRSEM. | FLAG | stage2_low_confidence | 0.0091364 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0091364 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -19C and clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044683 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | KSTP - Jerry Z running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056071 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | JFRS - Dave T on site to complete a low temp alarm test and a generator test run. | FLAG | stage2_low_confidence | 0.007394 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.007394 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | AUPSOH - Inlet Pipe Heat Trace Fault alarm came in. Checked site. Trending is okay. Will continue to monitor AUETFC - Inlet Line Standby Heat Trace alarm came in. Checked site. Trending is okay. Inlet and outlet heat trace is on. The standby has faulted. Shift report directs to disregard alarm | FLAG | stage2_low_confidence | 0.027114 | ML: above threshold (no LLM available) — 0.027 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] | 0.027114 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | 01:00 - EZ MAX ISSUES 01:35 - MKRSEM - Called Toronto Water (Brett) and requested to stop pumping to reservoir 02:00 - EZMAX Issues resolved | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal KCETDS - Activated duty 1 in preparation for MAPS to JFRS Feed run | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036722 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Town of East Gwillimbury operator (Ryan) called to inform of a watermain break on Yonge St south of Green Lane. Informed Dwayne L who sent Rob P to site. Created CMU5#W11639194 for Rob P. #CMU5 MAPS - Rick L finished annual calibrations and normal operations can resume. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064888 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | JFRS - Deactivated duty 1 and 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042363 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NMETIB - Heat Trace Controller 1 Fault alarm came in. Both heat trace controllers have faulted and is extremely cold. Called Joe D. but no answer. Will try again 02:38 - Called Joe D. again. Joe informed that he will take a look in the morning but to keep on the level trending. If any more issues arise, Joe would like a call back #CONSULT | FLAG | stage2_low_confidence | 0.015264 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] | 0.015264 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NMETHW - Riser Pipe Heat Trace Controller 1 and 2 Fault alarms came in. Checked site. Trending is okay. Will send an email to Joe D. | FLAG | stage2_low_confidence | 0.01426 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.01426 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | Carter D Signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | Connor Smith signing in -8C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041939 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | STW12- Placed well 2 back into auto STW3- Placed well 3 back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042395 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NRETCR - Activated duty 1 for the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046626 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | YWS + NYWS Normal KCETFS - Ian W leaving site. Communications and trending have been restored. Ian directed to disregard the historian heartbeat alarm for the night. | FLAG | stage2_low_confidence | 0.0077783 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077783 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | KCETDS - Outlet total chlorine residual lolo alarm. Checked site, trending shows a sudden dip of the total chlorine residual reading. The reading recovered within two reading intervals. Reset alarm. | FLAG | stage2_low_confidence | 0.013335 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.013335 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMNPSKC - PAC comm fail alarm. Checked site, operations appear normal. Trending not impacted. Alarm cleared. | FLAG | stage2_low_confidence | 0.008403 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.008403 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | ARPS - ROYKS to ROPKS comm failure alarm - cleared right away | FLAG | stage2_low_confidence | 0.013441 | ML: above threshold (no LLM available) — 0.013 | failure [equipment_failure]; alarm [control_system] | 0.013441 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMETRIB - Deactivated duty 1. NMVCBA/NMVCIB - Reverted setpoint changes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035342 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Paul) and requested they stop pumping to MKRSEM. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069353 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NRETCR, Activated D1 JFRS, Will activate D1 once level hits 80% for interim procedure NMTKBS, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0028655 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | AUW14- Placed wells back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043099 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | ARPS- Peter from OCWA Called and is rotating transfer pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063743 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHPSPA - Hydro power failure alarm. Checked site, generator is not running and ATS is pointing to utility hydro. One pump reactivated in duty 1. Cleared alarms and placed a second pump in duty 1. JFPS - WPS GEN xfer switch hydro power alarm. Checked site, generator not running and ATS pointing to utility hydro. Power blip affected Richmond Hil facilities. Pumps were not active when alarm came in. Cleared alarms. RHRSWA - Control panel power failure alarm. Power blip in Richmond Hill. Site operations normal, cleared alarm. MMW1 - Control panel power failure alarm, Well 8 high level and well 13 high level alarms. Re-activated well pumps 8 and 13. Cleared alarms when level dropped. | FLAG | stage2_low_confidence | 0.060478 | ML: above threshold (no LLM available) — 0.06 | failure [equipment_failure]; not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.060478 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | JFPS - Tyler ZJ working on P1 motor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043381 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | VNRSKS - Placed all VNPS PD7 pumps man/off and placed MAPS PD7 pumps in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052142 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | STETBR - Tower Level Lo alarm came in. Placed STW12 and STW3 man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058969 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NMETIB - Activated duty to help offset with NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060702 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | RHPSPA - Lee F on site for pumps vibration test. Requested Pumps 2&3 to duty 4, Pumps 1&4 to duty 1. | FLAG | stage2_low_confidence | 0.010127 | ML: above threshold (no LLM available) — 0.01 | vibration [equipment_failure] | 0.010127 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | ANW23- Stephen B leaving site. Generator is still running. Will be back onsite in roughly 40 minutes. Requested a call for any issues. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067765 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | GWTP- ZW4 Memb Air Inlet V Failed to Close, Membrane Air Valve Failed, Shutdown. Notified Patrick F. He will look into it. | FLAG | stage2_low_confidence | 0.018801 | ML: above threshold (no LLM available) — 0.019 | failed [equipment_failure]; valve failed [infrastructure] | 0.018801 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather -15C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043332 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | VNPS- Tim H onsite for work on chlorine analyzers. Requested to activate RHRSTR duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | KSTP - Technician from Black and MacDonald called. He is on site for CO2 system maintenance. Requested to send OP to open the gate. Notified Joe M. He contacted contractor (Bernard 905 301 4919). Work rescheduled for tomorrow. Joe M directed HL pumps man/off. Plant is off for the night. # Consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064294 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | AUW14 - Placed all wells man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042351 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | GWTP- Back pulse fill V failed to close alarm came in again notified Joe M. Directed to clear alarm if it comes in as long as valve closes #consult | FLAG | stage2_low_confidence | 0.016282 | ML: above threshold (no LLM available) — 0.016 | failed [equipment_failure]; alarm [control_system] | 0.016282 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | GWTP- ZW5 recovery exceeded recovery SP. Alarm cleared upon acknowledgment | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057016 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | AUW14- Placed wells 1-4 in man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042678 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | NMMCBR- Rob P notified ROC they are done on site EG flushing as valve has been reopened in system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069645 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | KSSP- Mem oper area MUA 10 temp switch lo alarm. Disregard on shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057007 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | VNRSKS - Activated Duty 1 to keep BVPS pumps running. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046768 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMTKKC - Sanitary pump station high level alarm, notified Joe D. Ian W confirmed- sanitary pump is running. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071266 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | MARS, Rick L on site doing calibrations to the LIT, Notified Toronto operator Pooja and ARPS Operator Peter that there is work being done on the LIT and that it should be disregarded till the work is completed 13:15, Rick L is finished on site, notified Toronto and ARPS that the work is finished | FLAG | stage2_low_confidence | 0.0077294 | ML: above threshold (no LLM available) — 0.008 |  | 0.0077294 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | QVW34 - Treated total chlorine low alarm. Wells not running, No water directed to users. Alarm cleared in two readings. | FLAG | stage2_low_confidence | 0.013158 | ML: above threshold (no LLM available) — 0.013 | not running [equipment_failure]; alarm [control_system] | 0.013158 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | RHRSTR - Activated duty 1 to fill system for the interim procedure | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049678 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | SHTP - UV reactor 3 minor fault alarm, Jacob M requested disregard minor faults alarms from UV1,UV3. | FLAG | stage2_low_confidence | 0.012159 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.012159 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | SHTP - Treated Water Turbidity Fault alarm came in. Checked site. High lifts are not running. Called Jacob M. who will take a look 23:31 - Jacob M. called back to inform that this can be disregarded for the night. Jacob would like a call back if this starts to interlock any of the pumps #CONSULT | FLAG | stage2_low_confidence | 0.012331 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; not running [equipment_failure]; alarm [control_system] | 0.012331 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMETIB - Activated duty 1 to help offset with NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046546 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | VNPS/RHRSTR - Yash S. on site for planned network work. Deactivated BVPS and VNP8, placed pumps man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055159 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | AURSBS - Activated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041071 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | STW12 - Joe M requested man/start well 2 pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004531 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | ANW23 - Stephen B on site for generator run , chlorine analyzers maintenance and Health and Safety inspection. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057113 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | RHRSWA- Cell 2 Valve Fault Alarm. Came in during power blip. Valve is Local Open. Notified Tim H. He will reset tomorrow. | FLAG | stage2_low_confidence | 0.013051 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.013051 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | RHPSPA - Discharge header flow 1 LoLo alarm. Checked site, duty just deactivated and the pumps shut down. Cleared alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0068195 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | GWTP- Patrick F working on compressors. Disregard Low pressure alarms. | FLAG | stage2_low_confidence | 0.01385 | ML: above threshold (no LLM available) — 0.014 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.01385 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | MTETNL, Sean P on site, disregard intrusion alarms | FLAG | stage2_low_confidence | 0.0072722 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0072722 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NBET27 - Outlet temp lolo alarm. Checked site, trending shows the outlet water temperature slowly dropping. No indication of a heat trace fault. Contacted Jacob M who will check SCADA. 13:00 - NBET27 - Jake M will monitor the situation for one hour and call back. #consult | FLAG | stage2_low_confidence | 0.010877 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.010877 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 1 at MAPS 04:54 - Reverted all changes | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025324 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038512 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MTW3- Phil D onsite for Cl analyzer maintenance and running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050335 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | GWTP - ZW6 membrane tank hi level alarm. Spoke with Patrick F who stated the alarm will clear itself once the neutralization process is complete. | FLAG | stage2_low_confidence | 0.0079501 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079501 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | STETBR-Tower level lo STW12/3- Placed P2/3 in man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041272 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | AUW14- Joe D placed pumps man/off, working on chemical system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048427 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | NMETHW- Eric S onsite working on Total Chlorine Analyzer 16:06- Eric S finished onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037633 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | KSTP- Jerry Z and Patrick F on site for generator training. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059445 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | KSTP- Carbon Dioxide HiHi Alarm. Notified Jack P. Can disregard. While on the phone alarm cleared. Can disregard if it comes back in. CONSULT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069126 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NMETHW - Duty 1 just activated, deactivated NMETIB Duty 1 to offset towers. Reverted system changes. NMETIB duty 1 stop from 85 back to 75% and NMVCBA flow from 20 back to 40l/s. Confirmed with Cole W. | FLAG | stage2_low_confidence | 0.0077477 | ML: above threshold (no LLM available) — 0.008 |  | 0.0077477 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | KSETDP - Sean P. working on influent pH meter. Site offline | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063286 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | Angelica Chepiga signing in,weather -5C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -8C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | MAPS PD7 - pump 3 uncommanded stop alarm. Checked site, pump 1 has activated and is pushing flow. Pump 2,3,4 all interlocked on the pump 3 shutdown. Waited for interlock to clear and reset alarms. Duty 1 rotated to pump 2, monitored pump start. | FLAG | stage2_low_confidence | 0.012659 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012659 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | GWTP - Sutton header fluoride low alarm. Checked site, Sutton system is filling. Trending shows a dip of the fluoride reading which recovered slightly. Will monitor site. | FLAG | stage2_low_confidence | 0.011715 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.011715 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | KCETDS - Combine chlorine Low alarm, quick dip, value back to normal, cleared alarm. | FLAG | stage2_low_confidence | 0.0075081 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075081 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MKRSEM- Called Metro spoke with Mehdi to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065451 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim procedure | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063691 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NMW12 - Silicate pump 1 uncommanded stop and leakage alarm. Checked site, well recently activated, duty rotated to silicate pump 2. Will monitor silicate tank level to determine if silicate is leaking through possible broken lines. Sent email to OCO. | FLAG | stage2_low_confidence | 0.02092 | ML: above threshold (no LLM available) — 0.021 | alarm [control_system]; leak [infrastructure]; leaking [infrastructure]; leakage [infrastructure] | 0.02092 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NMVCBA - Placed valve in manual at 40 L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044479 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | GWTP - Sutton Header Fluoride Low alarm. Notified Patrick F, he is on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069124 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | HUB 2 Server - Kyle C restarting server. QVW34 - Tyler ZJ working on pumps, will run pumps. William M on site monitoring. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042063 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | JFRS - Activated duty 1 to keep reservoir high for the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051319 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | JFRS - Activated duty 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040872 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NRETCR - Activated duty 1 to fill the towers for the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050948 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | RHRSTR - Activated duty 1 to maintain reservoir level for the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052959 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | STW3 - Influent free chlorine hi alarm. Checked site, well recently activated. Noted that the dosing setpoint for the active chlorinator is higher than the desired setpoint. Re-applied the initial setpoint and monitored site. 10:33 - STW3 - Effluent free chlorine hi alarm triggered as the initial spike of free chlorine exits the contact tank. The influent free chlorine reading is dropping following the dosage changes made. Monitoring site. | FLAG | stage2_low_confidence | 0.018645 | ML: above threshold (no LLM available) — 0.019 | alarm [control_system] | 0.018645 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | AURSBS - Activated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041249 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NBW3 - Influent free chlorine lolo alarm. Checked site, well activated in schedule mode. Trending shows a sudden drop of the influent free chlorine reading on well start. Influent free chlorine residual recovered quickly. Cleared alarms, returned hypo pump 2 to duty 1 and reset alarm. Monitored well activation. | FLAG | stage2_low_confidence | 0.016578 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system]; alarms [control_system] | 0.016578 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MKPSSA, Combined Cl2 Residual lolo, Pumping Station is offline at this time, very little water going through the analyzer, Travis W was on site and took a grab sample | FLAG | stage2_low_confidence | 0.0074256 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074256 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NMETIB - Activated duty 1 to keep level offset from NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048026 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to two MAPS pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060547 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NBW3 - Influent Free Chlorine LoLo switch alarm came in. Checked site. Duty just activated. Well locked out on duty start. After 5 mins, influent levels came back to optimal range. 19:43 - Cleared alarms after 10 mins. Well re activated and will monitor | FLAG | stage2_low_confidence | 0.007264 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.007264 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | NMVCBA - Placed valve man/open at 40 L/s 04:07 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030115 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | KSTP - post chlorinator 2 low vacuum alarm. Checked site, post chlorinator 1 rotated into duty 1 and is operating. Able to clear alarm. | FLAG | stage2_low_confidence | 0.007571 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.007571 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMW1/2/13/16/15, Placed wells back to auto. Jason G called saying everyone is working well on his end and things can go back to normal operation. Notified Jason G that well 13 is faulted at this current time, he will look into it NMTKKC, Activated D1 to have the system filling for Jason G | FLAG | stage2_low_confidence | 0.017288 | ML: above threshold (no LLM available) — 0.017 | fault [equipment_failure]; faulted [equipment_failure] | 0.017288 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MARS - Parth P. and Rick L. continuing annual calibrations on analyzers and generator LITs | FLAG | stage2_low_confidence | 0.0073146 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073146 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMETIB - Activated Duty 1 to offset with NMETHW, ok with William M. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049944 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | YWS + NYWS Normal VNRSKS - Swapped supply pump to one MAPS one VNPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046217 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | KSTP - Settle water turbidity hihi alarm. Plant offline for the night, no water directed to users and no operations on site. | FLAG | stage2_low_confidence | 0.0089088 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0089088 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | JFPS- Generator Running Status Alarm. Will notify Ops RHMCMD- Valve 1 Fault ALarm. Pac Control Power Fail. Alarm cleared RHRSWA- Power fail. Alarm cleared | FLAG | stage2_low_confidence | 0.010461 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; alarm [control_system] | 0.010461 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | HLETPR- Jordan onsite testing low temp | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057343 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | GTWP - ZW8 recovery - Exceeded Recovery SP. Checked site, ZW8 completing a backwash sequence. Alarm status changed to normal while checking site. Alarm cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.0088852 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0088852 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | JFPS- Power Fail. Alarm cleared RHMCMD- Power Fail. Alarm cleared. RHPSWA- Power Fail. Alarm cleared RHRSWA- Power Fail. Alarm cleared RHPSPA- Power Fail. Alarm cleared BVPS- Pump 1 Failed to start. Alarm cleared | FLAG | stage2_low_confidence | 0.0078231 | ML: above threshold (no LLM available) — 0.008 | failed [equipment_failure]; alarm [control_system] | 0.0078231 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | BLETNL- Kyle C updating OIT, disregard heartbeat alarms until further notice. 13:00 Kyle C completed work | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0053152 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MKRSEM- Called Toronto (Paul) and requested pumps on. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061457 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | MKRSEM - low level alarm. Called Toronto Water (Paul) and requested they activate two pumps to push flow to MKRSEM. | FLAG | stage2_low_confidence | 0.0090907 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0090907 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | AUW14 - Placed pumps 1&4 back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043788 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | HLW2 - Placed well in auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041532 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | Carter D Signing In, -24D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041696 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | SHTP, KMNO Pump 2 Leak/Fault, Notified Jacob M, he will look into it | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; leak [infrastructure] | fault [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | BLW3 - Kyle C working on new PLC, performing tests, disregard Historian Heartbeat alarm. 09:00 Dan Z on site with Kyle C for testing. Monitoring. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052011 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | YWS + NYWS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038034 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -9 C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046282 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | VNPS - Tim H running generator , will attend re- chlor after for chlorine analyzers maintenance and chlorine leak alarm test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | STETTL - Joe M cleaning chlorine analyzers and performing Health and Safety inspection. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0072156 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | KCETDS - Inlet Riser Heat Tracing Fault alarm came in. Checked site. Duty recently activated. Checked trends and trending is okay. Called Jacob M. who directed to continue monitoring tower and to give a call back if level starts flatlining #CONSULT | FLAG | stage2_low_confidence | 0.021753 | ML: above threshold (no LLM available) — 0.022 | fault [equipment_failure]; alarm [control_system] | 0.021753 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | ARPS - Airport Rd Discharge Flow lo alarm came in. Activated duty at KLET27 as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006132 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | STETBR - Tower level low alarm. Placed STW2 and STW3 in manual mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055576 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NMVCBA - Placed valve man/open at 40 L/s 01:58 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030115 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | GWTP - Train 2 - transmembrane pressure lo alarm. Alarm status changed to normal shortly after the alarm triggered. Alarm reset on acknowledgement. | FLAG | stage2_low_confidence | 0.0076562 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076562 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | AUW14 - Joe D and Lee F completed work , site is back to normal OP. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050148 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | STETBR - Joe M cleaning chlorine analyzers , performing Health and Safety inspection. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071487 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMW12 - Silicate pump 1 leakage alarm outstanding. Alex B working on it. # CMU5 W11649902 | FLAG | stage2_low_confidence | 0.010551 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | 0.010551 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NBW5 - Jordan B working on chlorinator 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044268 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MARS, Parth P has finished annual calibrations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059614 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMVCBA, Placed valve in manual and set the flow to 40L/sec | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047975 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NMETIB - Increased Duty stop from 75% to 85% and lowered NMVCBA flow from 40 to 20l/s, confirmed with Cole W. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060885 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | VNPS PD7 - Pump 3 man/off MAPS PD7 - Pump 1 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039272 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NRETCR - Activated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041074 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | MARS - Adjusted low level alarm setpoint from 55% to 60% for the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059555 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NMETIB - activated duty 1@ 51% as per Alex B. to offset with NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050181 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | STETBR - Wess from town of Stouffville flushing in zone 1. Notified Joe M. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050281 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather -12C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043332 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two MAPS pumps to one MAPS one VNPS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067409 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | GWTP - Sutton header fluoride low alarm. Value has not recovered. Contacted Joe M again and he directed to increase dosing factor from 1.05 to 1.10 and monitor for another hour. #consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066611 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MARS - Called Toronto Water (Poriya) and requested to increase flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065538 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | BLW34, Dan Z is leaving site, Kyle C is still working on the historian heartbeat | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052853 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | STW12, STW3 - Placed manual/ currently running for STETBR fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050408 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MKRSEM, Notified Toronto operator paul to start filling the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062836 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMVCBA, Placed valve to 80L/sec NMVCIB, Placed valve to 40L/sec ROC doing this to help offset the towers as both are active | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031223 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NRETBR - Heat Trace 2 Fault alarm came in. Checked site. Tower is draining. Heat Trace 1 is on and normal. Tower is still trending. Will call out if tower starts flatlining | FLAG | stage2_low_confidence | 0.016995 | ML: above threshold (no LLM available) — 0.017 | fault [equipment_failure]; alarm [control_system] | 0.016995 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | AUPSRR- Ric L onsite for calibrations. Deactivated AURSOH and placed Ridge Road chemical pumps in manual after confirming with with Jason G. | FLAG | stage2_low_confidence | 0.0092239 | ML: above threshold (no LLM available) — 0.009 |  | 0.0092239 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MAPS PD7 pumps 1&3 man/off VNPS PD7 pumps 1&4 to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039127 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | ARPS - Peel OCWA (Peter) called to inform they are completing the daily pump rotation. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0072072 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMTKKC, Contractor on site notified ROC that the card reader isn't working, notified Security, they will look into it. Site is back to normal | FLAG | stage2_low_confidence | 0.0084358 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084358 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MARS - Cross Connect valve uncom. Close alarm. Cole W requested disregard alarm. valve local/closed. | FLAG | stage2_low_confidence | 0.0084488 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0084488 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | MARS, Notified Toronto operator Zoran to increase the flow to MARS as both sites that take water from the res are active and are drawing it down at a decent rate | FLAG | stage2_low_confidence | 0.0099537 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099537 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | AUW14, Deactivated D1 AURSBS, Deactivated D1 VNRSKS, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0023902 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | JFRS - activated duty 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040872 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | VNRSKS- Deactivated D1 VNPS PD7- placed P1/4 in man/off MAPS PD7- placed P1/3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037553 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NBET27 - Outlet temp lolo. Jake M called back to inform that he will not be attending site. Jake directed to continue to monitor site and if the temperature continues to decrease to monitor the fill and drain cycles. | FLAG | stage2_low_confidence | 0.0099767 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099767 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | NMETIB- Deactivated duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053971 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | HLW2- Stephen B requested to place chlorinators from "all stop" to "disabled" mode for duty change/rotation so that chlorinator 1 will run over the weekend. | FLAG | stage2_low_confidence | 0.0075488 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075488 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NMETHW - Activated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041172 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | GWTP- Generator Alarm. Jack P working on it with contractor. Patrick F working on fluoride probes. | FLAG | stage2_low_confidence | 0.0083767 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0083767 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NMW136 - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows that the influent free chlorine reading spiked and then returned to normal range within two reading intervals. Reset alarm. | FLAG | stage2_low_confidence | 0.011229 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011229 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | HLW2 - Eric S on site , working on chlorine analyzers. Placed well 2 pump man/off . | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050464 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | MAPS PD7 - Pumps 1&3 man/off VNPS PD7 - Pumps 1&4 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040177 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | RHRSWA - Power failure alarm/restored,alarm cleared. RHPSPA - pumps stopped and restarted/ generator off. | FLAG | stage2_low_confidence | 0.01623 | ML: above threshold (no LLM available) — 0.016 | failure [equipment_failure]; alarm [control_system] | 0.01623 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NBW3 - well 7 pump on schedule mode, Influent chlorine residual low/low lockout, value back to normal. Cleared alarms and restarted well 7 pump. | FLAG | stage2_low_confidence | 0.0087074 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0087074 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMTKKC - Jason G called with update, Ian W on site powered UPS, Jason G collected grab sample. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070142 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | NBW3- Influent Free Chlorine LoLo. Well interlocked on schedule mode start up. Reset alarms and well started back up. | FLAG | stage2_low_confidence | 0.0079957 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0079957 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | AUPSRR - Post Injection Free Chlorine Hi alarm came in. Checked site. Noticed levels are back to optimal range. Trends indicate a slight spike and then comes back down. Cleared alarm | FLAG | stage2_low_confidence | 0.01187 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.01187 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | JFPS- Tyler S called. Pump 1 will remain OOS Local off RHPSWA- Tyler S also notified that Pump 1 will remain Local off | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | YWS+NYWS Normal 20:38- GWTP- Backpulse tank 2 level hi alarm. Notified Joe M. Directed to backwash train 1 and activate KSTKWP Duty #consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0041088 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | MAPS- PD7 P2 Disch. Valve 1 Uncmd Close, PD7 P2 Uncmd Stop. Pump 3 took over in duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005539 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | GWTP - Joe M. called and directed to activated duty 1. Joe also informed that if a lo fluoride alarm comes in, it can be disregarded. Joe would like a call back if the LoLo alarm comes in | FLAG | stage2_low_confidence | 0.0097913 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0097913 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | QVETQS- William M onsite testing hi and low level alarms. | FLAG | stage2_low_confidence | 0.0080181 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0080181 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | AUW14 - Placed pumps 1&4 manual/currently running. Notified Joe D. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048304 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMTKKC - Joe D called , site on portable generator, Ian W with contractors working on site. Ian W will call later to transfer site to normal power. | FLAG | stage2_low_confidence | 0.0089391 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089391 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | RHPSPA - Lee F finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052483 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | RHPSWA - Sean P on site, rebuilding Pump 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042208 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | VNRSKS - Placed all VNPS PD7 pumps man/off and placed all pumps at MAPS PD7 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055218 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | VNRSKS - Swapped supply p[umps to one VNPS and one MAPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064382 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | VNPSCD, Pre-Inj Free Cl2 Hi//MonoChloram lo alarm, notified David T, he will look into it but isn't to concerned, if the hihi comes in, he would like a call | FLAG | stage2_low_confidence | 0.0081475 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081475 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | HLW2- Eric S finished onsite. Placed well back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047576 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NRETCR - Deactivated duty 1 so JFRS can fill for the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051027 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | MTW12, MTW3 - Phil D requested to place pumps manual mode. Currently running. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052282 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | AUPSOH - Lee F on site for pumps 1-4 motor service. 13:25 Lee F working on pumps 3&4 , deactivated Duty 1 and placed pumps man/off . | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044673 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MTW12 - MTW12 to MTETNL Commfail alarm. Cleared alarms. Well 2 pump restarted. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0055917 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Mehdi) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069678 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | RHRSTR- Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053751 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | GWTP Low lift Patrick F cleaning turbidity meter, chlorine analyzers, testing chlorine leak alarm and Health and Safety check. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -4C and snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044927 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | STETBR - Tower Level Lo alarm came in. Checked site. Placed STW12 and STW3 man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0062692 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | NBW5- Turbidity Hi Alarm. Rotated silicate duties so pump 1 running. Will monitor. 14>28- Turbidity still hi. Notified Jordan B. He will take a look. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065349 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | KLPSWL- Benson S onsite for work orders. Generator run, Cl Leak detection, scrubber test, all analyzers, valve exercising, hi/low temp and health and safety. | FLAG | stage2_low_confidence | 0.026905 | ML: above threshold (no LLM available) — 0.027 | work order [maintenance_action]; leak [infrastructure] | 0.026905 | 0 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | MAPS PD7 - Pumps 1&3 man/off VNPS PD7 - Pumps 1&4 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040177 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | KSTP - Donald M called, working on site, plant is off until further notice. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064219 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMTKKC - Commfail alarm, not able to deactivate Duty 1. Notified Jason G. NMTKKC - Ian W will call Jason G . | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | SUETDR - Jackie S on site for chlorine analyzers maintenance, Low temp alarm testing and Valves exercising. | FLAG | stage2_low_confidence | 0.0081966 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081966 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NMW12 - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows the influent free chlorine reading spiked on well activation. monitoring site to ensure the influent free chlorine residual reading drops to normal range. | FLAG | stage2_low_confidence | 0.012931 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.012931 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MKRSMR - Travis W testing flood alarm, Hi/low level alarms, chlorine analyzers maintenance and performing Health and safety inspection. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | AUPSOH- Lee F finished onsite. Placed Pumps 3,4 back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004907 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MAPS- Ric L finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005474 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | AUW14, Placed well 1/4 man/off to take more from AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047074 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | QVETQS - System Pressure Low alarm, quick dip, recovered immediately at QVW12 duty stop. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060837 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | STW12 - Joe M requested STW12 pump 1 man/on. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044923 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing in -8C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037143 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NMETHW - Riser pipe heat trace controller 1 fault alarm. Joe D attending site after leaving RHPSWA. Created CMU5#W11645865 #CMU5 | FLAG | stage2_low_confidence | 0.010103 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; alarm [control_system] | 0.010103 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040295 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -23C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046216 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MKPSSA, Gary P notified the ROC that the station is back to normal working order, valves are open. notified him to get in contact with Travis W to let him know that the residuals may need to be looked at. A grab sample was taken on site | FLAG | stage2_low_confidence | 0.013308 | ML: above threshold (no LLM available) — 0.013 |  | 0.013308 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | GWTP - Jack P running generator, disregard alarms. | FLAG | stage2_low_confidence | 0.0077198 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0077198 | 0 | 0
2026-02 | 2026-02-06 | All Water System ROC General | ROC | MKRSEM - Reservoir 1 Level Lo alarm came in. Called Toronto Water (Brett) and requested two pumps on 03:08 - Called Toronto Water (Brett) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054082 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | Adam Button signing in -8C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004176 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | AURSBS - Deactivated duty 1, in preparation for interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047122 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | MKRSEM - Reservoir low level alarm. Called Toronto Water (Zoran) and requested two pumps to push flow to MKRSEM. NMETHW - Activated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053403 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | QVW12 - Justin Q and Ben H on site. Requested disregard Low pressure alarm. Testing. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055998 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | AUW14 - Lee F on site, working/locking out well 3 pump. Will call when work complete. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005122 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MKPSSA - Travis W on site for station check. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055339 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | KCETFS, PAC Rack 1-8 Alarm. Low priority, notified Benson S as he is responsible for the site, he will be passing it on to the on call operator 15:30, Jacob M called RO asking about the alarms, notified him about the original call out, Jacob M requested for PCS on call to take a look into it. Notified Ian W, he will look into, Ian believes it to be a blown fuse. 15:36, Notified Jacob M that Ian W will look into the issue 16:00, Ian W is heading to site CMU5: W11650111 | FLAG | stage2_low_confidence | 0.0075832 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0075832 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | NMETHW - ET @ 74%, notified Alex B, ok to activate NMETIB when NMETHW @75% to offset towers. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054691 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to two MAPS pumps for one fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066198 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | STETTL - Tower is struggling to fill while STETBR duty i1 is also active. Activated STW1 in manual mode to assist fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006539 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | RHRSTR - Deactivated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041621 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | AURSBS - Activated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041249 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to one MAPS one VNPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062908 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | AUW14- Placed wells back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042911 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | QVW12 - Influent free chlorine hi alarm. Checked site, influent is above target. Checked chemical dosing setpoints. The dosing setpoint for the active chlorinator has climbed above its setpoint. Re-applied initial chlorine dosage factor. | FLAG | stage2_low_confidence | 0.012201 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.012201 | 0 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | MTW3 - SIlicate pump 1 fault alarm. Checked site, well has been running for several hours. Silicate pump duty rotated to silicate pump 2 and normal operations resumed. Unable to clear alarm. Sent mail to OCO. NBW5 - Turbidity high alarm. Checked site, well recently activated. Trending shows a pattern of turbidity spikes on well start. Will monitor site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MAPS PD7- Ric L onsite for calibrations. Placed Pumps man/off. MAPS PD8- Ric L working on flow meter. No pumps are running. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005377 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto, as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061178 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | HLW2 - Treated Free Chlorine HiHi alarm came in. Checked site. Well is running. Trends indicate a spike. After 10 mins, treated free chlorine levels came back to optimal range and alarm cleared | FLAG | stage2_low_confidence | 0.0098228 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0098228 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | VNRSKS - Placed all pumps at VNPS PD7 Man/off and placed all pumps at MAPS PD7 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055385 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | QVETQS - System Pressure Lo alarm came in. Quick dip in trends but pressure comes back to optimal range. Alarm has cleared | FLAG | stage2_low_confidence | 0.0093796 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0093796 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | NMETIB - Activated duty 1 to help offset with NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046546 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | JFPS - WPD GEN xfer switch hydro power. Checked site, generator is running. Able to reset alarms. Pumps were not running when power failed. Operations normal. RHPSPA - Site hydro failure alarm. Checked site, trending shows flow did stop but the pumps started again. Operations normal, cleared alarms. RHPSWA - Site power failure alarm. Checked site no generator on site. Unable to reset power related alarms but the pump alarms did reset. Operations Normal RHMCMD - Valve 1 and valve 2 fault alarms. Checked site, valves are showing as closed but still registering flow. Shortly after the valves showed as open in manual again. Cleared alarms, operations normal. AUMCBS/VNMCBA - Control panel power failure. Trending shows normal operations on site. reset alarms. | FLAG | stage2_low_confidence | 0.056574 | ML: above threshold (no LLM available) — 0.057 | fault [equipment_failure]; failed [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.056574 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal QVW34 - influent free chlorine hihi alarm. Checked site, well is running in schedule mode. Trending shows a sudden reductio in flow production by the well but the chemical dosing stayed the same resulting in a high influent free chlorine reading. Adjusted the chlorinator dosing factor as it had increased slightly above the desired setpoint. Monitored site and the influent free chlorine reading dropped on the next reading. Will monitor the effluent free chlorine residual. NMTKBS - Activated duty 1 to maintain tank level for the interim procedure. ARPS - Peel/OCWA (David) called to inform he is rotating pump duty. | FLAG | stage2_low_confidence | 0.025001 | ML: above threshold (no LLM available) — 0.025 | alarm [control_system] | 0.025001 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMTKKC - Sanitary pump fail to stop alarm, notified Jason G. He is on site. Contractor cut a power cable. No power on site. NMW12, NMW136, NMW15 Commfail alarm . Jason G requested all wells place man/off. TK at 73%, Jason G investigating on site, will call back. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | KSTP - low lift pump 3 uncommanded stop alarm. Checked site, low lift pump 2 accepted duty 1 and is running. Reset alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071299 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | GWTP - ZW trans membrane pressure low alarm. Alarm status changed to normal shortly after alarm triggered. Alarm reset on acknowledgement. | FLAG | stage2_low_confidence | 0.0096664 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0096664 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWs + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033588 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | VNRSKS - Deactivated duty 1 in preparation for interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046931 | 0 | 0
2026-02 | 2026-02-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | VNRSKS - Deactivated duty. Switched pump 2 at MAPS PD7 man/off and placed pump 2 at VNPS PD7 into auto 03:00 - Placed PD7 to VNPS PD7 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003989 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Brett) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069673 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | QVETQS - System Pressure Lo alarm came in. Quick dip in trends but pressure comes back to optimal range. Alarm has cleared | FLAG | stage2_low_confidence | 0.0093796 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0093796 | 0 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | MKPSSA - discharge lo pressure. Confirmed with Dwayne L. linear team doing valving at discharge of facility at McCowan and 16th Ave. Req. not to run pumps. Emailed ROC, Linear and East teams. | FLAG | stage2_low_confidence | 0.0089474 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089474 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | KBSP, Marcus R on site, testing the Filter Inlet Flood/Alum Leak-Flood alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; leak [infrastructure] | flood [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | SUSP- UV ch1 critical fail/ high level/common critical alarms. Flow started up and channel 2 active disregard on shift report. Alarms cleared upon acknowledgement. | FLAG | stage2_low_confidence | 0.0099347 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0099347 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | NBSP - Inlet channel Hi alarm, Mech Bar screen fail to stop and OOS alarms. All alarms cleared in a few minutes. Will monitor. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | SUSP- UV ch1 critical fail/ high level/common critical alarms. Flow started up and channel 2 active disregard on shift report. Alarms cleared upon acknowledgement. | FLAG | stage2_low_confidence | 0.0099347 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0099347 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | NMSSBP - Talha H working on OIT's and has directed to disregard historian heartbeat alarms. | FLAG | stage2_low_confidence | 0.0093432 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0093432 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | KCSSKR - Site back to normal OP, Dan H leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060906 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -5C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | SUSP - UV System Critical Failure, UV Ch 1 High Level, and UV CH 1 Common Critical Alarms came in. Checked site. Site just activated. Alarms value turned to normal and cleared right away. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.024202 | ML: above threshold (no LLM available) — 0.024 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.024202 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | BLSS - Young J leaving site. Normal operations have resumed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063231 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | HLSSBS- Hydrogen Sulphide Sample 1 Fault Alarm. Disregard as per SCADA Report | FLAG | stage2_low_confidence | 0.010832 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.010832 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | Carter Dunn Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052492 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | MTSP - Ian W working on the OIT and has directed to disregard the historian heartbeat alarm. | FLAG | stage2_low_confidence | 0.0081624 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081624 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | KSSP- Neil O on site to work on UV system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055137 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | SUSP- Influent Flow HiHi Alarm. Quick spike. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067146 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | AUSS- Kyle B from PCS is working on P4 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043817 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | NMSSHS, PAC Comm fail, Notified Yash S, he is looking into it | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | SUSP- UV ch1 critical fail/ high level/common critical alarms. Flow started up and channel 2 active disregard on shift report. Alarms cleared upon acknowledgement. | FLAG | stage2_low_confidence | 0.0099347 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0099347 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | Adam Button signing in -3C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004176 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | SUSP - Ian W testing a new UV Bypass alarm, requested disregard until further notice. 15:55 Ian W finished on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system] | bypass [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | AUSSYS - Odour control e stop alarm. Kevin S signed in on site in the logbook. Called Kevin who will investigate the alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | Connor Smith signing in -10C Windy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042119 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | AUSSSR - Aysix System Heartbeat alarm came in. Ack/rest and site went back to normal operations | FLAG | stage2_low_confidence | 0.0082071 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0082071 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | SEOC4 - Shaft 4 to shaft 2 comm failure, PAC communication failure. Gound generator running status. Status went to normal within couple minutes and able to clear alarm | FLAG | stage2_low_confidence | 0.016508 | ML: above threshold (no LLM available) — 0.017 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.016508 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | BLSS- Young J onsite for south collector repairs. Will be shutting off all pumps. Disregard all alarms. | FLAG | stage2_low_confidence | 0.018199 | ML: above threshold (no LLM available) — 0.018 | repair [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.018199 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | AUSS - Marcos T on site and will be turning off the Odor control system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063542 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | Adam Button signing in 5C Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041687 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | NBSP- Aeration basin 2 back DO lo alarm came in. Recovered after 12 mins alarm cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060422 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | NMSSHS - Evgeni S rebooting OIT, disregard heartbeat alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069797 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | KCSSKR - Generator running due to , Duty was not active at the time Alarm panel AC power restored dialer alarm came in right after | FLAG | stage2_low_confidence | 0.0078597 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0078597 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather +4C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | KSSP - UV Panel 1 Lamp Low intensity alarm, disregard as per shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0056999 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | MTSP, Bar Screen Fault Alarm, Terry R called back, informed the ROC that the bar screen will be off for the night and that they will be diverting to the lagoon till the issue is resolved | FLAG | stage2_low_confidence | 0.024349 | ML: above threshold (no LLM available) — 0.024 | fault [equipment_failure]; alarm [control_system] | 0.024349 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | LSSS - Ubah student from EME , sampling P6, assigned P6 to duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | LSSS - Pump 1 fault alarm. Notified Chris R, he will investigate. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | Ethan U signing in Weather: 0 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | EGSSSC- Diesel containment flood alarm came in Notified Cam B. Directed to disregard alarm #consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; containment [safety] | flood [critical]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | Carter D Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | SEOC Fan 1 and Fan 2 Uncommanded stop alarms. Contacted Phil R who directed to clear alarms. Alarms cleared and fans activated. | FLAG | stage2_low_confidence | 0.0084138 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0084138 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | MTSP, Bar Screen Fault, notified Terry R, he is looking into it | FLAG | stage2_low_confidence | 0.010099 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.010099 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038155 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | SHSP - Ian W on site to test the new UV system bypass alarm. Ian has directed to disregard this alarm until the work is done. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system] | bypass [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | KBSP, Marcus R on site, working on the UV system and the water service system on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067444 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | AUSS - Pump 5 W discharge header MV3 failed to open alarm. Checked site, duty rotated to pump 3 which is active and pushing flow. Reset alarm. | FLAG | stage2_low_confidence | 0.014937 | ML: above threshold (no LLM available) — 0.015 | failed [equipment_failure]; alarm [control_system] | 0.014937 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | NBSP- System minor fault alarm came in. switching from bank 1a to bank 1b disregard on shift report NMSSHS- PAC comm failure. Cleared upon acknowledgement. Trends show gaps. Notified Yash S will investigate | FLAG | stage2_low_confidence | 0.015927 | ML: above threshold (no LLM available) — 0.016 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system] | 0.015927 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | KCSSKR - As per Daniel H stakeholders onsite for a feasibility study. Directed to disregard alarms including wet wells Hi and HiHi alarms. He is on site monitoring. | FLAG | stage2_low_confidence | 0.012282 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012282 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046808 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | KBSP - Water sump level hi switch alarm. Marcus R called to inform he triggered this alarm. | FLAG | stage2_low_confidence | 0.0081413 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081413 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | NMSSBP- Mech Screen 1 Overtorgue Alarm. Screen 2 already OOS. Notified Chris R. He will attend site. 04:00- Finished onsite. Screen 1 back into service. 05:35- Mech Screen 1 Overtorque Alarm came back in. Chris R will attend site. W11688330 CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | NMSSHS/EGSSSC- Evgeny S working on OITs disregard historian heartbeat alarms | FLAG | stage2_low_confidence | 0.0087092 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0087092 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | SHSP - Generator running, clarifier 2 rake drive cut, UV major. Power blip in area. Restored shortly after but alarms outstanding. Called Gavin W, will head to site SHSSDK - Generator running CMU = W11683632 | FLAG | stage2_low_confidence | 0.0089457 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0089457 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | HLSSBS - Hydrogen Sulphide Sample 1 fault alarm- disregard after hours as per shift report. | FLAG | stage2_low_confidence | 0.011561 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system] | 0.011561 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | SEOC - OCF Water Supply Unusual Flow Rate alarm came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0079889 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079889 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | SEOC5, Comm fail, Notified Yash S, he is looking to fix the issue 15:49, Yash S ended up going to site to fix the issue, he is now finished on site CMU: W11695267 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | KBSP, Marcus R on site, working on aeration probe alarms | FLAG | stage2_low_confidence | 0.0075281 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0075281 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | KSSP= Scum Chamber hi level alarm came in. Disregard on shift report | FLAG | stage2_low_confidence | 0.0072718 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072718 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | NMSSBP- Talha H done rebooting OIT cleared historian heartbeat alarm KBSP- Ian W done work on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063231 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | SEOC OCF - Fan 1 and Fan 2 uncommanded stop and General HVAC alarms. Fan 1 and Fan 2 restarted after ack/reset alarms. General HVAC alarm outstanding. Disregarded as per SCADA review. | FLAG | stage2_low_confidence | 0.0095011 | ML: above threshold (no LLM available) — 0.01 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0095011 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | KSSP - RAS combined no flow alarm. Checked site, all RAS pumps manual/off but the WAS pumps are active indicating that operators are wasting sludge | FLAG | stage2_low_confidence | 0.010239 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010239 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | MTSS - David D on site to complete a dialer alarm test. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065236 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | SECC, Yash S on site, replacing OITs and working on system panel | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060955 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | Carter D signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -8C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | LSSS - Pump 1 Fault alarm. Checked site, duty 1 is assigned to pump 5 which is active. Pump 1 is listed as out of service duty 7 in the shift report. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; out of service [equipment_failure]; alarm [control_system] | fault [equipment_failure]; out of service [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | KSSP, Neil O is on site, working on the UV alarms | FLAG | stage2_low_confidence | 0.007307 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.007307 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | NBSP - UV system minor fault alarm. Checked site one UV bank is active and the duty for the UV banks recently swapped. Alarm is a disregard on the shift report as long as one bank is active. | FLAG | stage2_low_confidence | 0.02466 | ML: above threshold (no LLM available) — 0.025 | fault [equipment_failure]; alarm [control_system] | 0.02466 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -16C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046216 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | Ethan U signing in Weather: -2c | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003463 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | Ethan U signing in Weather -4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | NMSSHS- Yash S restored comms on site trends okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005695 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | KSSP - UV Panel 1 Lamp low intensity and UV Ch1 bank 1A Low UV intensity fault alarm. Checked site , UV 1 is running. High priority alarms, not in the shift report. Notified Cam B, he will investigate. # Consult | FLAG | stage2_low_confidence | 0.013974 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.013974 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | KSSP - UV CH.1 Bank 1A Low UV Intensity Fault alarm came back in. Alarm was coming in and immediately turning normal. Alarm came back in but did not clear on its own. Checked site. Noticed that UV Ch 1 is running. Called Cam B. who will investigate further #CONSULT | FLAG | stage2_low_confidence | 0.01833 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.01833 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | NMEQBP- Kingsley M is rebooting OIT on site. Disregard historian heartbeat until done KSSP- Ian W testing UV bypass alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system]; alarms [control_system] | bypass [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | KBSP, Marcus R is working on the SCUM tanks NBSSJA, Parth P/Rick L are finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004718 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | NBSP - UV System Minor alarm. Checked site, UV Bank 1 B is running. Disregard alarm as per shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065578 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | Carter Dunn Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052492 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | BLSS - Young J called to inform that the south forcemain and pump 5 will remain out of service. Normal operations have resumed through the other pumps. Young J leaving site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | NMSSBP- Mech screen 2 fault alarm. Notified Kevin S will try to clear remotely and reach out to CMS if work order is need to fix issue. | FLAG | stage2_low_confidence | 0.026463 | ML: above threshold (no LLM available) — 0.026 | fault [equipment_failure]; work order [maintenance_action]; alarm [control_system] | 0.026463 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | SUSP- UV CH 1 common critical/high level and critical failure alarm came in. Channel 2 in D1 alarms cleared upon acknowledgement | FLAG | stage2_low_confidence | 0.013772 | ML: above threshold (no LLM available) — 0.014 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.013772 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | SHSP - Ian W working on OIT, disregard Historian Heartbeat alarm for the duration of the work. 13:19 Ian W completed work | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0049753 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | BLSS- Young J onsite with contractors for South Collector work. WIll be placing all pumps off. and isolating forcemain. Disregard alarms while onsite. | FLAG | stage2_low_confidence | 0.012326 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012326 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | KBSP - Dan H on site to oversee the generator TSSA upgrades. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059966 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | HLSSBS- Terry C and Bill V on site to work on P3 NMSSBP- Mech screen 1 overtorque alarm came in. Notified Kevin S closed gate 2 as 1 was still available. Will try to reset alarm and will escalate if alarm cannot be reset. Talha H rebooting OIT disregard historian heartbeat alarm | FLAG | stage2_low_confidence | 0.011378 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011378 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | NMSSHS - PAC Communication failure alarms multiple times. Notified Yash S. He will investigate. | FLAG | stage2_low_confidence | 0.017482 | ML: above threshold (no LLM available) — 0.017 | failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system] | 0.017482 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | MTSP - Ian W testing the UV bypass alarm. Ian directed to directed to disregard the alarm until his work is complete. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system] | bypass [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | NBSP- Alum ROC alarm/ tank lo alarm came in. Alum tank filled yesterday level was not low before LIT level dropped suddenly. Trends recovered. Able to reset alarms SUSP- UV ch1 critical fail/ high level/common critical alarms came in. Flow started up and channel 2 active disregard on shift reports. alarms cleared upon acknowledgement | FLAG | stage2_low_confidence | 0.015997 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system]; alarms [control_system] | 0.015997 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | AUSS- Satnam M called and requested to manually open Pump 3 MV4 valve. placed manual open. Valve fully opened. Placed back into auto. He is leaving site. | FLAG | stage2_low_confidence | 0.0074377 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074377 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | QVSSSC- Inlet Channel High Switch Alarm. Disregard as per SCADA Report. | FLAG | stage2_low_confidence | 0.0073922 | ML: above threshold (no LLM available) — 0.007 | scada [control_system]; alarm [control_system] | 0.0073922 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | BLSS- Young J called and requested on call Electrician to attend site for assistance with South Main Vlv Overtorque. Notified Satnam M. W11683750 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043305 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | EGSSSC- Evgeny S rebooting OIT disregard historian heartbeat until done | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066981 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | LSSS- P 1 motor trip on high temp. Rotated to P5 automatically Notified Chris R will create W/O | FLAG | stage2_low_confidence | 0.008825 | ML: above threshold (no LLM available) — 0.009 | trip [equipment_failure] | 0.008825 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather -7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | KBSP - UV Ch2 bank 1A Low UV intensity fault alarm, UV Ch 2 Common Minor alarm, UV channel 2 in running - Disregard alarms as per shift report. | FLAG | stage2_low_confidence | 0.015065 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.015065 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS normal Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046291 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | QVSSSC, HLSSBS - Talha H completing an OIT reboot. Talha has directed to disregard the associated historian heartbeat alarm. | FLAG | stage2_low_confidence | 0.015415 | ML: above threshold (no LLM available) — 0.015 | sso [critical]; alarm [control_system] | 0.015415 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | NBSP- Alum tank level lo/ ROC alarm came in. Second time it has come in today. Left outstanding and emailed west waste water about issue | FLAG | stage2_low_confidence | 0.010088 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010088 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | HMSS - Barscreen 1 and 2 not in auto alarm. Called Lauren S who is on site and will swap the bar screens back to auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066172 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | KBSP- Ian W on site to test UV bypass alarms. Disregard until done work 10:51- KBSP- Ian W working on OIT disreagrd historian heartbeat until done | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system]; alarms [control_system] | bypass [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | KSSSQW- Wetwell 1 LOE alarm came in. Trends show potential issue with LIT 1. Emailed North wastewater. Controlling LIT is LIT 2. Site okay. | FLAG | stage2_low_confidence | 0.0077146 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077146 | 0 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | Connor Smith signing in -8C cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00423 | 0 | 0
2026-02 | 2026-02-27 | All Wastewater System ROC General | ROC | MTSP, Dewatering Press Fault, Notified Terry R, directed to disregard at this time, Maint will be looking at it on Tuesday (March 3rd) | FLAG | stage2_low_confidence | 0.010521 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure] | 0.010521 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | NBSSJA, Rick L/Parth P on site, working on the Diesel LIT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059024 | 0 | 0
2026-02 | 2026-02-25 | All Wastewater System ROC General | ROC | KSSP- Neil O on site for UV work | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052797 | 0 | 0
2026-02 | 2026-02-26 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | SEOC4 - Shaft 4 fan duty rotation imminent alarm. Disregard as per the shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059806 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | AUSS, Bar Screen not in auto, notified Phil R, he is heading to site CMU5: W11627091 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038746 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -11C and partly cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046527 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | KSSP - Makeup Air Unit 6 Temp Sw Lo alarm came in. Disregarded as per shift report YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0044108 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | SECC, HVAC General Alarm/O2 Monitoring Alarm, Phil R was heading to do his Sunday rounds, notified him that these 2 alarms came in on Christians night shift again (went out on Saturday to clear them). Directed to disregard for the night, someone will look at it on monday | FLAG | stage2_low_confidence | 0.013889 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system]; alarms [control_system] | 0.013889 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | SUSP - UV System Critical Failure alarm came in. Checked site. Alarms went normal. Occurred on plant startup. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.019017 | ML: above threshold (no LLM available) — 0.019 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019017 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS+ YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048651 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | AUSS - Phil R. called to inform that he will need a second person to assist with the bar screen. Called Young j. no answer. Called Neil O. who will speak with Phil R. 18:30 - Neil O. called back to inform that he is headed to site. CMU5 Created W11627111 #CONSULT #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055222 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | NMSSHS- Barry M onsite running diesel generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060095 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | KSSSQW- Darren B finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056097 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | HMSS- Illegal entry alarm no OPS on site followed up with security spoke with Divij who will dispatch security to site | FLAG | stage2_low_confidence | 0.008684 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.008684 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | BLSS. Screen Upstream Lvl hihi, trends look completely off, notified Young J, he will look into the issue consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005514 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | SUSSWB- Venthilation H2S hihi alarm came in. Notified Cam B. Directed to disregard | FLAG | stage2_low_confidence | 0.0089331 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; h2s [safety] | 0.0089331 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | LSSS, Wet Well 1/2 Screen Differential Level LOE/hihi alarm, contacted Phil R, he is heading to site CMU5: W11631417 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0050557 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | KBSP- Lauren S running generator on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054331 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | SUSSHS- Talha H working on OIT. Disregard Heartbeat Alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069633 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | HLSSBS- Historian heartbeat alarm came in. Notified Kyle C will investigate SUSSHS-Talha H rebooting OIT Disregard historian Heartbeat alarm until done GRSSWA- Talha H rebooting OIT Disregard historian Heartbeat alarm until done | FLAG | stage2_low_confidence | 0.01039 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.01039 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | KSSSQW- Darren B onsite for wetwell cleaning. Disregard related alarms. Also informed of Pump 3 Vibration Out of Range Alarm that came in. | FLAG | stage2_low_confidence | 0.014455 | ML: above threshold (no LLM available) — 0.014 | vibration [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.014455 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, -15D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042054 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | AUSS- Kyle B from PCS onsite working on UPS Faults. | FLAG | stage2_low_confidence | 0.011181 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure] | 0.011181 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | KBSP- Lauren S on site to run generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00544 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | NMVCBP - EGSSSC force main pressure lolo alarm. Checked site, pump is running and flow is heading to Newmarket pumping station. Email from Niel O stated this alarm can be disregarded if it comes in early morning while the pumps are running. Cleared alarm. | FLAG | stage2_low_confidence | 0.01681 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system] | 0.01681 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | SUSP- UV ch 2 bank 2 a low UV intensity fault alarm. Disregard on shift report as dosage okay. | FLAG | stage2_low_confidence | 0.011956 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system] | 0.011956 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | SUSP - UV CH.2 Bank 2A Low UV Intensity Fault alarm keeps coming in. Neil informed this can be disregarded. Neil also directed to disregard the sludge hi alarm that may come in later tonight | FLAG | stage2_low_confidence | 0.018613 | ML: above threshold (no LLM available) — 0.019 | fault [equipment_failure]; alarm [control_system] | 0.018613 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, -11D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042054 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | SUSP- Bar screen hi level alarm. Notified Mike B. will take a look on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006963 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | KBSP. Young J called the ROC to request a CMU5 for Kyle C. Kyle C will be looking into the effluent trending issue CMU5: W11627065 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049352 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | NMVCBP - EGSSSC FM Pressure Lo alarm and ROC FM Pressure Lo alarm came in multiple times. Neil was aware and is headed to site. CMU5 Created W11627122 19:50 - Neil called back and requested Brent S. to give him a call. Called Brent S. 20:15 - Neil called back to inform that he is finished on site and has placed the ROC Forcemain valve in duty 2. The alarms can continue to be disregarded as long as the pumps are running when the alarms come in and the pressure comes back to optimal range within 5 mins #CONSULT #CMU5 | FLAG | stage2_low_confidence | 0.012955 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012955 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | KSSP - Alum Chem Rm MUA - 11 Differential pressure Switch hi alarm came in. Checked site. Fan is running. Will call if the low temp alarm comes in. Will send an email to Neil O. | FLAG | stage2_low_confidence | 0.0093121 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0093121 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | SUSP- Mike B onsite running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057342 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | MTSP- Generator Running Status. Called Marcos T. He is onsite running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069549 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | HMSS- Young J on site to run generator, test drywell flood alarm, hi lo temp and exercise valves on each pump | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | KBSP- Theo from AB on site. Grinding on generator room may cause smoke detection alarms to come in. Theo will call back when done. | FLAG | stage2_low_confidence | 0.020032 | ML: above threshold (no LLM available) — 0.02 | smoke [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.020032 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | AUSSYS- Kevin S onsite for generator run. Also testing hi/low temp and drywell flood alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-01 | All Wastewater System ROC General | ROC | LSSS - Bar Screen 1 Fault alarm came in. Checked site. Called Phil R. who directed to disregard alarm and will take a look first thing in the morning. #CONSULT | FLAG | stage2_low_confidence | 0.011151 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; alarm [control_system] | 0.011151 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | Connor Smith signing in -15C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042123 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | SUSSHS- Cam B onsite running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057659 | 0 | 0
2026-02 | 2026-02-02 | All Wastewater System ROC General | ROC | SUSP - Sludge Tank Level HiHi alarm came in. Disregarded as per Neil O. YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055242 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | YDSS+YNSS normal Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046291 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | KSSP- Headworks building flood alarm came in. Notified Neil O. Chris C on site testing alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | SUSP- UV system Critical failure/ ch1 high level/UV CH.1 Common Critical Alarm. All alarms cleared upon acknowledgment. UV2B running normal. | FLAG | stage2_low_confidence | 0.01448 | ML: above threshold (no LLM available) — 0.014 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.01448 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | QVSSSC- Tyson C will attend site. created CMU5 W11653911 #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042844 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | NBSP - Alum pump 3,4 & 5. Alum pump 5 general alarm. Alum pumps 2 & 4 running at the time. Informed Lauren S, will look into issue Consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065597 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | Ethan U signing in Weather -4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | BLSS, Pump 1/4 had an emergency stop, all pumps were turning off, security system showing armed, contacted Lauren S as all pumps are randomly turning off, Lauren S directed to call Dan H as he is doing work at the site all night. Contacted Dan H for confirmation and confirmed to disregard alarms at still till hes finished consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system]; alarms [control_system] | emergency [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | AUSS- Dan K. done on site was able to get coolant temp alarm cleared. Heater is back on line and directed to disregard alarm if it comes back in | FLAG | stage2_low_confidence | 0.0098731 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0098731 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | RHAMF - Kyle C on site to complete work with Kevin Shaji. Kyle has directed to disregard all alarms from site. | FLAG | stage2_low_confidence | 0.0097005 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0097005 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | BLSS - Power outage, Generators 1 and 2 running alarms. Notified Gavin W. # Consult HMSS - Power blip , Pump 2 fault alarm placed man/off. 4 pumps available. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | Connor Smith signing in 2C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041757 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | AUSSSR, Line 3 Valve Overtorque Alarm, Notified Chris R, he is heading to site CMU5: W11676699 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0044534 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | BLSS - Dan H called, station back to normal operation. Dan H and contractors leaving site. | FLAG | stage2_low_confidence | 0.0072589 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072589 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | KSSP- UV ch 1 bank 1a Low UV intensity fault. No dip in intensity or dosage. Alarm cleared upon acknowledgement | FLAG | stage2_low_confidence | 0.012877 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.012877 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | QVSSSC- Kevin K called back. Power has been restored to site and no Vac truck required. Kevin K notified ROC that he called Wessuc to cancel truck and they are no longer being dispatched. Tyson C on site and Kevin K will be shortly to troubleshoot outstanding issues | FLAG | stage2_low_confidence | 0.015204 | ML: above threshold (no LLM available) — 0.015 |  | 0.015204 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | BLSS - Site power failure alarm. Checked site, utility power has been restored and the generators have shut down. Alectra map still shows a local power outage but it is affecting a much smaller amount of customers. Will monitor site to ensure proper operation | FLAG | stage2_low_confidence | 0.033384 | ML: above threshold (no LLM available) — 0.033 | failure [equipment_failure]; alarm [control_system] | 0.033384 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | RHAMF1 - Power blip, generator started and stopped. Fan 1 and Fan 2 VFD faults alarm came back. Jimmy from NAC on site, reset alarms. Fans 1and 2 restarted. | FLAG | stage2_low_confidence | 0.014916 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.014916 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | NBSP- UV system minor fault. Disregard on shift report as banks transfer over | FLAG | stage2_low_confidence | 0.010903 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure] | 0.010903 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | NMVCBP - Parth P finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052949 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDOC - Eric S leaving site, will attend site another time to work on biofilter drain pH | FLAG | stage2_low_confidence | 0.0072278 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072278 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | SHSP -Lance J testing Filter Drain sump High float alarm and RAS/WAS Drain Sump High Float alarm. | FLAG | stage2_low_confidence | 0.0084523 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0084523 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | SUSP, UV Common major alarms, contacted Cam B, he is on site working the UV alarms SHSP, Compressor 1 E Stop/Motor overload alarm, notified Lance J, he is on site, directed to disregard compressor alarms till we hear back from him or if it hits the end of the day | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; alarm [control_system]; alarms [control_system] | sso [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | SEOC67- Terry C on site to run generator. Not transferring over | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046109 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | KBSP - Reject Sump Pump #1 E-Stop Alarm. Disregard as per shift report | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | AUSS- P4 e stop ,moisture and leakage alarms came in. Called Dan K. who will investigate | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; leak [infrastructure]; leakage [infrastructure] | alarm [control_system]; alarms [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDSS + YTNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050431 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | KSSP- UV ch1 bank 1a lo UV intensity fault came in again. notified Neil O will take a look on site | FLAG | stage2_low_confidence | 0.0084739 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0084739 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | NBSP - Inlet level Hi alarm, mechanical bar screen failed to stop, Bar screen out of service alarm. All alarms cleared in a few minutes. Will monitor. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; out of service [equipment_failure]; alarm [control_system]; alarms [control_system] | failed [equipment_failure]; out of service [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: 0C and rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004415 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: 1C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | NBSP- Young J and Gluzen R on site to work on clarifier 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045162 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | BLSS - Generator running status still active. Checked Alectra Utility website. Outage map shows a power failure on top of BLSS location with an estimated time of restoration of 02:00 - 04:00 am. | FLAG | stage2_low_confidence | 0.013818 | ML: above threshold (no LLM available) — 0.014 | failure [equipment_failure] | 0.013818 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | MTSS- Terry R to test Wetwell hi level alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065643 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | HMSS- Power loss on site. Gavin W on site will take a look and investigate | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064034 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | Adam Button signing in 3C Foggy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041576 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | SUSP - Terry C on site to complete maintenance on blower 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004553 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | AUSSSR- Line 1 OOS due to valve fault. Notified Dan K. Directed to disregard. Maintenance is working to get it online but may be out for a couple days | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure] | fault [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | KBSP - Marcus R on site to complete an Alum tank fill. BLSS - Gavin W leaving site. Issue with security contacts on the door, unable to arm the system. Transferred to security. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071778 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | KSSP- Gen eye wash activation alarm came in. Notified Kevin K. Will confirm with contractors on site | FLAG | stage2_low_confidence | 0.0077314 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077314 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | yds + ynss normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049649 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | MTSP - Aeration tank 1 DO lo. Currently tank1 is the controlling tank with 2 blowers running. No mention of running a third blower on shift report. Followed up with Dan K. Okay to run third blower in man/on. Around 19:00 when tank 1 took a dive in reading to lo level. Will continue to monitor Consult | FLAG | stage2_low_confidence | 0.010431 | ML: above threshold (no LLM available) — 0.01 |  | 0.010431 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | BLSS- Dan H done on site all back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055194 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | MTSP - Terry R called to request opening sludge transfer valve to drain thickening tank. Man/open Sludge transfer Vlv and closed after tank reached 0.0m | FLAG | stage2_low_confidence | 0.0074759 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074759 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | SUSP- Satnam M on site to work on barscreen | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055509 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | PVSS- Pump 3 Fault Alarm, Odour Fan Umcommanded Stop. Alarms cleared. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | SUSP - UV System Major Fault alarm outstanding. Called Cam B. who will take a look | FLAG | stage2_low_confidence | 0.014817 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system] | 0.014817 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | YDSS+ YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048651 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | NBSP - Sludge thickener level hi, called and confirmed Lauren S still onsite wasting Consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061581 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | AUSS- Gen 1 engine warning, gen 1 engine coolant temperature low alarms - notified Barry M. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0069734 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | NBSSJA - Gavin W running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056669 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | JDSS - Terry C finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052463 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | SUSR - David D working on floats, disregard wet well Hi level alarms for the duration of the work. | FLAG | stage2_low_confidence | 0.0097529 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0097529 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -1C and flurries | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045056 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | BLSS - Multiple Emergency stop alarms came in. Daniel H. called to inform that he will be on site all night for a shutdown. Dan informed that all alarms can be disregarded 22:33 - Daniel called back and requested to call on call electrician. Called David D. who will give Daniel a call 01:40 - David D. called back and requested a CMU5. CMU5 Created W11654525 #CONSULT | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system]; alarms [control_system] | emergency [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | Carter D Signing In, -6D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041513 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | H5NBSP - Ian W restarting server. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042829 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -2C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal AUSSYS - Line trouble high wetwell on dialer. Site appears okay on trends and levels okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064381 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | RHAMF - Eric S reset fans onsite, leaving shortly | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060606 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | Connor Smith signing in -2 Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | KSSP - Alum Chem Room MUA -11 Differential Pressure Switch Hi alarm came in. Higher priority alarm. Called Chris C. who will take a look. | FLAG | stage2_low_confidence | 0.0076476 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076476 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | SHSP - Lance J on site to test the filter reject sump float alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068962 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | SEOC6 - Terry C finished and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044429 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | RHAMF - Unit 2 recirculation water flow lolo and pump pressure low alarm. Checked site, pump 2 has interlocked due to the lolo flow alarm. Attempted to reset alarms, alarms cleared and then returned. Shift report states that all alarms can be disregarded as long as one fan is running. Checked fans, both AMF fans are currently active. Disregard alarms. | FLAG | stage2_low_confidence | 0.020933 | ML: above threshold (no LLM available) — 0.021 | alarm [control_system]; alarms [control_system] | 0.020933 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | HLSSBS - Tyson C. doing pump 3 inspection | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044671 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | QVSSSC, Tyson C on site, running generator/testing temp alarms and testing flood/sump alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | YDSS + YYNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050431 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | RHAMF1, Fan 1/2 Faulted, Notified Jimmy from NAC, he will send his team over to the site | FLAG | stage2_low_confidence | 0.0098466 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; faulted [equipment_failure] | 0.0098466 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | SECC- Eric S on site for gas analyzer work. Will call when done 12:13- SECC-Eric S done on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003744 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | KCSSKR- Screen failed to stop alarm came in. Able to reset alarm | FLAG | stage2_low_confidence | 0.013571 | ML: above threshold (no LLM available) — 0.014 | failed [equipment_failure]; alarm [control_system] | 0.013571 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | NBSP - Ian W testing new alarm for UV system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066387 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | SUSP- UV bank 1a Major alarm common major alarms came in. Bank 1b running okay and flow stated up. Disregard on shift report cleared upon acknowledgment | FLAG | stage2_low_confidence | 0.008189 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.008189 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | BLSS, Young J is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052706 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | KBSP - Terry C working on generator, disregard alarms for the duration of the work. 11:03 Marcus R running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0056058 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | NBSP - Vortex #2 Water Scour Uncommanded Close alarm came in. Ack/reset as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061465 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | KBSP - Marcus R working on Head work blowers. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059591 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | NBSP- Alum P 3 uncommanded stop alarm came in. Left outstanding as alum P2 is running in its place. Emailed West waste water Ops | FLAG | stage2_low_confidence | 0.0073584 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073584 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038155 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | AUSS- Dan K notified ROC. P1/4 will be OOS for tonight and if P3 valve faults come in try to reset and if it doesn't it should be able to clear remotely a couple hours later. Placed P4 in man/off | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure] | fault [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | SUSP - Cameron B. is on site working on the UV's. Directed to disregard bank 2A alarms | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0065468 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | Carter D Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | AUSS- P3 MV4 interlocked on fault. Would not reset. Notified Dan K. Directed to leave outstanding for the day HLSSBS- Tyson C on site to run generator test flood alarms sump alarms and JHS inspections | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; fault [equipment_failure]; alarm [control_system]; alarms [control_system] | flood [critical]; fault [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | AUSS- Dan K req Tyler ZJ to give him a call regarding generator issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065325 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | QVSSSC- Dan from Wessuc Called and spoke with Kevin K that a operator will be dispatched within in an hour if needed SHSP- Power fail on site blowers clarifier faults as well as generator running. Notified Lance j on site and will reset outstanding alarms SHSSDK-P1 failed to start and vfd fault alarms came in P2 uncommanded stop during power outage. Reset alarms P2 running in auto Notified Lance J of outage and will attend site when done at SHSP | FLAG | stage2_low_confidence | 0.038797 | ML: above threshold (no LLM available) — 0.039 | fault [equipment_failure]; failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.038797 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | NBSP - UV system minor fault, disregard as per shift report | FLAG | stage2_low_confidence | 0.010017 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.010017 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather -12C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043332 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | BLSS - Site hydro fail alarm and low flow alarms. Checked site, generator is running and pump duty has resumed. Pumps cycled through duty as they struggled with discharge valve faults. Waiting for the wet well level to drop to normal levels before clearing pump alarms. HMSS - PAC Control panel power failure alarm and wetwell level alarms. Checked site, generator is running and ATS is pointing to the generator indicating a true power outage. Operations appear normal with pump 2 in duty 1 pushing flow. Overflow to Toronto maintenance hole 1 alarm triggered but there is no indication of higher than normal wet well levels. Cleared all alarms except generator running. 20:31 - BLSS/HMSS - Alectra power outage map shows a large power outage in the area of BLSS and HMSS. Will monitor situation. 21:39 - BLSS - Utility power has been restored and generators have shut down. On power transfer the duty 1 pump (pump 3) faulted, and duty rotated to pump 2 which is operating normally. Will let pump 2 run for a few minutes before resetting alarms as the duty will rotate back to pump 3. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; fault [equipment_failure]; faulted [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; fault [equipment_failure]; faulted [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal NBSP - Vortex 1 air scour uncommanded close alarm. Cleared alarm as per the shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043788 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | NBSP- Sludge Thickener Level HiHi Alarm. Can disregard as per Lauren S CONSULT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053001 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | Adam Button signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052504 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | Carter D Signing In, -3D/Snowing YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030718 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | RHAMF1- Station Power Failure. AMF Fan 1, Fan 2 VFD Fault Alarms, Odour Control System Offline. Notified Jimmy from NAC. He will send someone in the morning to reset. | FLAG | stage2_low_confidence | 0.016125 | ML: above threshold (no LLM available) — 0.016 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.016125 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | Ethan U signing in Weather -1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | LSSS, LSSS2 to LSSS4 Comm Fail, notified Yash S, he will look into it | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | LSSS- Phil R on site to test sump pit flood and auto dialer NMSSBP- Terry R on site for site inspections may be rotating duty | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | LSSS - Emily B from EME on site for sampling and requested that pump 6 be placed in duty 1. Made necessary change. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058644 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | NMSSBP - Mech screen 1 fault alarm. Checked site, channel 1 inlet gate is manual/closed. No flow to the faulted barscreen. | FLAG | stage2_low_confidence | 0.013549 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] | 0.013549 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | MTSP - Man/stop blower 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041058 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | RHAMF - Unit 2 reciculation pump presure lolo, water flow lolo. Disregard alarm as per shift report as fans running | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068801 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | KSSP - Sludge holding Blwr 1 hi dif press alarm, alum, chem Rm MUA-11 Dif press Sw hi alarm. Both sludge blowers are off. Informed Darren B, disregard for the night Consult | FLAG | stage2_low_confidence | 0.0075869 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075869 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | LSSS4- PAC comm fail. Cleared upon acknowledgement. Trends okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | LSSS - Artour L. is on site for asset tagging | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005566 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | KSSP- Tyson C on site to work on membrane and to disregard membranes not inauto and low water alarms on site | FLAG | stage2_low_confidence | 0.0092001 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0092001 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | BLSS, Young J on site with contractor, directed to disregard alarms all night as he will be there watching over the station, pumps will be in local | FLAG | stage2_low_confidence | 0.011452 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011452 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | RHAMF - AMF Fan 1 & 2 VFD fault. Informed Eric S as primary oncall Jimmy H unavailable. Will look into issue in the morning | FLAG | stage2_low_confidence | 0.010388 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.010388 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -15C and sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044737 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | NBSP - Vortex #1 Air Scour Uncommanded close alarm came in. Ack/reset as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061052 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | SHSP- Compressor 1 e stop switch hihi and overload alarms came in. Notified Lance J. Contractors on siter working on compressor and compressor 2 is D1. Directed to disregard until work is completed | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; alarm [control_system]; alarms [control_system] | sso [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | NMVCBP - Parth P on site to complete a flowmeter calibration. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060383 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | NMSSBP - Barry M. called to inform that he is on site looking into the high wet well levels | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069324 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | ABMC - Kyle B on site for UPS maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055179 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | AUSS- P3 disc hdr MV4 fault alarm came in. Wasn't able to clear Placed P3 in man/off emailed Central-east wastewater | FLAG | stage2_low_confidence | 0.01302 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.01302 | 0 | 0
2026-02 | 2026-02-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | JDSS- Terry C on site to replaced batteries on generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005871 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather -9C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | QVSSSC - Tyson C on site for pumps testing. Will run pumps in manual mode, disregard High wet well level alarms. | FLAG | stage2_low_confidence | 0.0097601 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0097601 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | AUEQSJ - Rick L on site for annual calibration. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005641 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | NMSSHS- Barry M on site to test dialer, hi lo temp and drywaell flood alarms KSSSQW- Darren B o n site to run generator and perform JHS inspections | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038155 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | RHAMF1- Jimmy from NAC on site resetting alarms. Notified Jimmy of outstanding VFD alarms and generator running status | FLAG | stage2_low_confidence | 0.007369 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.007369 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | KSSP - UV Channel 1 1 A bank low intensity fault alarm. Checked site, UV channel 1 bank 1A is currently active. Dosage and power levels are good and trending shows intensity is stable but slightly dipping below low alarm setpoint. Shift transfer states that minor fault alarms are a disregard. The major fault box status is normal indicating this is a minor fault alarm. Alarm cleared on acknowledgement and triggered again. Monitoring site. | FLAG | stage2_low_confidence | 0.058064 | ML: above threshold (no LLM available) — 0.058 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.058064 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | BLSS - Scrubber blower 1 uncommanded stop alarm, drywell SF3 uncommanded stop alarm, pump room EF4 uncommanded stop alarm, pump 3 uncommanded stop alarm, screen 1 uncommanded stop alarm and pump 5 fault alarm. Checked site, operations appear normal, pump 4 is operating in duty 1 and pushing flow. Fans and ventilation systems seem to have faulted, possibly due to a power blip. Able to clear all alarms except the pump5 fault but pump 5 is currently local off and OOS. Ventillation and screen systems back online. HMSS - PAC control panel power fail alarm and pump 4 uncommanded stop alarm. Checked site, pump 5 is operating in duty 1 and pushing flow. Possible power blip, able to reset alarms. GRSSWA - wet well 1 ultrasonic lolo level alarm. Checked site, operations appear normal. Reset alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -4C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | NMSSBP - Mechanical Screen 2 Overtorque Alarm came in. Will send an email to Daniel K. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060675 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | SEOC4 Eric S finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039415 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | NMSSBP, Mech Screen 2 Emergency stop, notified Barry M, he will look into it | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in,weather +2C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | KSSP - UC Ch, 1 bank 1A low UV intensity fault, alarm cleared to normal status. UB panel 1 lamp low intensity, reading appears okay for intensity and UV running okay | FLAG | stage2_low_confidence | 0.01381 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system] | 0.01381 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | NMSSBP- Mech Screen 1 Overtorque Alarm. Called Chris R. Requested to place Screen 2 Gate 1 man/closed and will leave outstanding for the weekend. Requested a call if any issues with screen 1. CONSULT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071234 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -4C and snow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045642 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | SUSP- Satnam M done on site. Notified Satnam M barscreen and vortex/ dewatering screws are not in auto. Will place back in auto 11:56- Satnam M confirmed with Ops headworks is normally in local but runs in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062424 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | MTSP - Aeriation tank 2 DO lolo, man/start blower 2 13:28 - Place blower 2 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038711 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | SEOC 4 - Shaft 4 air DMP2 uncommanded close alarm and shaft 4 FAN2 uncommanded stop alarm. The DMP2 uncommanded close alarm is a disregard on the shift report. Fan 2 is faulted but duty rotated to fan 1 which is operating. Able to clear both alarms. | FLAG | stage2_low_confidence | 0.024568 | ML: above threshold (no LLM available) — 0.025 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.024568 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | SUSP- Sludge tanke level hihi alarm came in. Notified Darren B directed to disregard alarm #consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067795 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | MTSP- Aeration tank 2 DO lo alarm came in. Will continue to monitor and placed blower in manual if DO lolo comes in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069684 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | SUSP - UV Ch1 critical failure, high level. Alarm due to fault upon plant start up due to a high channel level. Alarm will clear once UV gates open. Disregard as per shift report. Alarms cleared when acknowledged | FLAG | stage2_low_confidence | 0.020491 | ML: above threshold (no LLM available) — 0.02 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.020491 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | SUSP- UV system Critical failure/ ch1 high level/Critical alarm/ UV2 high level and common critical alarms came in. Cleared upon acknowledgment and came in as UV ch1 opened up disregard on shift report | FLAG | stage2_low_confidence | 0.019271 | ML: above threshold (no LLM available) — 0.019 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019271 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: 1C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | Adeela Khan signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052739 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003864 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | KBSP - Marcus R working on filters and DO sensors. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060958 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | SUSSWB - Ventilation H2S OOR Alarms. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.010005 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system]; h2s [safety] | 0.010005 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | HLSSBS - Hydrogen Sulphide Sample 1 Fault alarm came in. Critical alarm. Shift report directs to disregard alarm. | FLAG | stage2_low_confidence | 0.012724 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.012724 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | KSSP - RSHW Grit room H2S OOR/Fault alarm, disregard as per shift report | FLAG | stage2_low_confidence | 0.016856 | ML: above threshold (no LLM available) — 0.017 | fault [equipment_failure]; alarm [control_system]; h2s [safety] | 0.016856 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | QVSSSC - Ricardo L. is on site for annual calibrations. May need to enter a confined space but will inform the ROC. | FLAG | stage2_low_confidence | 0.0077512 | ML: above threshold (no LLM available) — 0.008 |  | 0.0077512 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | KSSP - Phil from AB Project Management and Construction is on site and will be working in the generator room. Phil informed he will call back if he will be running the generator 09:01 - Chase J. called to inform that he will be running the generator in test mode 15:58 - Phil is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055024 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | KSSP - Collection blower 2 high diff pressure alarm. Checked site, duty rotated to blower 1 which activated. Unable to clear alarm, shift report states it is a disregard. | FLAG | stage2_low_confidence | 0.0089053 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0089053 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | RHAMF1- Eric from NAC on site. He cleared alarms on site, Ack/reset alarms, Recirculation Pump 1 restarted. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0069171 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | AUSS - Generator 1,2,3 not in auto alarms, cleared right away. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0060089 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | QVSSSC- Rick L and Parth P on site for annual calibrations AUSS- Phil R on site working on P4, wet well high level test, surge tanks and inlet gates | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057246 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | 10030 Bayview Ave Richmond Hill Storm Sewer- Called Roads spoke with Karen to notify them that storm sewers are operated by the roads department not water or waste water Ops. | FLAG | stage2_low_confidence | 0.008024 | ML: above threshold (no LLM available) — 0.008 |  | 0.008024 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | KSSP. Neut Process (MC) Took Too Long alarm, critical alarm, notified Darren B, he is looking into it 19:38, Darren B is heading to site CMU: W11658868 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0033873 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | Ethan U signing in Weather -4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | HLSSBS- Tyson C done on site heading to QVSSSC | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056133 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | Adam Button signing in in -3C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042347 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | Adam Button signing in -6C Snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042225 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | 10030 Bayview Avenue, Richmond Hill - City of Richmond Hill Operator (Eve 416 460 2683) called Roads Operator Karen to inform of a broken lead on a Storm Sewer main. Karen called the ROC and informed this is a W/WW issue. 05:20 - Called Marcus R. who informed this is a c-east WW. 05:25 - Called Daniel K. who requested an email and will attend site. After checking all pipes, Daniel noticed that this is not anything related to central east WW and would be under roads jurisdiction. 06:00 - Passed all information onto Adam B. #CONSULT | FLAG | stage2_low_confidence | 0.0086618 | ML: above threshold (no LLM available) — 0.009 |  | 0.0086618 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | QVSSSC - PAC Commfail alarm. Trends missing since 10:51, notified Ian W, he will check SCADA. 11:15 Ian W will call Kevin K. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system] | scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | AUSSSR - Aysix System Heartbeat alarm came in. Cleared alarm and site is back to normal operations | FLAG | stage2_low_confidence | 0.0080095 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080095 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | KBSP - Reject sump pmp 1 E. stop. Disregard as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048984 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | KBSP - Lauren S working on headworks, disregard alarms for the duration of the work. | FLAG | stage2_low_confidence | 0.0091301 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0091301 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | KSSP- UV panel lamp lo intensity and intensity fault alarms came in. Have been reoccurring all day. Notified Darren B. Directed to disregard for night as long as dosage is okay #consult | FLAG | stage2_low_confidence | 0.019191 | ML: above threshold (no LLM available) — 0.019 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019191 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | KSSP- Neil O cleared alarms on site and is leaving. Contractors are done for the dya | FLAG | stage2_low_confidence | 0.0082335 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0082335 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | QVSSSC - Kevin K called, he placed pumps man/off for pump testing and monitoring remotely, disregard wet well level alarm. Tyson C will attend site. | FLAG | stage2_low_confidence | 0.010581 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010581 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | QVSSSC- Kevin K req vac truck services to pump down wetwell. Called Wessuc (1-866-493-7782) as per procedure. Spoke with Mark who will follow up with Ops and notify ROC in 10 mins for truck dispatch. | FLAG | stage2_low_confidence | 0.0075472 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075472 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | SEOC 67- Phil R onsite running generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043925 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | SHSP- Garrick from Ferguson Electric is on site fore generator work. Not transferring over | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068386 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, -2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | RHAMF1- Power back to normal, generator stopped, Jimmy from NAC reset all alarms and leaving site. | FLAG | stage2_low_confidence | 0.0073005 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0073005 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | YDOC- Fan 1 Fault Alarm outstanding from this morning. Notified Phil R. | FLAG | stage2_low_confidence | 0.010357 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; alarm [control_system] | 0.010357 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | KBSP - Marcus R. working on DO probes and rectangular clarifiers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064916 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | QVSSSC- Tyson C called. He will be running pumps in manual and local. Disregard related alarms. | FLAG | stage2_low_confidence | 0.0095644 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0095644 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | KSSSP- Neil O working on membrane turbidimeters. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060113 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | NBSP- UV system minor fault alarm. UV 1b running okay disregard on shift report | FLAG | stage2_low_confidence | 0.011037 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; alarm [control_system] | 0.011037 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | LSSS- Brent St C on site with Wajax. They will be performing maintenance on generators on site and will be running them during this time. Later in the day Chris R will be on site for power transfer. KBSP- Lauren S on site to work on all blowers including sludge/aeration and diversion tank blowers | FLAG | stage2_low_confidence | 0.015068 | ML: above threshold (no LLM available) — 0.015 |  | 0.015068 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | QVSSSC- Eric S on site to work on LIT 2 NBSP- Young J on site to work on sani sump hi level and reject sumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048202 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | KSSP- Tyson C onsite testing headworks gas detectors. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061749 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | RHAMF - UNIT Recirculation Water flow LoLo and pump pressure low alarm. Same alarms that triggered for recirculation pump 2. Both AMF fans still running. Disregard as per the shift report. | FLAG | stage2_low_confidence | 0.0096728 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0096728 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | AUSS- David D and Satnam M on site to work on P4 10:09-KBSP- Marcus R and Lauren are on site. Lauren S working on RAS/WAS system and contractors will be working on HVAC system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054484 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | MTSP - Final Effluent Flow LoLo alarm came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0076256 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076256 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | QVSSSC- Power loss on site Force main 1 2 valve fault and wet well 1/2 hydrostatic lolo/OOR alarms came in. Notified Tyson C will be on site later today but to call if site doesnt run in duty KBSP- Lauren S on site to test hi sump level for head works. and tertiary building | FLAG | stage2_low_confidence | 0.021304 | ML: above threshold (no LLM available) — 0.021 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.021304 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | YDOC - Eric S. working on biofilter drain pH | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059324 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 0c | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | Carter D Signing In | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | MTSS - Terry R testing wet well hi and sump pit alarms. | FLAG | stage2_low_confidence | 0.0080291 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0080291 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | QVSSSC- Eric S finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055575 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | AUEQSJ - Rick L finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052609 | 0 | 0
2026-02 | 2026-02-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | SEOC4 - Eric S on site replacing O2 sensor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042261 | 0 | 0
2026-02 | 2026-02-11 | All Wastewater System ROC General | ROC | KSSP, Lo UV Intensity fault, notified Darren B as he is on site and its not in the shift report, directed to disregard consult | FLAG | stage2_low_confidence | 0.0086999 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure] | 0.0086999 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | SUSP- UV CH 1 Common Critical Alarm. UV Ch. 1 High Level Alarm. UV System Critical Failure Alarm. Alarms cleared upon acknowledging. Known issue on SCADA Report | FLAG | stage2_low_confidence | 0.01605 | ML: above threshold (no LLM available) — 0.016 | failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.01605 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | KSSP- UV ch1 common major/ Major/ Module Comm fail and UV panel major fault alarms came in. Bank 2 running currently. Notified Neil O of alarms and will take a look on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | SUSP - Outstanding UV System Major Fault alarm. Called Darren B. who directed to disregard alarm. #CONSULT | FLAG | stage2_low_confidence | 0.011323 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; alarm [control_system] | 0.011323 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | AUSS - Pump 5 dicharge MV@ failed to open alarm. Checked site. Duty 1 rotated to pump 4 which is pushing flow. Cleared alarms. | FLAG | stage2_low_confidence | 0.013857 | ML: above threshold (no LLM available) — 0.014 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.013857 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | KBSP - Reject sump pump 1 Estop alarm. Checked site . Reject pump 2 is running. Disregard alarm as per SCADA review. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system] | scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047212 | 0 | 0
2026-02 | 2026-02-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | KSSP- UV panel lamp lo intensity and intensity fault alarms, UV1 running, intensity normal. Disregard alarm as per Darren B. | FLAG | stage2_low_confidence | 0.013475 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.013475 | 0 | 0
2026-02 | 2026-02-13 | All Wastewater System ROC General | ROC | NMSSBP - Mech screen 1 overtorque alarm. Checked site, mechanical screen 1 has interlocked and is local/off. Called Dan K who directed to close the screen 1 inlet gate 1. Made the necessary change. Daniel K will inspect the screen on Sunday. #consult | FLAG | stage2_low_confidence | 0.0090298 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0090298 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | NBSP- Harie R on site working on air compressors | FLAG | stage2_low_confidence | 0.009037 | ML: above threshold (no LLM available) — 0.009 | sso [critical] | 0.009037 | 0 | 0
2026-02 | 2026-02-22 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | Adam Button signing in -5C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004176 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-16 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | Connor Smith signing in -1 Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | KSSP- Citric Acid Tank Lvl HiHi. Tank showing in normal range. Cleared alarm YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053611 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | KSSP - Scum chamber 1 high level. Disregard as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048763 | 0 | 0
2026-02 | 2026-02-18 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather -2C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | SEOC6 - Phil R. called to inform that he is on site and will be testing the generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051002 | 0 | 0
2026-02 | 2026-02-20 | All Wastewater System ROC General | ROC | AUSSYS- All pumps in man/off and wetwell 1/2 no discharge path alarms came in. Notified Kevin S. On site with pumps off to actuate valves | FLAG | stage2_low_confidence | 0.0077666 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0077666 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | MTW3 - Patrick F found a verry small leak after attending site. Leaving scrubber local/on over night | FLAG | stage2_low_confidence | 0.0091849 | ML: above threshold (no LLM available) — 0.009 | leak [infrastructure] | 0.0091849 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | RHAMF - Station power failure, AMF fan 1 & 2 VFD fault. Called Jimmy H (NAC contact) unable to get a hold. Called Eric S, will follow up with Jimmy later and follow back up if he will attend site today 9:40 - Eric onsite reset fans | FLAG | stage2_low_confidence | 0.012093 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; failure [equipment_failure] | 0.012093 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-14 | All Wastewater System ROC General | ROC | KSSP - UV panel 1 lamp low intensity. UV still running with intensity. Email sent to North WW regarding alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067669 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | BLSS - Pump 3 uncmd stop, scrubber blo 2 uncmd stop/start, drywell SF3 uncd stop, disch vlv failed to open. Able to clear alarms | FLAG | stage2_low_confidence | 0.016152 | ML: above threshold (no LLM available) — 0.016 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.016152 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | NMSSHS - High well well on dialer. Site appears fine no duty active with levels within range PVSS - Pump failure on dialer, site appears in good standing, no issues with pumps, duty 1 off | FLAG | stage2_low_confidence | 0.021739 | ML: above threshold (no LLM available) — 0.022 | failure [equipment_failure]; pump failure [infrastructure] | 0.021739 | 0 | 0
2026-02 | 2026-02-12 | All Wastewater System ROC General | ROC | SEOC 4 - Shaft 4 O2 Monitor alarm, disregard as per shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054668 | 0 | 0
2026-02 | 2026-02-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-17 | All Wastewater System ROC General | ROC | KBSP- Lauren S performing oil change on clarifier 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046607 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | AUSSSR- Line1 valve overtorque/ failed to close. Created CMU5 W11639400 and emailed Dan K as per shift report. #CMU5 | FLAG | stage2_low_confidence | 0.010018 | ML: above threshold (no LLM available) — 0.01 | failed [equipment_failure] | 0.010018 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | RHAMF1 - Power failure, generator running, odour control system offline alarms, Recirculation pumps interlocked on pressure low/low alarm. Power restored, alarms outstanding. Notified Phil R. He will check SCADA and contact NAC. 08:30 Fan 1 VFD fault alarm outstanding. Notified Jimmy H from NAC, he will attend site. | FLAG | stage2_low_confidence | 0.022417 | ML: above threshold (no LLM available) — 0.022 | fault [equipment_failure]; failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.022417 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | KSSP - Eric S replacing O2 sensor. 10:10 Eric S completed work, leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036673 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | KSSP - Chase J requested disregard UV Panel Major fault alarm, UV 2 running normal. And disregard collection Blower 2 High Diff Pressure alarm. # Consult | FLAG | stage2_low_confidence | 0.015476 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system] | 0.015476 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | KSSP - Mem Operating Area MUA - 10 Temp Switch Lo alarm came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063101 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | Adeela Khan Signing in. Weather: -18C and clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044683 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | KSSP - Makeup Air Unit 6 Temp Switch Lo alarm came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006025 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | NBSP- Gavin W onsite for generator test. Also will be doing Health and Safety work orders. | FLAG | stage2_low_confidence | 0.01228 | ML: above threshold (no LLM available) — 0.012 | work order [maintenance_action] | 0.01228 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | RHAMF1 - Jimmy H from NAC called, he is on site, reset VFD fault alarm. As per Daniel K cleared alarm and restarted Fan 1. | FLAG | stage2_low_confidence | 0.01279 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.01279 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | KSSP - Membrane Air Blower 1 failed to start, called Chris C, no response, will call again. Chris C on site. 12:50 Chris C will check. | FLAG | stage2_low_confidence | 0.0082622 | ML: above threshold (no LLM available) — 0.008 | failed [equipment_failure] | 0.0082622 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | KCSSKR - Young J on site to test the wet well level hi alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067276 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | PVSS - Eric S working on H2S sensor. 13:15 Eric S finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | h2s [safety] | 0.005009 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | KSSP- Mike B onsite working on chemical containment flood alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system]; containment [safety] | flood [critical]; alarm [control_system]; alarms [control_system]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | KSSP - Chase J on site to test the eyewash stations. Will trigger JHSC alarms. | FLAG | stage2_low_confidence | 0.0083392 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0083392 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | SHSP- David D onsite working on Effluent Pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059475 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | RHAMF - Multiple power related alarms came in. Checked site. Both fans are no longer running. AMF Fan 1, 2 VFD Fault and Odour Control System Offline alarms are outstanding. Generator is not running and site is still connected to hydro power.Called Jimmy H (416 826 0586) from NAC, as per interim, who will send his operators to site. Jimmy did not mention if he will call a Central East Operator to site yet. | FLAG | stage2_low_confidence | 0.042473 | ML: above threshold (no LLM available) — 0.042 | fault [equipment_failure]; not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.042473 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | NMSSJA- Harie R onsite testing drywell flood, hi/low temp, and autodialer. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | SHSP - Lance J cleaning effluent tank. UV system off for the duration of work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069856 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather -15C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043332 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | NBSP - Process Building Temp Hi/Low alarm came in. Will send an email to the west ww team | FLAG | stage2_low_confidence | 0.008095 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.008095 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | BLSS - Screen Differential Level Hi alarm came in. Disregarded as per shift report due to a foamy influent. Will call if hi wet well comes in | FLAG | stage2_low_confidence | 0.010277 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010277 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather -12C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043332 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | NMSSBP - Daniel K. attended site to take a look at a gas monitor and noticed the front gate is stuck open. Spoke to Corporate security and they will dispatch mobile security to close the gate | FLAG | stage2_low_confidence | 0.011778 | ML: above threshold (no LLM available) — 0.012 |  | 0.011778 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | KSSP - MUA2 Low Temp alarm came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054969 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | MTSP - Final Effluent LoLo alarm came in. Disregarded as per shift report YDSS + YNSS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0042624 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | NMSSBP - Mech screen 2 overtorque alarm. Checked site, barscreen 2 is interlocked and local off. Barscreen 1 is duty 1 and operating. Called Daniel K who will attend site later today. Created CMU5#W11645852 #consult #CMU5 | FLAG | stage2_low_confidence | 0.0082822 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0082822 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | MTSP - Aeration tank 2 DO lolo alarm. Checked site, two blowers are active. Trending shows that the DO reading is recovering. Reset alarm | FLAG | stage2_low_confidence | 0.0076864 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076864 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | NBSP - Sludge thickener level hihi alarm. Checked site, trending shows the sludge thickener level increased rapidly to above the hihi alarm setpoint. No mention of this alarm on the disregard list. Contacted Marcus R who directed to place the WAS pumps into manual/off mode and disregard the alarm until Monday at 09:00. #consult | FLAG | stage2_low_confidence | 0.010472 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010472 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | RHAMF- Ji Xiao from NAC onsite requested to reset alarms. Fans started back up | FLAG | stage2_low_confidence | 0.0088516 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0088516 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | MTSP - Final Effluent Free Chlorine LoLo alarm came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0079149 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079149 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | SUSP - Sludge Tank Level HiHi alarm came in. Checked site. Noticed that level had gone back below the hihi level and alarm cleared | FLAG | stage2_low_confidence | 0.0097527 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0097527 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | MTSS - Talha H completing an OIT reboot and directed to disregard the historian heartbeat alarm. | FLAG | stage2_low_confidence | 0.008305 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.008305 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | Connor Smith signing in -8C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041939 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | KBSP - Marcus R leaving site. Odour system recirc pump low flow is a disregard for the night. | FLAG | stage2_low_confidence | 0.0074359 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074359 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | Carter D Signing In, -24D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041696 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | SECC - Sump 1 level low switch alarm. Checked site, sump pump 1 is interlocked on the alarm. Trending shows a dip of the sump level which recovered quickly. Cleared alarm. | FLAG | stage2_low_confidence | 0.0086521 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086521 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | BLSS - Daniel H on site to complete scheduled work. Dan will be manually operating the site and has directed to disregard all alarms from site. | FLAG | stage2_low_confidence | 0.011262 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011262 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | BLSS - Eric S on site, replacing O2 sensor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042254 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | AUSSMP - Bar Screen 1 General and Not in Auto alarms came in. Checked site. Bar screen 1 turned local and bar screen 2 is OOS. Called Daniel K. who is headed to site. CMU5 Created W11645773 22:42 - Daniel K. called back to inform he will need Lee F. to attend site. Called Lee F. who will speak to Daniel K 22:59 - Lee F. is headed to site. CMU5 Created W11645784 04:00 - Daniel K. called back to inform that he and Lee F. are finished on site. They were unable to get Bar Screen 1 back online but have now put Bar Screen 2 back online. Daniel informed that he had to close channel 1 inlet gate #CONSULT #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | NBSSJA- Eric S finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055568 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | LSSS - assigned P6 to Duty 1 for Ubah F ( IAM student), for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050807 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | RHAMF1 - Jimmy from NAC called, he reset recirculation pump 2 VFD. Cleared alarm, Recirculation pump 2 restarted. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065912 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | RHAMF - Station power failure alarm. Power blip affected several Richmond Hill facilities. Various additional alarms triggered which interlocked the pumps. Able to clear most alarms. Outstanding alarms include AMF fan 1 and 2 VFD faults and odor control system offline. Attempted to contact Jimmy Huiman but the call would not connect to the given number. Called Eric Sang who stated they will contact Jimmy. | FLAG | stage2_low_confidence | 0.050191 | ML: above threshold (no LLM available) — 0.05 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.050191 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | KSSP- Uv Ch2 2a adjacent lamp fail. Disregard on shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048538 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | KSSP- alum chem room MUA dif press sw hi alarm came in. Emailed north wastewater about outstanding alarm | FLAG | stage2_low_confidence | 0.0086601 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086601 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | YDSS+YNSS normal KSSSQW- P3 vibration OOR alarm came in. Disregard on shift report | FLAG | stage2_low_confidence | 0.008657 | ML: above threshold (no LLM available) — 0.009 | vibration [equipment_failure]; alarm [control_system] | 0.008657 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | NBSSJA- Diesel tank level hihi alarm came in. Disregard on shift report | FLAG | stage2_low_confidence | 0.0073746 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073746 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | LSSS - Pump 4 Disch valve overtorque alarm. Pump in local mode, Daniel K on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0056074 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | JDSS- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. 15:40- Work Completed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0040541 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -22C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046216 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | SHSP- Filter Room Smoke Detector. Notified Lance J. Can disregard. | FLAG | stage2_low_confidence | 0.011666 | ML: above threshold (no LLM available) — 0.012 | smoke [equipment_failure] | 0.011666 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDOC - Phil R. running generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055872 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | QVSSSC - Inlet channel high switch alarm. Disregard as per the shift report. | FLAG | stage2_low_confidence | 0.0075771 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075771 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | SUSSWB- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069708 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | KSSP - Chris C called, work on generators completed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061568 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | SHSP - Filter Room smoke detector alarm. Notified Marcus R , he will check SCADA and attend site. # CMU5 W11643074 | FLAG | stage2_low_confidence | 0.013394 | ML: above threshold (no LLM available) — 0.013 | smoke [equipment_failure]; scada [control_system]; alarm [control_system] | 0.013394 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038978 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | NBSP - Process Bld UPS Fault alarm, notified Ian W. He will check SCADA. # CMU5 W11643060 17:50 Ian W checked SCADA, requested disregard alarm until tomorrow. | FLAG | stage2_low_confidence | 0.011367 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.011367 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | KSSP- UV Major Alarms. Called Chris C. He will look into it. | FLAG | stage2_low_confidence | 0.0081804 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0081804 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | LSSS- Wet well screen diff level LOE came in trends okay. Reset alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070868 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | SHSP - Filter Room Smoke Detector alarm. Marcus R. called back to inform that he is finished on site and has cleaned the smoke detector. Marcus informed this alarm can be disregarded for the night. | FLAG | stage2_low_confidence | 0.023592 | ML: above threshold (no LLM available) — 0.024 | smoke [equipment_failure]; alarm [control_system] | 0.023592 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | SEOC - OCF Fan Room 1 GO2 Low alarm came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057729 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | KSSP - Channel Aeration Blower 2 High Differential Pressure alarm came in. Checked site. Noticed duty had rotated so that blower 1 is in duty 1. Will send an email to OIC | FLAG | stage2_low_confidence | 0.0089861 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0089861 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS - Master Control Panel Failure alarm came in. Checked site. After 5 mins, alarms cleared and site is back to normal operations. Site was still connected to hydro power and generator did not run 20:11 - Alarm came back in along with control Panel Power Failure at YDOC3 and YDOC6. Called Ian W. who will take a look. CMU5 Created W11645765 20:56 - Ian W. called back to inform that everything looks okay and that these alarms may have been triggered due to high winds #CONSULT #CMU5 | FLAG | stage2_low_confidence | 0.021585 | ML: above threshold (no LLM available) — 0.022 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.021585 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | AUSS - Bill VB working on bar screens/ conveyors. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061081 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038155 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | KSSP - Recirculation pump no flow alarm. Checked site, recirculation p[ujmp showing in local off. Chase J is signed into site in the log book. While monitoring noticed the pump start in local indicating that Chase J is aware and making changes. | FLAG | stage2_low_confidence | 0.016015 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system] | 0.016015 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | NMSSHS - Meter chamber 2 flood alarm. Checked site, operations are normal. Shift report directs to disregard. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | RHAMF- Contractor Ji Xiao onsite requested to clear alarms. Fans started back up. He will remain onsite for 20 minutes. | FLAG | stage2_low_confidence | 0.0081002 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0081002 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | KSSSQW - Pump 3 Vibration OOR alarm came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.010845 | ML: above threshold (no LLM available) — 0.011 | vibration [equipment_failure]; alarm [control_system] | 0.010845 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | PVSS- Ultrasonic mode alarm. Pumps 2, 3 in manual and pump 1 interlocked. Notified Young J. Requested to place pumps into auto and clear alarm. | FLAG | stage2_low_confidence | 0.0076803 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076803 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | NBSP - David D. working on generator, oil changes. Station to stay in utility power. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071069 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | BLSS - Dan H leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054317 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | SUSP - UV system low dosage, critical failure, lolo transmittance and major fault alarm. Checked site, noted UV system dosage reading was very high and UV intensity was very high. Contacted Chase J. While speaking with Chase noted that the UV weir gate was not open for the active channel, but was open for the inactive channel. Chase J directed to swap the UV bank duty to channel 1. Made necessary changes. Chase J will check SCADA to determine if a site visit or further changes are needed. #consult | FLAG | stage2_low_confidence | 0.054073 | ML: above threshold (no LLM available) — 0.054 | fault [equipment_failure]; failure [equipment_failure]; scada [control_system]; alarm [control_system] | 0.054073 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | Adam Button signing in -8C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004176 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | SHSP - WAS Pump 2 Uncommanded Stop alarm came in. Pump was not running. Alarm was able to be cleared | FLAG | stage2_low_confidence | 0.012299 | ML: above threshold (no LLM available) — 0.012 | not running [equipment_failure]; alarm [control_system] | 0.012299 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | KCSS - Satnam M on site for pumps maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056112 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | KBSP - Odor system recirculation pump low H2O flow alarm. Called Marcus R who will check SCADA. 19:52 - KBSP - Marcus R attending site to determine if the piping system or pump couplings have failed. Created CMU5#W11650161 #consult #CMU5 | FLAG | stage2_low_confidence | 0.0097464 | ML: above threshold (no LLM available) — 0.01 | failed [equipment_failure]; scada [control_system]; alarm [control_system] | 0.0097464 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | KCSS - Lauren S testing Drywell flood alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | Carter D Signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052084 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | MTSP - Final Effluent Flow LoLo alarm came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0076256 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076256 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | KSSP - Membrane Control Room RTU - 3 Temp Switch Low alarm came in. Checked site. Will monitor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0062404 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | NBSP - Vortex #2 Air lift uncommanded close alarm came in. Ack/reset as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060752 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | KSSP - Alum Chem Rm MUA - 11 Differential pressure Switch hi alarm came in. Checked site. Fan is running. Will send an email to North WW | FLAG | stage2_low_confidence | 0.0076547 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076547 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | KSSP - Membrane air blower 1 failed to start. Checked site, blower 2 has rotated into duty 1 and is operating as expected. Alarm cleared on reset. | FLAG | stage2_low_confidence | 0.015186 | ML: above threshold (no LLM available) — 0.015 | failed [equipment_failure]; alarm [control_system] | 0.015186 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | BLSS - Young J and Lauren S testing High wet well level, dry well flood and temp alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | SUSP - UC common critical alarm, high level alarm and critical failure alarm. Checked site, UV channel flow recently started. Shift report states this scenario is a disregard. Alarm status changed to normal while checking site and the alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.034407 | ML: above threshold (no LLM available) — 0.034 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.034407 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -4C and snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044927 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | NMSSBP - Daniel K off site. Barscreen 2 is OOS. All flow going through barscreen 1. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 Bank 2 A low UV intensity fault. Checked site, one UV bank is running. Shift report directs to disregard all UV minor alarms. This alarm is classified as a minor alarm, as the major alarm status is normal. | FLAG | stage2_low_confidence | 0.021933 | ML: above threshold (no LLM available) — 0.022 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.021933 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | EGSSSC - Tyson C completed generator run test. Leaving site. BLSS - Eric S finished on site. PVSS - Lauren S running generator, testing temperature and drywell flood alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | SHSP - Lance J running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056138 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | EGSSSC- Tyson C onsite for work orders. Running generator, health and safety, drywell flood, sump pump and auto dialer test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action] | flood [critical]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | SEOC4 - Phil R. running generator YDOC - informed Phil R. outstanding BFILT 2 outlet temp lo from earlier gen run, okay to disregard | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046762 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | SEOC- Phil R onsite running diesel generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059183 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | KSSP - Chris C running generator test, contractors on site for semi-annual gen inspection. Chris C will call when site back to normal power. | FLAG | stage2_low_confidence | 0.0086181 | ML: above threshold (no LLM available) — 0.009 |  | 0.0086181 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | KSCSSKR- Lauren onsite running generator, testing diesel containment flood and hi/low temp MTSS- Terry R onsite running diesel generator. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; containment [safety] | flood [critical]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | RHAMF1 - Power blip, Generator started and stopped, FAN 1 and Fan 2 VFD fault alarms, Recirculation pumps 1/2 not running. Notified Daniel K. He requested to call NAC. Called Jimmy (NAC), he will attend site. | FLAG | stage2_low_confidence | 0.019498 | ML: above threshold (no LLM available) — 0.019 | fault [equipment_failure]; not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019498 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | HMSS - Young J on site to complete a high wetwell level alarm test and a metro overflow alarm test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; alarm [control_system]; overflow [infrastructure] | overflow [critical]; alarm [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | NBSP, UV System Minor Fault, As per shift report, directed to disregard since bank 1b is running | FLAG | stage2_low_confidence | 0.0090063 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure] | 0.0090063 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | NBSP- Gavin W working on Grit Blowers. Disregard related alarms | FLAG | stage2_low_confidence | 0.0082391 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0082391 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in,weather -5C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | NMSSBP- Barry M onsite testing hi/low temp, aurodialer, and drywell flood | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | JDSS - Darren B on site to complete a generator test run. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005926 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | NBSP - UV System Minor Fault alarm came in. Checked site. Disregarded as per shift report. 1 Bank is running | FLAG | stage2_low_confidence | 0.01257 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.01257 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | GRSSWA- Darren B onsite running generator and performing health and safety work orders. | FLAG | stage2_low_confidence | 0.012057 | ML: above threshold (no LLM available) — 0.012 | work order [maintenance_action] | 0.012057 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | NMSSBP - Barry M. running generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056688 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | EGSSSC - Diesel failure alarm came in on the dialer. Checked site. Generator is not running and site is connected to hydro power | FLAG | stage2_low_confidence | 0.01817 | ML: above threshold (no LLM available) — 0.018 | failure [equipment_failure]; not running [equipment_failure]; alarm [control_system] | 0.01817 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | AUSS - Kevin S testing temperature, Drywell flood alarms and dialer alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | NBSP- Inlet Channel High Float, Mech Bar Screen Dif. Level HiHi Alarm, Bar Screen max successive starts. Notified Gavin W. Requested to clear alarm | FLAG | stage2_low_confidence | 0.01039 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.01039 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | SUSP, SUSSWB, JDSS- Evgeny S rebooting OITs. Disregard Heartbeat alarms. KSSSQW- Talha H working on OITs. Disregard Heartbeat Alarm. | FLAG | stage2_low_confidence | 0.0081585 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0081585 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | AUSSSR - cleared line valve faults from generator run at AUSS. Notified Kevin S. SUSSWB - Cam B. running generator | FLAG | stage2_low_confidence | 0.0097166 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.0097166 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | Carter D signing in, -9D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041513 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | RHRSTR, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040424 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | LSSS, Marcos T on site, requests PCS to reset OIT, notified Ian W who instructed to call Artour L as Ian is currently driving. Notified Artour L, he will look into the matter | FLAG | stage2_low_confidence | 0.0099264 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099264 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | Christan Van Beek signing in. Weather: -23C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046107 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | BLSS - Screen Differential Level Hi alarm came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0077612 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077612 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | KBSP - Marcus R working on DO sensors. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057599 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | NBSP - Scum Hopper Level HiHi alarm came in. Checked site. Trends indicate a spike but came back to optimal range. Alarm cleared | FLAG | stage2_low_confidence | 0.0096183 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0096183 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | AUSS - Satnam M. working on generator, will be disconnected for 30min 9:00 - finished power work, cleared related alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.004563 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | AUSSSR - Aysix System Heartbeat alarm came in. Checked site. Alarm was able to clear | FLAG | stage2_low_confidence | 0.0078245 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0078245 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -9 C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046282 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | MTSS- Communication Loss to MTSS. Alarm cleared on its own. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070234 | 0 | 0
2026-02 | 2026-02-06 | All Wastewater System ROC General | ROC | NBSSJA, Eric S on site, replacing diesel level sensor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057973 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | MTSS - Talha H finished with the OIT reboot and has cleared the historian heartbeat alarm. | FLAG | stage2_low_confidence | 0.0078117 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0078117 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | NMSSBP - Daniel K called to inform that the gate is open on site and requested a call to security. Contacted security who informed that the gate is missing a piece of locking hardware which has been ordered. Security is completing two manual checks of the site daily. 14:37 - NMSSBP - Daniel K requested the assistance of an additional operator to complete work required to get the barscreen active. Contacted Marcus R who will attend site. Created CMU5#W11645886 #consult #CMU5 | FLAG | stage2_low_confidence | 0.013593 | ML: above threshold (no LLM available) — 0.014 |  | 0.013593 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | NMSSBP - Marcus R leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055548 | 0 | 0
2026-02 | 2026-02-03 | All Wastewater System ROC General | ROC | BLSS - Young J running generator and testing eyewash alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070125 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -8C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -19C and clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044683 | 0 | 0
2026-02 | 2026-02-07 | All Wastewater System ROC General | ROC | RHAMF1 - Unit Recirculation Pump 2 Overload Alarm came in. Checked site. Both fans are still running. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0074537 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0074537 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | AUSS - Kevin S running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056123 | 0 | 0
2026-02 | 2026-02-09 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-02 | 2026-02-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-02 | 2026-02-05 | All Wastewater System ROC General | ROC | KBSP- Marcus R working on aeration blower 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045157 | 0 | 0
2026-02 | 2026-02-27 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site for station check Reviewed scada and trends, Duty active, reservoir at 67%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1505 hrs Reservoir pre: FCL = 2.26 mg/l. Analyzer: 2.30 mg/l @ 1530 hrs: Reservoir Post: FCL= 1.59 mg/l. Analyzer: 1.53 mg/l @ 1534 hrs: Treated FCL = 1.53 mg/l Analyzer: 1.57mg/l TCL = 1.71 mg/l Chemicals: Hypo System: Duty1: pump2 Pumps speed: 49% Dosage: 10:50 mL/min Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 145% P2 ~ 145% Well pump discharge pressure: P2 ~ 445 P3 ~ 729 No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.00063769 | 0 | 0
2026-02 | 2026-02-04 | All Wastewater System ROC General | ROC | KSSP - Membrane air blower 1 failed to start, collection blower 2 high diff pressure alarm and Alum chem room MUA diff pressure hi alarm. Called Chase J to inform. | FLAG | stage2_low_confidence | 0.016463 | ML: above threshold (no LLM available) — 0.016 | failed [equipment_failure]; alarm [control_system] | 0.016463 | 0 | 0
2026-02 | 2026-02-23 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | Onsite to complete station check. Verified online chlorine analyzers via hach field kit. Post reservoir analyzer: 0.98 mg/L Post reservoir grab: 0.78/0.80/0.79 mg/L Treated analyzer: 0.92 mg/L Treated free grab: 0.75/0.75 mg/L Calibrated analyzers based on grab results. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066824 | 0 | 0
2026-02 | 2026-02-25 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site to collect weekly bact samples from raw and treated sample taps (W11619988). Verified online chlorine analyzers via hach field kit. Post-reservoir free analyzer: 1.03 mg/L Grab: 1.00 mg/L @ 11:55 Treated free analyzer: 0.96 mg/L Treated free grab: 0.93 mg/L Treated total grab: 1.00 mg/L Reservoir inlet free analyzer: 3.58 mg/L Reservoir inlet free grab: 3.10/3.12 mg/L Calibrated reservoir inlet free analyzer based on average of grab results. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062755 | 0 | 0
2026-02 | 2026-02-23 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off during the updates and the Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.010733 | ML: above threshold (no LLM available) — 0.011 |  | 0.010733 | 0 | 0
2026-02 | 2026-02-24 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | - increase dosage factor 130% - 140% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043509 | 0 | 0
2026-02 | 2026-02-02 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site for station check Reviewed Scada and trends, Duty just deactivated, reservoir at 89%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None | FLAG | stage2_low_confidence | 0.0073168 | ML: above threshold (no LLM available) — 0.007 | scada [control_system]; alarm [control_system] | 0.0073168 | 0 | 0
2026-02 | 2026-02-23 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | -increased dosage factor in 1 & 2 125% - 130% -activated duty early target an inlet residual of over 3.00mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050684 | 0 | 0
2026-02 | 2026-02-15 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | Responding to post reservoir analyzer low alarm; Pre-inj (mg/L) 1635 Analyzer FCl 0.46 Grab FCl 1.11 Treated (mg/L 1644 Analyzer FCl 0.78 Grab FCl 1.12 Drained sample reservoirs, zero calibrated, then span calibrated based on multiple grabs for both Treated and Post-Reservoir chlorine analyzers. Analyzer values spiked once reservoirs were drained. Added Depolox sand to keep probe clean. Drifting analyzer values may have been interference from recent analyzer maintenance / cleaning, or changes in aquifer chemistry. Will continue to monitor. Based on grabs and pre-reservoir analyzer, chlorine dosing appears to have been adequate. Reservoir just finished filling to duty 1, will not run to test analyzers and dosage at this time. Primed hypo P2 line, pump also appears fine. No other issues. | FLAG | stage2_low_confidence | 0.009912 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.009912 | 0 | 0
2026-02 | 2026-02-13 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to complete station check. Review trends. Inspect hypo P1 and 2, suction and discharge lines have air pockets (post-reservoir analyzer trending down over last cycle). Replace tube elements and prime pumps / lines. Activate duty to monitor hypo dosing. Enter data into PWQ. Span calibrate: Treated FCl analyzer from 1.33 to 1.59mg/L Post-Reservoir FCl from 0.87 to 1.50mg/L Pre-Reservoir FCl from 2.69 to 3.20mg/L -based on grabs Dose calculation and analyzer trending combined with air pockets in chemical lines indicated lower chemical dosing over previous cycle. Analyzers will need to be monitored and adjusted on next station check, based on grabs and span cal adjustments from today. | FLAG | stage2_low_confidence | 0.01957 | ML: above threshold (no LLM available) — 0.02 |  | 0.01957 | 0 | 0
2026-02 | 2026-02-17 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site for station check and collection of weekly bacT sample Reviewed scada and trends, Duty active, reservoir at 79%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1505 hrs Reservoir pre: FCL = 2.94 mg/l. Analyzer: 2.95 mg/l @ 1508 hrs: Reservoir Post: FCL= 1.38 mg/l. Analyzer: 1.51 mg/l Adjusted Post FCL analyzer from 1.54 to 1.38 mg/l based on average of 3 grabs @ 0924 hrs: Treated FCL = 1.2 mg/l Analyzer: 1.54mg/l TCL = 1.53 mg/l Adjusted Adjusted treated FCL analyzer reading from 1.51 to 1.28 mg/l based on average of 3 grabs Chemicals: Hypo System: Duty1: pump2 Pumps speed: 42% Dosage: 9.03 mL/min Standby: hypo pump2 Rotated hypo pumps duty, placed hypo p1 in duty1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 446 P3 ~ 731 No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0017669 | 0 | 0
2026-02 | 2026-02-18 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site to top up hypo | FLAG | stage2_low_confidence | 0.011497 | ML: above threshold (no LLM available) — 0.011 |  | 0.011497 | 0 | 0
2026-02 | 2026-02-13 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | Filled hypo tanks 26/27 L to 37/37 L | FLAG | stage2_low_confidence | 0.0099366 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099366 | 0 | 0
2026-02 | 2026-02-11 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site for station check and collection of weekly bacT samples Reviewed scada and trends, Duty active, reservoir at 77%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 0901 hrs Reservoir pre: FCL = 3.14 mg/l. Analyzer: 3.11 mg/l @ 0909 hrs: Reservoir Post: FCL= 1.77 mg/l. Analyzer: 1.78 mg/l @ 0924 hrs: Treated FCL = 1.66 mg/l TCL = 1.79 mg/l Analyzer: 1.26mg/l Adjusted treated FCL analyzer reading from 1.26 to 1.66 mg/l based on average of 3 grabs Chemicals: Hypo System: Duty1: pump2 Pumps speed: 42% Dosage: 9.03 mL/min Standby: hypo pump2 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 446 P3 ~ 731 No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.00046432 | 0 | 0
2026-02 | 2026-02-06 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site for station check Reviewed scada and trends, activated duty Duty active, reservoir at 64%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1240 hrs Reservoir pre: FCL = 2.84 mg/l. Analyzer: 2.86 mg/l @ 1233 hrs: Reservoir Post: FCL= 1.63 mg/l. Analyzer: 1.59 mg/l @ 1225 hrs: Treated FCL = 1.59 mg/l Analyzer: 1.81mg/l TCL = 1.00 mg/l Adjusted treated chlorine analyzer based of repeated 2 grabs from 1 mg/l to 1.59 mg/l Chemicals: Hypo System: Duty1: pump2 Pumps speed: 42% Dosage: 9.02 mL/min Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 446 P3 ~ 729 Deactivated duty after station checks | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.00094783 | 0 | 0
2026-02 | 2026-02-03 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site to complete the following WOs: JHSC Health and Safety Inspection (1M) Generator Test Run Pressure Regulating Valve Maintenance Turbidity Analyzer TU5300 Maintenance and Calibration Sodium Hypochlorite System Maintenance, Wells 2/3 , Valve Exercise Wells 2/3, Pumps 2 and 3 Strainer Air Release valve inpection and cleaning Siemens Depolox 5/Micro 2000 Chlorine Analyzer started diesel generator at 1050 hrs and stopped at 1216 hrs Generator hours at start 311.12 Generator hours at stop 312.18 Notified ROC before and after completion of WOs Activated duty, verified analyzers reading NO issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0022786 | 0 | 0
2026-02 | 2026-02-09 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site for station check Reviewed scada and trends, activated duty Duty active, reservoir at 73%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1230 hrs Reservoir pre: FCL = 3.24 mg/l. Analyzer: 3.20 mg/l @ 1234 hrs: Reservoir Post: FCL= 1.77 mg/l. Analyzer: 1.76 mg/l @ 1244 hrs: Treated FCL = 1.67 mg/l Analyzer: 1.87mg/l TCL = 1.64 mg/l Chemicals: Hypo System: Duty1: pump1 Pumps speed: 43% Dosage: 9.20 mL/min Standby: hypo pump2 Rotated hypo pumps duty, placed hypo p1 in duty1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 454 P3 ~ 731 Deactivated duty after station checks | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.00056005 | 0 | 0
2026-02 | 2026-02-04 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | <span style="color: rgba(0, 0, 0, 0.87); font-family: Muli, sans-serif; font-size: 14.4px; letter-spacing: 0.2864px; background-color: rgb(255, 255, 255);">Did some troubleshoot with post reservoir treated analyzer and turbidity meter. Noticed chlorine analyzer dropping after several adjustments. Cleaned analyzer sample bowl, flushed sample line and zeroed analyzer. Chlorine analyzer share sample line with turbidity analyzer, cleaned turb analyzer and calibrated.</span><br style="outline: none; box-sizing: border-box; cursor: pointer; overflow-wrap: inherit; word-break: inherit; color: rgba(0, 0, 0, 0.87); font-family: Muli, sans-serif; font-size: 14.4px; letter-spacing: 0.2864px; background-color: rgb(255, 255, 255);"><span style="color: rgba(0, 0, 0, 0.87); font-family: Muli, sans-serif; font-size: 14.4px; letter-spacing: 0.2864px; background-color: rgb(255, 255, 255);">Returned both analyzers to service after cleaning and activated duty for raw and treated water bacT sample collection</span> | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure] | overflow [critical]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-25 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11620710: Sample results (08:12): Free- 0.05, Total- 2.84 * Adjusted free analyzer from 0.15 to 0.05 based on multiple grabs (0.05, 0.05, 0.06) * Adjusted total analyzer from 2.61 to 2.84 based on multiple grabs (2.84, 2.84, 2.84) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056826 | 0 | 0
2026-02 | 2026-02-12 | Aurora (East) First Commerce Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Took weekly bacti sample Verified analyzer and entered all readings and grabs into PWQ sheet Outlet Free@0943 G:0.05 A:0.06mg/L Outlet Total@0944 G:2.80 A:2.86mg/L Mono-2.45 FA-0.06 TA-0.55 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039428 | 0 | 0
2026-02 | 2026-02-19 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp tests Ventilation inspection Inlet/outlet heat trace inspection Dehumidifier cleaning/inspection Depolox analyzer maintenance Air valve flush/inspection Portable generator test/inspection Performed station housekeeping Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0090591 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action] | 0.0090591 | 0 | 0
2026-02 | 2026-02-17 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11606256: Sample results (10:18): Free- 0.00, Total- 2.60 * Adjusted total analyzer from 2.77 to 2.60 based on multiple grabs (2.58, 2.60, 2.60) * Topped up acetate depolox reagent * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044949 | 0 | 0
2026-02 | 2026-02-04 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite for station check/collect samples- WO# W11569241, W11569211: Sample results (14:38): Free- 0.07, Total- 2.80 * Replaced KI depolox reagent * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044569 | 0 | 0
2026-02 | 2026-02-27 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. Pumps 4 and 5 in standby. Entered data into process sheets. No issues found. | FLAG | stage2_low_confidence | 0.0073447 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073447 | 0 | 0
2026-02 | 2026-02-24 | Aurora (East) Wellington Pumping Station | CENTRAL | -Performed station check - logged station readings into PWQ sheet | FLAG | stage2_low_confidence | 0.014771 | ML: above threshold (no LLM available) — 0.015 |  | 0.014771 | 0 | 0
2026-02 | 2026-02-26 | Aurora (East) Wellington Pumping Station | CENTRAL | -Finished the following work orders *Valve exercises *Pump and motor inspection *Ventilation inspection *Performed sump pit inspection *Tested low temp alarm *Tested flood alarm *Diesel generator test run Start fuel- 1803 L Stop fuel- 1763 L Start hours- 372.1 Stop hours- 373.3 Pre test inspection completed- no abnormalities* Generator tested under load (P4): 1799 rpm 600 V 60 Hz 97 A Oil pressure- 40psi Oil temp - 65C Coolant temp- 170 F No abnormalities during generator test run- placed generator back into auto once test completed- station back on hydro power *Performed H&S inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-02 | Aurora (East) Wellington Pumping Station | CENTRAL | On-site for a station and equipment check No issues found All readings entered into PWQ sheet | FLAG | stage2_low_confidence | 0.010949 | ML: above threshold (no LLM available) — 0.011 |  | 0.010949 | 0 | 0
2026-02 | 2026-02-02 | Aurora (East) Wellington Pumping Station | CENTRAL | Look at check valve 4 Can?t hear any water passing with pump 5 running Need operations to isolate valve to open top cover plate for visual inspection | FLAG | stage2_low_confidence | 0.011634 | ML: above threshold (no LLM available) — 0.012 |  | 0.011634 | 0 | 0
2026-02 | 2026-02-25 | Aurora (East) Wellington Pumping Station | CENTRAL | Onsite to put pump 4 back in service after check valve replacement. Tested the pump-ok Performed air valve maintenance on discharge header valve that was passing water-ok Leaving site with pump 4 running in auto | FLAG | stage2_low_confidence | 0.01287 | ML: above threshold (no LLM available) — 0.013 |  | 0.01287 | 0 | 0
2026-02 | 2026-02-20 | Aurora (East) Wellington Pumping Station | CENTRAL | Onsite for station check Recordings in PD sheet Pump 4 OOS until wired by electrician. Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-19 | Aurora (East) Wellington Pumping Station | CENTRAL | Vibration reading | FLAG | stage2_low_confidence | 0.021721 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021721 | 0 | 0
2026-02 | 2026-02-19 | Aurora (East) Wellington Pumping Station | CENTRAL | Chris Iliohan Tyler Smith in to remove check valve on pump 4 work in progress | FLAG | stage2_low_confidence | 0.011988 | ML: above threshold (no LLM available) — 0.012 |  | 0.011988 | 0 | 0
2026-02 | 2026-02-20 | Aurora (East) Wellington Pumping Station | CENTRAL | Chris Iliohan Tyler Smith complete install of new check valve on pump 4. Electrician to wire up pressure sensor. | FLAG | stage2_low_confidence | 0.014102 | ML: above threshold (no LLM available) — 0.014 |  | 0.014102 | 0 | 0
2026-02 | 2026-02-06 | Aurora (East) Wellington Pumping Station | CENTRAL | Onsite for station check: Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0093813 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093813 | 0 | 0
2026-02 | 2026-02-18 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. 09:24 Pump 5 running at 165 l/s. Pump 4 remains LOTO and isolated due to passing CV. Entered data into process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067981 | 0 | 0
2026-02 | 2026-02-13 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. 11:27 Pump 5 standby. Pump 4 remains LOTO and isolated due to passing CV. Entered data into process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064443 | 0 | 0
2026-02 | 2026-02-09 | Aurora (East) Wellington Pumping Station | CENTRAL | Station Check (no issues found) Input data to PWQ | FLAG | stage2_low_confidence | 0.011449 | ML: above threshold (no LLM available) — 0.011 |  | 0.011449 | 0 | 0
2026-02 | 2026-02-03 | Aurora (East) Wellington Pumping Station | CENTRAL | Measure slanted disc Motor running backwards check passing Closed discharge valve put operation lock on ordering new swing flex check for replacement | FLAG | stage2_low_confidence | 0.015274 | ML: above threshold (no LLM available) — 0.015 |  | 0.015274 | 0 | 0
2026-02 | 2026-02-25 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11620710: Sample results (12:36): Free- 0.09, Total- 2.88 * Adjusted total analyzer from 2.67 to 2.88 based on multiple grabs (2.84, 2.88, 2.88) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054814 | 0 | 0
2026-02 | 2026-02-11 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | On site for station check and sampling. MBDW - W11589385. 13:53 hrs. Tower level at 45% and draining. 13:55 hrs. Verified analyzer (mg/l) and collected sample. Free chlorine grab: 0.09. Analyzers: 0.07. Total chlorine grab: 2.92. Analyzer 2.95. Filled out data into process sheets. Topped up analyzer KI and acetate reagent. No issues found on site. | FLAG | stage2_low_confidence | 0.0079862 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079862 | 0 | 0
2026-02 | 2026-02-17 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11606256: Sample results (14:20): Free- 0.00, Total- 2.70 * Adjusted total analyzer from 3.22 to 2.70 based on multiple grabs (2.66, 2.70, 2.68, 2.70) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056378 | 0 | 0
2026-02 | 2026-02-19 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | -Finished the following work orders *Depolox analyzer maintenance *H&S inspection *Valve exercises | FLAG | stage2_low_confidence | 0.016622 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action] | 0.016622 | 0 | 0
2026-02 | 2026-02-04 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite for station check/collect samples- WO# W11569241, W11569211: Sample results (11:52): Free- 0.04, Total- 2.84 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055881 | 0 | 0
2026-02 | 2026-02-23 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Station and equipment check Took grabs @ 9:45 am (reform/boost) from post sample tap Total: 3.22 mg/l Free0.05 mg/l All other readings on PD sheets Batched ammonia tank 1 Chemicals/reagents on Ops normal | FLAG | stage2_low_confidence | 0.0090197 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure] | 0.0090197 | 0 | 0
2026-02 | 2026-02-25 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and sampling. W11619908 11:13 outlet flow at 400 L/s. Rechloramination boosting on. Reservoir level at 74%. Topped up chemscan sulphuric acid reagent. Verified residuals (mg/l): 11:25 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03 Depolox 5: 0.06. Total grab: 1.62 Micro2000: 1.61 Chemscan: 1.59 Monochloramine grab: 1.52 Chemscan: 1.59. Free ammonia grab: 0.07. Chemscan: 0.06. Total ammonia grab: 0.38. Chemscan: 0.35. Nitrite: 0.003. pH: 8.00. Temperatrue: 7 Celsius. 11:32 Post-injection chlorine grabs: Free grab: 0.07. Depolox 5: 0.05. Total grab: 3.20. Micro2000: 3.22 Chemscan: 1.32 Monochloramine grab: 2.85 Chemscan: 2.77. Free ammonia grab: 0.04. Chemscan: 0.08. Total ammonia grab: 0.61. Chemscan: 0.59. No other issues found. | FLAG | stage2_low_confidence | 0.0088292 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure] | 0.0088292 | 0 | 0
2026-02 | 2026-02-26 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Under the direction of Ben Hess, Worked along side Network Analyst Aaron Magsakay, to replaced a Network switch to Cisco IE3300 inside a Control panel and Remote IO panel. Informed ROC prior to begin this work Provided 24 VDC power to new switch from 24VDC power supply. When powered up Remote IO panel network switch, RACK 0 SLOT 7 Digital Input Card fuse was blown. Replaced the Fuse. all ok There is a trend gap on SCADA between 09:27 AM to 10:04 AM due to this work. Some of the trends will be Back filled from PAC Back up files After the replacement, checked all the ports and reset the comm alarms. | FLAG | stage2_low_confidence | 0.034916 | ML: above threshold (no LLM available) — 0.035 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.034916 | 0 | 0
2026-02 | 2026-02-27 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. 13:55 outlet flow at 366 L/s. Rechloramination boosting on. Reservoir level at 46%. Topped up ammonia tank 2. Replaced chlorine cylinder bank A with Joseph D?eMarco. Verified residuals (mg/l): 14:08 Pre-injection/outlet grabs. Free grab: 0.02 Depolox 5: 0.05. Total grab: 1.63 Micro2000: 1.66 Chemscan: 1.61. Monochloramine grab: 1.56 Chemscan: 1.61. Free ammonia grab: 0.08. Chemscan: 0.06. Total ammonia grab: 0.39. Chemscan: 0.37. 14:29 Post-injection chlorine grabs. Rechloramination has stopped dosing. Free grab: 0.02. Depolox 5: 0.01. Total grab: 1.70. Micro2000: 1.77 Monochloramine grab: 1.53 Chemscan: 1.58 Free ammonia grab: 0.04. Chemscan: 0.12. Total ammonia grab: 0.41. Chemscan: 0.51. No issues found on site. | FLAG | stage2_low_confidence | 0.010483 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure] | 0.010483 | 0 | 0
2026-02 | 2026-02-02 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Onsite for station check: Changed CL2 cylinders: 0/26 kg to 68/26 kg * Verified analyzers Calculated dosages Chemical levels- Ok Depolox reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038994 | 0 | 0
2026-02 | 2026-02-26 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | 10:06 ROC notified while I was not at site that that SCADA tech Yash Patel was performing network upgrades to AURSBS and that sample pumps 1 and 2 had stopped running. These sample pumps supply water to chlorine analyzers and when they dont run the analyzer readings spike high, triggering hihi alarms (5.00 mg/l). ROC notified me they had turned on both sample pumps back on and that dosing systems currently interlocked. I directed ROC to place chlorine and ammonia dosing systems in manual off. 10:37 notified Ben Hess and Justin Quail of chlorine dosing occuring while a loss of trends and accurate analyzer readings occured. 11:14 Arrived on site. Reviewed trends. Station chlorine dosing system and chlorine sample trends are missing from at 09:27 until 10:04. Station was dosing and outlet flow at 480 l/s before the data loss. Yash informed me missing data should be recorded in PAC and processed/ back dated by tomorrow morning at 08:30. Station trends currently show chlorinator 2 open and closing at 10:04, and fully closed by 10:05:15, with 1 minute and 15 seconds of dosing occuring while analyzers reading 5.00 mg/l, and a furhter 38 minutes without any trending data. 11:26 verified chlorine analyzers (mg/l): Post injection free: 0.02. Depolox 5: 0.01. Post injection total: 1.66 micro2000: 1.68. Chemscan: 1.66. 11:52 placed chemical dosing system back online. Notified ROC system is back online. No issues remain. Will discuss with Team lead and supervisor is adverse filling required. | FLAG | stage2_low_confidence | 0.51011 | ML: above threshold (no LLM available) — 0.51 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.51011 | 0 | 0
2026-02 | 2026-02-19 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Onsite to complete work orders. 09:36 Notified ROC of working on site. Station outlet flow a 440 l/s and currently dosing. Dehumidifier cleaning and inspection. Dechlorination puck dispenser cleaning. Sump pit inspection. JHSC inspection. Chlorine Chemical dosing system inspection. Ammonia pump 1 inpsection. Replaced tubing element. Max pumprate 1500 ml/ min. Ammonia dosing system inspection. Changed chlorine cylinder bank B with Alex Bell. 11:39 chemscan analyzer maintenance. Analyzer offline alarm triggered. Chemical systems are no longer dosing as duty is off. Ammonia pumps in manual off. Tested zero with no issues. Flushed/cleaned strainers. Topped up Potassium Iodine reagent. No issues found. Siemens Depolox 5/micro 2000 chlorine anlayzer maintenance. Verified analyzers (mg/l) 11:55. Pre injection free: 0.04. depolox: 0.06. Pre injection total: 1.64. Micro2000: 1.58. Chemscan: 1.62. 12:00 Post injection free: 0.07/0.08/0.07. Analyzer: 0.01. Adjusted analyzer to match grabs: Post injection total: 1.65. micro2000: 1.70. Chemscan: 1.63. 12:18 Chlorine leak detection test. Removed shut off valves from cylinders and tested leak sensor. Chlorine emerg system fault alarm triggered and chlorine gas alarm triggered. No issues found with system. Acknowledged and cleared alarm. No new issues found on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; gas alarm [safety] | fault [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; gas alarm [safety] |  | 1 | 0
2026-02 | 2026-02-19 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Onsite to respond to post injection free chlorine hihi of 0.30 mg/l. Dosing system interlocked at 13:45. 14:15 grab 0.05. Analyzer: 0.05. Cleared interlock and dosing resumed. Analyzer began climbing. 14:25 Grab 0.05/0.05/0.05. Analyzer 0.28. Adjusted to match grabs. Analyzer stabilized and no issues remain. | FLAG | stage2_low_confidence | 0.014142 | ML: above threshold (no LLM available) — 0.014 |  | 0.014142 | 0 | 0
2026-02 | 2026-02-17 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and sampling. Card readers not operating. Notified Security and Christine floyd. Technition on the way. Accessed site using eKey. 11:59 outlet flow at 40 L/s. Rechloramination boosting on. Reservoir level at 74%. Topped up ammonia tank 1. 12:09 Central duty stopped and rechloramination dosing stopped. Verified residuals (mg/l): 12:23 Pre-injection/outlet grabs. Collected sample. W11605405 Free grab: 0.08 Depolox 5: 0.06. Total grab: 1.69 Micro2000: 1.72 Chemscan: 1.65 Monochloramine grab: 1.57. Chemscan: 1.64. Free ammonia grab: 0.07. Chemscan: 0.05. Total ammonia grab: 0.38. Chemscan: 0.35. Nitrite: 0.003. pH: 8.05. Temperatrue: 7 Celsius. 12:36 Post-injection chlorine grabs: Free grab: 0.05. Depolox 5: 0.01. Total grab: 1.70. Micro2000: 1.66 Chemscan: 1.70 Monochloramine grab: 1.56 Chemscan: 1.60. Free ammonia grab: 0.08. Chemscan: 0.09. Total ammonia grab: 0.39. Chemscan: 0.36. No other issues found. | FLAG | stage2_low_confidence | 0.011023 | ML: above threshold (no LLM available) — 0.011 | oos [equipment_failure] | 0.011023 | 0 | 0
2026-02 | 2026-02-20 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Onsite for station check Recordings in PD sheet Filled ammonia tank 2 JHSC inspection -ok Air valve flush Hoist and crane inspection -ok Station ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003836 | 0 | 0
2026-02 | 2026-02-11 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified Depoloxs (mg/L) 8:43 Pre: Free: Grab 0.04, A 0.06 Total: Grab 1.60, A 1.54 8:55 Post: Free: Grab 0.07, A 0.06 Total: Grab 3.12, A 3.09 9:20 #11588572 bact. & operational samples Ammonia Tank 2 (new batch) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026645 | 0 | 0
2026-02 | 2026-02-13 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. 08:50 outlet flow at 0 L/s. Rechloramination boosting not on. Reservoir level at 56%. Topped up ammonia tank 2. Verified residuals (mg/l): 09:26 Pre-injection/outlet grabs: Free grab: 0.09 Depolox 5: 0.06. Total grab: 1.55 Micro2000: 1.53. Chemscan: 1.60 09:49 Monochloramine grab: 1.38. Chemscan: 1.44. Free ammonia grab: 0.09. Chemscan: 0.09. Total ammonia grab: 0.36. Chemscan: 0.27. Adjusted offset to match grab. 09:41 Post-injection chlorine grabs: Free grab: 0.06. Depolox 5: 0.01. Total grab: 1.53. Micro2000: 1.52 Chemscan: 1.55 Monochloramine grab: 1.44. Chemscan: 1.52 Free ammonia grab: 0.08. Chemscan: 0.12. Total ammonia grab: 0.37. Chemscan: 0.36. 10:01 activated Aurora Central duty. Found left chlorine cylinder bank not pulling any more chlorine. Scale reading 10.3 kg but appear empty. Manually adjusted scale to read 0 kg. 10:30 Joe D. onsite and assisted in replacing left chlorine cylinder bank. No other issues found. | FLAG | stage2_low_confidence | 0.016749 | ML: above threshold (no LLM available) — 0.017 | oos [equipment_failure] | 0.016749 | 0 | 0
2026-02 | 2026-02-06 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Station and equipment check Change chlorine cylinders with Joe D (right bank) Took grabs from pre injection sample tap @ 8:25 am Total: 1.70 mg/l Free: 0.05 mg/l Analyzers matched Took grabs from post injection sample tap @ 8:35 am Total: 3.21 mg/l Free: 0.05 mg/l Analyzers matched All other readings on PD sheets shared online file Changed yellow reagent on chemscan unit @ 9:40 am Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044444 | 0 | 0
2026-02 | 2026-02-04 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Station and equipment check Take weekly BacT sample and grabs @ 13:15 (post) Total: 1.91 mg/l Free: 0.02 mg/l No adjustments required Topped up Ammonia tank 1 Chemicals/reagents ok Chemical system not active at time of readings Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048474 | 0 | 0
2026-02 | 2026-02-09 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified Depolox (mg/L) 12:25 PRE: Free: Grab 0.06, A 0.06 Total: Grab 1.72, A 1.73 12:36 POST: Free: Grab 0.04, A 0.01 Total: Grab 1.70, A 1.67 Chemscan: (Green, Muratic/distilled top up) Ammonia Tank #2 (new batch) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026879 | 0 | 0
2026-02 | 2026-02-25 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | On site for station check and sampling. W11619908. 12:25 Tower level at 56% and draining at 4 l/s. 12:30 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.05. Analyzer: 0.02. Total chlorine grab: 2.22 analyzer: 2.22. Nitrite grab: 0.000. Free ammonia: 0.08 Total ammonia: 0.46. Monochloramine: 1.93. Temperature: 3.6 celsius. pH: 8.01. No issues on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037271 | 0 | 0
2026-02 | 2026-02-17 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | On site for station check and sampling. MBDW - W11605405. 13:05 Deactivated zone 3 duty. 13:08 Tower level at 64% and draining. 13:33 hrs. Verified analyzer (mg/l) and collected sample. Free chlorine grab: 0.09. Analyzers: 0.07. Total chlorine grab: 2.11. Analyzer 2.09. Monochloramine: 1.90. Free ammonia: 0.08. Total ammonia: 0.46. Nitrite: 0.004. pH: 8.01. Temperature: 5.4 Celsius. Filled out data into process sheets. No issues found on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042147 | 0 | 0
2026-02 | 2026-02-18 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | Onsite to complete work orders: Heat trace inspection. 10:27 Low building temperature alarm. triggered alarm no issues. Reservoir sample line flow is low. Dissasembled and found turberculation build up before valve. flushed out and reassembled line. Site cleaning. Portable gas generator inspection and test run. JHSC inspection 11:30 Chlorine analyzer maintenance. Verified chlorine analyzer (mg/l): free grab: 0.05. Analyzer: 0.08. Total grab: 2.11. Analyzer: 2.12. No issues remaining. | FLAG | stage2_low_confidence | 0.020447 | ML: above threshold (no LLM available) — 0.02 | work order [maintenance_action]; alarm [control_system] | 0.020447 | 0 | 0
2026-02 | 2026-02-17 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | Deleted accidental double entry. See prior post. | FLAG | stage2_low_confidence | 0.013768 | ML: above threshold (no LLM available) — 0.014 |  | 0.013768 | 0 | 0
2026-02 | 2026-02-11 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 11:25 Verified CL17s (mg/l) Free: Grab 0.05, A 0.00 (performed zero calibration then cal. standard to 0.05) Total: Grab 2.10, A 2,17 12:45 #11588572 bact. & operational samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055003 | 0 | 0
2026-02 | 2026-02-04 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | Onsite for station check/collect samples- WO# W11568172, W11568601: Sample results (12:38): Free- 0.02, Total- 2.15 * Adjusted total analyzer from 1.99 to 2.15 based on multiple grabs (2.15, 2.15, 2.15) * Replaced KI depolox reagent * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046302 | 0 | 0
2026-02 | 2026-02-25 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/collect sample- WO# W11620710: Sample results (13:15): Free- 0.01, Total- 2.92 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052756 | 0 | 0
2026-02 | 2026-02-27 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-02 | 2026-02-24 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-02 | 2026-02-02 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for Bathurst tank isolation trial Isolated zone valve (Aurora west PD and Newmarket West PD) in the yard, opened HV11 in PS. Ran pumps in different configurations. Performed station check Station ok Reversed changes all back to normal operations | FLAG | stage2_low_confidence | 0.0089179 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089179 | 0 | 0
2026-02 | 2026-02-13 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-02 | 2026-02-19 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | -Finished the following work orders *Chlorine analyzer maintenance *Vent inspection *Tested hi/lo temp alarm *Pump and motor inspection *Dehumidifier cleaning *Performed diesel generator test run Start fuel- 2505 L Stop fuel- 2485 L Start hours- 204.5 Stop hours- 205.8 Pre test inspection completed- no abnormalities* Generator tested under load (P3 and P4): 1799 rpm 600 V 60 Hz 94 A Oil pressure- 428 kpa Coolant temp- 87 C No abnormalities during generator test run- placed generator back into auto once test completed- station back on hydro power *Performed H&S inspection *Performed PRV inspection | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; alarm [control_system] | 0.0022358 | 0 | 0
2026-02 | 2026-02-11 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | On-site for reservoir station check and sampling. W11589385 Reservoir at 63% filling and draining. NM West pumps running in duty. Entered data into pumping station process sheets. 13:23 verified analyzer (mg/l): Free grab: 0.03. Analyzer: 0.04. Total grab: 2.94. Analyzer: 2.95. Collected sample. No other issues found. Left site. | FLAG | stage2_low_confidence | 0.0088374 | ML: above threshold (no LLM available) — 0.009 |  | 0.0088374 | 0 | 0
2026-02 | 2026-02-17 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/collect sample- WO# W11606256: Sample results (13:35): Free- 0.01, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052756 | 0 | 0
2026-02 | 2026-02-20 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/complete WO: Verified analyzers Depolox reagents- Ok Performed station housekeeping Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066393 | 0 | 0
2026-02 | 2026-02-05 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Motor service 1 - 4 Changed oil on all four motors | FLAG | stage2_low_confidence | 0.0088868 | ML: above threshold (no LLM available) — 0.009 |  | 0.0088868 | 0 | 0
2026-02 | 2026-02-09 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Adjusted total analyzer from 2.83 to 3.00 based on multiple grabs (2.98, 3.00, 3.00) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061624 | 0 | 0
2026-02 | 2026-02-04 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/collect samples- WO# W11569241, W11569211: Sample results (11:00): Free- 0.03, Total- 3.08 * Adjusted total analyzer from 2.85 to 3.08 based on multiple grabs (3.08, 3.08, 3.08) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058064 | 0 | 0
2026-02 | 2026-02-06 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Adjusted total analyzer from 3.08 to 2.90 based on multiple grabs (2.88, 2.90, 2.90) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061624 | 0 | 0
2026-02 | 2026-02-26 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite to complete work orders: Diesel generator inspection and test run. 09:25 Generator pre-inspection. Run hours at 239 and 40 minutes. Battery 27.3 Volts. Oil level ok. Battery terminals ok. Coolant level ok. Fuel level 2188 L (44%). Notified ROC of work to be completed. 09:37 initiated Diesel run. 09:42 Activated zone 3 to run pump 2 to increase generator load. AUETAD tower level at 49%. 09:50. Placed all chemical dosing in manual off. 09:53 Chlorine leak detection test. Halogen emergency valve shut off inpsection. Scrubber 1 fail to start. Retested for longer and found no issues. Acknowledged and cleared alarms. 12:12. Placed all dosing systems back online. Found chlorine room supply fan 2 and exhaust fan 1 breakers open. Closed breakers and fans worked with no issues. Dechlorination puck dispenser cleaning and inspection. 10:40 Chlorine chemical system inspection. Uncommanded chlorine system stop alarms triggered while completing a vacuum test on chlorine dosing system. No issues found. 10:42 deactivated zone 3 duty. 10:55 completed generator test. Fuel level at: 2159 L. Run hours: 240 and 53 minutes. No issues remaining. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | emergency [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-27 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for rechlorination station check. 12:50 Reservoir filling at 81 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 68%. Replaced cl17 post injection free and zone 3 total analyzer reagents. Verified analyzer residuals (mg/l): 13:00 Pre-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.04. Total Chlorine grab: 1.94 CL17: 1.91. Chemscan: 1.98. monochloramine grab: 1.66. Chemscan: 1.72. Free ammonia grab: 0.09. Chemscan: 0.05. Adjusted offset to match grab. Total Ammonia: 0.41. Chemscan: 51. Adjusted offset to match grab. 13:16 Post-injection grabs: Free chlorine grab: 0.03 Analyzer: 0.05. Total Chlorine grab: 2.54 CL17: 2.59. Chemscan: 2.64. monochloramine grab: 2.21. Chemscan: 2.23. Free ammonia grab: 0.05. Chemscan: 0.02. Total Ammonia: 0.49. Chemscan: 53. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.024765 | ML: above threshold (no LLM available) — 0.025 | oos [equipment_failure] | 0.024765 | 0 | 0
2026-02 | 2026-02-23 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site to complete station check. -Verified analyzers: Pre Injection Free Chlorine @ 13:08 Grab: 0.06 mg/L Analyzer: 0.04 mg/L Pre Injection Total Chlorine @ 13:08 Grab: 1.87 mg/L Analyzer: 1.92 mg/L Post Injection Free Chlorine @ 13:14 Grab: 0.03 mg/L Analyzer: 0.05 mg/L Post Injection Total Chlorine @ 13:14 Grab: 2.40 mg/L Analyzer: 2.40 mg/L Zone 3 Free Chlorine @ 13:11 Grab: 0.07 mg/L Analyzer: 0.04 mg/L Zone 3 Total Chlorine @ 13:11 Grab: 2.32 mg/L Analyzer: 2.31 mg/L Reservoir Outlet Free Chlorine @ 13:19 Grab: 0.03 mg/L Analyzer: 0.03 mg/L Reservoir Outlet Chlorine @ 13:19 Grab: 2.26 mg/L Analyzer: 2.31 mg/L -Topped up reservoir outlet free chlorine analyzer reagents -Entered data into PD sheet | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00021402 | 0 | 0
2026-02 | 2026-02-25 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check and sampling. W11619908 10:19 Reservoir draining at 17 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting not active. Reservoir level at 66%. Verified analyzer residuals (mg/l): 10:25 Pre-injection grabs: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.40 CL17: 2.35. Chemscan: 2.39. 10:35 Post-injection grabs: Free chlorine grab: 0.3 Analyzer: 0.04. Total Chlorine grab: 2.34 CL17: 2.32. Chemscan: 2.45. 10:38 Zone 3 grabs: Free chlorine 0.04. Analyzer: 0.04 Total chlorine: 2.20. Analzyer: 2.25 10:42 Reservoir outlet grabs and collected sample: Free chlorine grab: 0.02. Analyzer: 0.03. Total chlorine grab: 2.22 Analyzer: 2.29. Monchloramine grab: 2.04. Free ammonia: 0.07. Total ammonia: 0.47. pH: 8.02 Temperature: 5.4 Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.0057871 | 0 | 0
2026-02 | 2026-02-02 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Station and equipment check Verified outlet analyzer only as instrumentation was on site for calibrations, will re verify Wednesday during samples Outlet grabs @ 2:30 pm Total: 2.25 mg/l Free: 0.04 mg/l No adjustments required Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060025 | 0 | 0
2026-02 | 2026-02-02 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite for annual calibrations Informed ROC. They placed duty in manual off Performed maintenance and calibration on Zone 3 Total, Res Outlet free and total, pre injection total AIT, Chlorinators. Zone 3 total A = 2.26 mg/L G = 2.31 mg/L Reservoir Outlet Free A = 0.03 mg/L G = 0.05 mg/L Reservoir Outlet Total. A = 2.24 mg/L G = 2.28 mg/L Pre injection total A = 2.28 mg/L G = 2.30 mg/L Pre injection total chlorine reading briefly went Low/High during mA check. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed building and left site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0012456 | 0 | 0
2026-02 | 2026-02-10 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite to complete work orders: 09:07 Notified ROC of work. Placed dosing system in manaul off. Completed maintenance on all CL17 and CL17sc analzyers. Replaced pre-injection free and reservoir outlet total analyzer reagent. 10:00 Cleaned chemscan analyzer strainers. Tested zero. No issues found. Verified chlorine analyzers (mg/l). 10:25 Pre injection free: 0.08 CL17: 0.03 pre injection total: 1.81 Cl17:1.86. Chemscan analyzer: 1.77. 10:35 Post injection free: 0.05 CL17:0.03 post injection total: 1.78 CL17: 1.84. Chemscan analyzer outlet free: 0.02 cl17:0.03 outlet total: 2.22. CL17: 2.27 Zone 3 free: 0.02 CL17: 0.04 zone 3 total: 2.22. CL17: 2.27. JHSC inspection. Ammonia point visual inspection. 11:19 Chemical tank inspection. Tested ammonia flood alarm. 11:21 placed all dosing pumps back in auto. No issues found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check and sampling. W11605405 14:20 eservoir filling at 68 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 72%. Topped up ammonia tank 2. Verified analyzer residuals (mg/l): 14:32 Pre-injection grabs: Free chlorine grab: 0.08. Analyzer: 0.04. Total Chlorine grab: 1.77 CL17: 1.82. Chemscan: 1.81. 14:36 Post-injection grabs: Free chlorine grab: 0.08 Analyzer: 0.05. Total Chlorine grab: 2.60 CL17: 2.60. Chemscan: 2.71. 14:46 Reservoir outlet grabs and collected sample: Free chlorine grab: 0.03. Analyzer: 0.04. Total chlorine grab: 2.32 Analyzer: 2.33. Monchloramine grab: 2.06 Free ammonia: 0.07. Total ammonia: 0.48. Nitrite: 0.003. pH 8.01. Temperature 5.4 Celsius. 14:46 Zone 3 grabs: Free chlorine 0.03. Analyzer: 0.04 Total chlorine: 2.32. Analzyer: 2.32 Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.0049368 | 0 | 0
2026-02 | 2026-02-18 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Replaced zone 3 free analyzer reagents. Replaced right chlorine cylinder with Joe Demarco. No issues found. | FLAG | stage2_low_confidence | 0.0094328 | ML: above threshold (no LLM available) — 0.009 |  | 0.0094328 | 0 | 0
2026-02 | 2026-02-20 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site to complete station check. -Verified analyzers: Pre Injection Free Chlorine @ 12:23 Grab: 0.07 mg/L Analyzer: 0.04 mg/L Pre Injection Total Chlorine @ 12:23 Grab: 2.32 mg/L Analyzer: 2.36 mg/L Post Injection Free Chlorine @ 12:29 Grab: 0.05 mg/L Analyzer: 0.03 mg/L Post Injection Total Chlorine @ 12:29 Grab: 2.36 mg/L Analyzer: 2.33 mg/L Zone 3 Free Chlorine @ 12:36 Grab: 0.08 mg/L Analyzer: 0.04 mg/L Zone 3 Total Chlorine @ 12:36 Grab: 2.30 mg/L Analyzer: 2.25 mg/L Reservoir Outlet Free Chlorine @ 12:44 Grab: 0.07 mg/L Analyzer: 0.03 mg/L Reservoir Outlet Chlorine @ 12:44 Grab: 2.30 mg/L Analyzer: 2.31 mg/L -Topped up chemscan DI water -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00016914 | 0 | 0
2026-02 | 2026-02-11 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 11:00 PRE: Free: Grab 0.06, A 0.04 Total: Grab 1.80, A 1.85 11:20 POST: Free: Grab 0.05, A 0.03 Total: Grab 2.20, A 2.29 11:30 Reservoir: Free: Grab 0.04, A 0.03 Total: Grab 2.20, A 2.29 11:45 Zone 3: Free: 0.05, A 0.04 Total: 2.15, 2.29 11:10 #11588572 bact. & operational samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0016514 | 0 | 0
2026-02 | 2026-02-13 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check: 13:13 Reservoir draining at 13 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting not active. Reservoir level at 60%. Verified analyzer residuals (mg/l): 13:29 Pre-injection grabs: Free chlorine grab: 0.06. Analyzer: 0.04. Total Chlorine grab: 2.36 CL17: 2.33. Chemscan: 2.37. Monchloramine grab: 2.00 Chemscan: 2.00 Free ammonia: 0.06. Chemscan: 0.02. Total ammonia: 0.45. Chemscan: 0.50. 13:42 Post-injection grabs: Free chlorine grab: 0.05 Analyzer: 0.03. Total Chlorine grab: 2.30 CL17: 2.33. Chemscan: 2.49. 10:09 Monchloramine grab: 2.05. Chemscan: 2.05 Free ammonia: 0.05. Chemscan: 0.02. Total ammonia: 0.46. chemscan: 0.46. 13:56 Zone 3 grabs: Free chlorine 0.03. Analyzer: 0.02 Total chlorine: 2.28. Analzyer: 2.29 13:56 Reservoir outlet grabs and collected sample: Free chlorine grab: 0.03. Analyzer: 0.02. Total chlorine grab: 2.28 Analyzer: 2.32 Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.0083109 | ML: above threshold (no LLM available) — 0.008 | oos [equipment_failure] | 0.0083109 | 0 | 0
2026-02 | 2026-02-09 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 9:30 PRE: Free: Grab 0.03, A 0.03 Total: Grab 1.81, 1.85 9:45 POST: Free: Grab 0.04, A 0.05 Total: Grab 2.48, A 2.44 10:05 Reservoir: Free: Grab 0.03, A 0.03 Total: Grab 2.40, 2.31 10:15 Zone 3: Free: Grab 0.06, A 0.03 Total: Grab 2.38, A 2.29 Chemscan (Green and distilled top up) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0016628 | 0 | 0
2026-02 | 2026-02-06 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Station and equipment check Took grabs @ 10:50 am Post injection Total: 2.35 mg/l Free: 0.04 mg/l Outlet sample tap Total: 2.30 mg/l Free: 0.04 mg/l Chemical system not active at time of readings No adjustments required Topped up ammonia tank 1 Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0028086 | 0 | 0
2026-02 | 2026-02-04 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite for station check/collect samples- WO# W11568172, W11568601: Sample results (13:35): Free- 0.02, Total- 2.18 * Replaced post inj total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035403 | 0 | 0
2026-02 | 2026-02-03 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite for annual calibrations Informed ROC. They placed duty in manual off Performed maintenance and calibration on pre injection and post injection free AIT, post Total AIT, chlorine room gas detector and Chemscan analyzer. Took a multiple grab samples. No adjustments required. Post injection total AIT A = 1.82 mg/L G = 1.81 mg/L Post injection free AIT A = 0.03 mg/L G = 0.05 mg/L Pre injection feee AIT A = 0.04 mg/L G = 0.05 mg/L Post injection total chlorine reading briefly went Low due to tubing popped out. Took a grab sample and confirmed reading of 1.83 mg/l. Secured the tubing and monitored for a while. No issues. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed building and left site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0037095 | 0 | 0
2026-02 | 2026-02-27 | Aurora Well 5 | CENTRAL | Onsite for station check/complete assigned work orders- informed ROC: CL2 leak test Performed station housekeeping Replaced treated free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Work orders created to install safety guard for well motor shaft * | FLAG | stage2_low_confidence | 0.008947 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action]; leak [infrastructure] | 0.008947 | 0 | 0
2026-02 | 2026-02-26 | Aurora Well 5 | CENTRAL | Onsite to complete assigned work orders, and troubleshoot CL2 ejector #2- informed ROC: Rebuilt ejector #2, replaced diaphragm with new one. Once rebuilt, attempted to draw vacuum by locally running CL2 booster #2. Released any air from chlorine booster #2. Still not dosing via chlorinator #2. Will create work order for chlorinator #2 to be investigated further. CL2 booster #2 and chlorinator #2 in local/off until issue resolved. Performed maintenance on silicate injection #1 due to suspected clogged injection point. Isolated the station and pulled silicate injection point #1. Flushed with hot water and cleaned injection point. Re-opened station isolation valves and primed silicate pump #1. Placed pump #1 back into auto and will monitor on next run cycle. Changed CL2 cylinders: 0/41 kg to 68/41 kg * Ammonia system inspection Silicate system inspection Chlorine system inspection Station/equipment- Ok | FLAG | stage2_low_confidence | 0.27232 | ML: above threshold (no LLM available) — 0.272 | oos [equipment_failure]; work order [maintenance_action]; clog [infrastructure]; clogged [infrastructure] | 0.27232 | 0 | 0
2026-02 | 2026-02-25 | Aurora Well 5 | CENTRAL | Onsite for station check/collect samples- WO# W11620710: Sample results (11:58): Free- 0.07, Total- 2.88 * Quarterly raw ph sample: Well 5 raw ph- 8.04 Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030971 | 0 | 0
2026-02 | 2026-02-24 | Aurora Well 5 | CENTRAL | Onsite for station check/complete assigned work orders- informed ROC: H/S inspection Deep well exhaust inspection Exhaust fan/damper inspection CL2 analyzer maintenance Turbidimeter maintenance Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.0058998 | 0 | 0
2026-02 | 2026-02-02 | Aurora Well 5 | CENTRAL | Onsite for station check: Replaced treated total CL17 reagents * Verified analyzers Chemical levels- Ok Station/equipment- Ok Well 5 remains in local/off * | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039234 | 0 | 0
2026-02 | 2026-02-17 | Aurora Well 5 | CENTRAL | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.15mg/L total=2.88mg/L@13:15 influent free=2.62mg/L effluent free=2.48mg/L Analyzer: treated free=0.12mg/L total=2.90mg/L influent free=2.60mg/L effluent free=2.39mg/L -Collected weekly BacT sample YD# W11606256 & in-house water quality samples -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.013714 | ML: above threshold (no LLM available) — 0.014 |  | 0.013714 | 0 | 0
2026-02 | 2026-02-10 | Aurora Well 5 | CENTRAL | Onsite to put well 5 back in service- motor repaired and raw water sample passed 08:45- started back flushing using dechlorination pucks 09:55- treated total grab: 2.58, treated total analyzer: 2.57 09:58- influent total grabs: 2.00, 2.02, 1.98 10:00- backflush completed- closed backflush valve. Contact tank turned over 10:08- selected backflush completed via scada 10:10- started well in man/on- will monitor residuals onsite. Confirmed all chemical systems in auto. influent free recovered shortly after start up 10:20: influent free grab- 2.65 10:20: influent free analyzer- 2.74 10:22: influent free grab- 2.80 10:22: influent free analyzer- 2.83 10:28: influent free grab- 2.86 10:29: influent free analyzer- 2.86 10:38: influent free grab- 2.70 10:38: influent free analyzer- 2.78 10:40: effluent free grab- 0.32 10:40: effluent free analyzer- 0.22 10:45: treated free grab- 0.12 10:45: treated total grab- 1.87 10:45: treated free analyzer- 0.04 10:45: treated total analyzer- 1.94 10:50: effluent free grab- 0.73 10:50: effluent free analyzer- 0.66 10:58: effluent free grab- 1.27 10:58: effluent free analyzer- 1.17 11:06: influent free grab- 2.70 11:06: influent free analyzer- 2.73 11:25: treated free grab- 0.08 treated free analyzer- 0.10 11:25: treated total grab- 2.60 treated total analyzer- 2.54 11:25: Mono- 2.17 FA- 0.02 TA- 0.45 11:42: influent free grab- 2.58 11:42: influent free analyzer- 2.65 11:42: effluent free grab- 2.20 11:42: effluent free analyzer- 2.26 Verified all analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 back in service- Auto Duty 1. Informed Central and ROC operators | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | repair [maintenance_action]; scada [control_system] | 0.00029628 | 0 | 0
2026-02 | 2026-02-20 | Aurora Well 5 | CENTRAL | Onsite for station check: Changed CL2 cylinders: 50/0 kg to 50/68 kg * Replaced influent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034644 | 0 | 0
2026-02 | 2026-02-13 | Aurora Well 5 | CENTRAL | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004871 | 0 | 0
2026-02 | 2026-02-10 | Aurora Well 5 | CENTRAL | -Responded influent free LoLo - upon arrival, influent free analyzer reading=0.32mg/L - performed grab test influent free=0.39mg/L - checked treads - chlorinator 2 was running in the last cycle - checked chlorinator 2 - not dosing - put chlorinator 1 in duty 1 and disabled duty rotation - locked out chlorine booster 2 - backflushed contact tank until influent free=0.93mg/L - restarted well 5 in auto - well 5 was running normally for 10 mins | FLAG | stage2_low_confidence | 0.11191 | ML: above threshold (no LLM available) — 0.112 | oos [equipment_failure] | 0.11191 | 0 | 0
2026-02 | 2026-02-11 | Aurora Well 5 | CENTRAL | On-site for station check and sampling. W11589385 and W11476274. Chlorinator 2 remains locked out. Silicate pump 1 is OOS after hi turbidity lock out over night. Silicate pump 2 ran this morning with no issues. 12:00 Remotly placed well 5 in manual on. 12:23 running at 45.3 l/s. 12:31 collected raw samples. Verified chlorine analyzers (mg/l). 12:35. Influent free chlorine grab: 2.66 Analyzer: 2.67. 12:38 Effluent free chlorine grab. 2.46. Analyzer: 2.36 12:38. Treated free chlorine grab: 0.07 CL17: 0.12. 12:38. Treated total chlorine grab: 2.82 CL17: 2.88. Collected treated sample. Will investigate silicate pump 1 more tomorrow and leave OOS for now. Entered data into process sheets. No other issues found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | Aurora Well 5 | CENTRAL | Onsite for CL2 cylinder change: 0/20 kg to 68/20 kg * | FLAG | stage2_low_confidence | 0.0074402 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074402 | 0 | 0
2026-02 | 2026-02-13 | Aurora Well 5 | CENTRAL | Onsite to respond to lolo influent causing station lockout- informed by ROC: Upon arrival, took grab to verify influent free analyzer: Grab (14:44): 1.20 Analyzer (14:44): 1.27 Based on influent scada trending, appears that regulator didn?t drop down quick enough during CL2 cylinder switch over, causing influent residual to drop 14:47- ack/reset all outstanding alarms- well 5 started back up in auto duty 1. Informed ROC, will continue to monitor station via scada Station/equipment- Ok | FLAG | stage2_low_confidence | 0.013824 | ML: above threshold (no LLM available) — 0.014 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.013824 | 0 | 0
2026-02 | 2026-02-03 | Aurora Well 5 | CENTRAL | On-site to collect raw water bacti sample. Ran well 5 to waste. All chemical pumps off. Isolated well from distribution system CT not achieved alarm came in due to flow meters calculation, not applicable After sample collected return system back to normal while keeping well off in local | FLAG | stage2_low_confidence | 0.028691 | ML: above threshold (no LLM available) — 0.029 | sample collected [regulatory]; alarm [control_system] | 0.028691 | 0 | 0
2026-02 | 2026-02-06 | Aurora Well 5 | CENTRAL | Onsite for station check: Verified analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 in local/off- waiting for passing raw sample results prior to putting well back in service * | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059338 | 0 | 0
2026-02 | 2026-02-09 | Aurora Well 5 | CENTRAL | Onsite for station check: Verified analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains in local/off * | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042822 | 0 | 0
2026-02 | 2026-02-24 | Aurora Well 6 | CENTRAL | -Performed station check | FLAG | stage2_low_confidence | 0.012231 | ML: above threshold (no LLM available) — 0.012 |  | 0.012231 | 0 | 0
2026-02 | 2026-02-20 | Aurora Well 6 | CENTRAL | On site to complete PMs. Site offline. Completed JHSC inspection. | FLAG | stage2_low_confidence | 0.013964 | ML: above threshold (no LLM available) — 0.014 |  | 0.013964 | 0 | 0
2026-02 | 2026-02-18 | Aurora Well 6 | CENTRAL | Onsite for station check: Station offline * Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070744 | 0 | 0
2026-02 | 2026-02-03 | Aurora Well 6 | CENTRAL | Onsite for station check: Station offline * Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070744 | 0 | 0
2026-02 | 2026-02-09 | Aurora Well 6 | CENTRAL | Onsite for station check: Station offline * Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070744 | 0 | 0
2026-02 | 2026-02-26 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | -Collected in-house water quality sample | FLAG | stage2_low_confidence | 0.013201 | ML: above threshold (no LLM available) — 0.013 |  | 0.013201 | 0 | 0
2026-02 | 2026-02-24 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | -Performed station check at Raw Building | FLAG | stage2_low_confidence | 0.013205 | ML: above threshold (no LLM available) — 0.013 |  | 0.013205 | 0 | 0
2026-02 | 2026-02-20 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Under the direction of Joseph Demarco, Worked along side Network Analyst Aaron Magsakay, to replaced a Network switch to Cisco IE3300 inside a Network panel at AUW14 Treatment Building and Raw water building. Provided 24 VDC power to new switch. Informed the ROC regarding possible comm fail alarm. Well were Manual off. There is a trend gap on SCADA between 9:16 AM to 9:47 AM due to this work. Some of the trend data will be back filled by PAC backup file After the replacement, checked all the ports and reset the comm alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; alarms [control_system]; backup [infrastructure] | scada [control_system]; alarm [control_system]; alarms [control_system]; backup [infrastructure] |  | 1 | 0
2026-02 | 2026-02-25 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | On site to take silicate for MTW1/2 and MTW3. No issues on site put everything back to normal. | FLAG | stage2_low_confidence | 0.010039 | ML: above threshold (no LLM available) — 0.01 |  | 0.010039 | 0 | 0
2026-02 | 2026-02-26 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for CL2 cylinder change: 60/0 kg to 60/68 kg * | FLAG | stage2_low_confidence | 0.0074402 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074402 | 0 | 0
2026-02 | 2026-02-25 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for raw station check/collect raw samples- WO# W11620710: Quarterly raw ph samples: Well #1 raw ph- 8.09 Well #2 raw ph- 8.06 Well #3 raw ph- 8.05 Well #4 raw ph- 8.05 Building flood alarm received- noticed float tipped underneath grading. Sump doesn?t appear to be pumping- will create work order * Onsite for treated station check/collect sample- WO# W11620710: Sample results (10:30): Free- 0.07, Total- 2.90 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Work order created to install safety guard for well 4 motor shaft * Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; work order created [maintenance_action] | 0.0049908 | 0 | 0
2026-02 | 2026-02-02 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for station check: Received ammonia skid delivery * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039389 | 0 | 0
2026-02 | 2026-02-23 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | On-site for station check. Wells 2 and 3 running at 102.9 l/s. Topped up silicate day tanks. topped up ammonia tank 1. Verified chlorine analyzer (mg/L): 13:50 Influent free grab: 2.58. Analzyer: 2.63. 14:11 Effluent free grab: 2.64. Analyzer: 2.52. 13:20. Treated free grab: 0.00. Analyzer: 0.12. 13:20. Treated total grab: 3.19. Analyzer: 2.96. No new issues found on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049469 | 0 | 0
2026-02 | 2026-02-02 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Look at check valve passing | FLAG | stage2_low_confidence | 0.012523 | ML: above threshold (no LLM available) — 0.013 |  | 0.012523 | 0 | 0
2026-02 | 2026-02-13 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for raw station check/complete assigned work orders: Rotork actuator inspections Pump and motor inspections Station/equipment- Ok | FLAG | stage2_low_confidence | 0.013757 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action] | 0.013757 | 0 | 0
2026-02 | 2026-02-18 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite to complete assigned work orders- informed ROC: CL17 analyzer maintenance Turbidimeter maintenance CL2 leak test Generator test run: Start time:12:10 Stop time: 13:28 Start hours: 91.15 Stop hours: 92.50 Start fuel: 6,850 L Stop fuel: 7,030 L Pre test inspection completed- no abnormalities Generator operating stats (under load- P2/P3): 1800 rpm 600 Volts 60 hertz Oil pressure 78 psi Oil temp 187 F Coolant temp 177 F Fuel pressure 102 psi No abnormalities during generator test run- placed generator back into auto once test run completed Changed CL2 cylinders: 0/60 kg to 68/60 kg (Donald M onsite to assist) * Station back in auto Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; leak [infrastructure] | 0.0010086 | 0 | 0
2026-02 | 2026-02-20 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Received CL2 cylinders: 24 received, 24 returned Replaced influent free CL17 reagents Replaced treated total CL17 reagents Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/completed WO: Air release valve inspection Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0018728 | 0 | 0
2026-02 | 2026-02-17 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check/collect sample- WO# W11606256: Sample results (11:30): Free- 0.10, Total- 3.10 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/collect samples- WO# W11606256: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032094 | 0 | 0
2026-02 | 2026-02-13 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050598 | 0 | 0
2026-02 | 2026-02-05 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite to complete assigned work orders- informed ROC: H/S inspection Chlorine system inspection Silicate system inspection Ammonia system inspection Adjusted silicate p1 max flow from 680 to 760 mL/min Adjusted silicate p2 max flow from 740 to 800 mL/min Adjusted ammonia p1 max flow from 350 to 360 mL/min Adjusted ammonia p2 max flow from 350 to 380 mL/min Performed station housekeeping Completed on-call SCADA review Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; scada [control_system] | 0.0063207 | 0 | 0
2026-02 | 2026-02-11 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | On-site for station check and sampling. Micro sampling - W11589385. 09:16 Wells 1 and 4 running with a combined flow of 100 l/s. Collected well 1 and 4 raw samples. 09:45 rotated to running wells 2 and 3. 09:55 collected well 2 and 3 raw samples. Topped up well 3 oil reservoir from 1/4 to full. Topped up silicate day tanks. Verified chlorine analyzer (mg/L): 10:16 Influent free grab: 2.78/2.78/2.78. Analzyer: 2.68. Adjusted to match grab average. Changed right chlorine cylinder bank with Joe Williams. 10:50 Effluent free grab: 2.62/2.67/2.68. Analyzer: 2.47. Adjusted to match grab average. 11:01. Treated free grab: 0.09. Analyzer: 0.12. 11:01. Treated total grab: 3.08. Analyzer: 3.03. Collected treated sample. Changed treated free analyzer reagent. recored station data into process sheets. No new issues found on site. | FLAG | stage2_low_confidence | 0.025608 | ML: above threshold (no LLM available) — 0.026 |  | 0.025608 | 0 | 0
2026-02 | 2026-02-06 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030966 | 0 | 0
2026-02 | 2026-02-03 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for CL2 cylinder change: 0/49 kg to 68/49 kg * | FLAG | stage2_low_confidence | 0.0074402 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074402 | 0 | 0
2026-02 | 2026-02-03 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite to receive silicate delivery: 3,530L / 3,425L to 11,534L / 11,450L | FLAG | stage2_low_confidence | 0.008109 | ML: above threshold (no LLM available) — 0.008 |  | 0.008109 | 0 | 0
2026-02 | 2026-02-04 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for station check/collect samples- WO# W11569241: Sample results (09:10): Free- 0.07, Total- 2.84 * Replaced effluent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/collect samples: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0024014 | 0 | 0
2026-02 | 2026-02-05 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Well 3 motor service | FLAG | stage2_low_confidence | 0.0092499 | ML: above threshold (no LLM available) — 0.009 |  | 0.0092499 | 0 | 0
2026-02 | 2026-02-09 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Adjusted ammonia p1 max flow from 360 to 350 Adjusted ammonia p2 max flow from 380 to 350 Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0027251 | 0 | 0
2026-02 | 2026-02-26 | Bayview Pumping Station | EAST | Under Direction of OIC (Dan Zhou) On site for; - Station checks @ 13:52 switched pump duty, pump 3 duty 1 to duty 2, pump 4 duty 2 to duty 1 Grabs @ 14:02 hrs. FCl: 0.05 mg/L TCl: 1.56 mg/L Analyzer Free Chlorine: FCl: 0.04 mg/L Analyzer Total Chlorine: TCl: 1.53 mg/L Pumps 1 and 4 active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-23 | Bayview Pumping Station | EAST | Under Direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 10:21 hrs. FCl: 0.06 mg/L TCl: 1.54 mg/L Analyzer Free Chlorine: FCl: 0.04 mg/L Analyzer Total Chlorine: TCl: 1.57 mg/L Pumps 1 and 3 not active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.0010317 | 0 | 0
2026-02 | 2026-02-02 | Bayview Pumping Station | EAST | Under Direction of OIC (Dan Zhou) On site for; - Station checks @ 12:08 hrs. Let city of Toronto employee (Mohammed) in station to take a picture of the totalizer. Grabs @ 11:12 hrs. FCl: 0.04 mg/L TCl: 1.43 mg/L Analyzer Free Chlorine 0.06 mg/L Analyzer Total Chlorine: 1.44 mg/L Duty Inactive Changed pump duty from pumps 1 and 4 to 1 and 3. Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-20 | Bayview Pumping Station | EAST | Under Direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 13:20 hrs. FCl: 0.07 mg/L TCl: 1.50 mg/L Analyzer Free Chlorine: FCl: 0.04 mg/L Analyzer Total Chlorine: TCl: 1.44 mg/L @ 13:12 hrs. manually stopped pump 4 to switch duty to pump 3 Duty active @13:24 returned pumps 1 and 3 to auto Pumps 1 and 3 active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-13 | Bayview Pumping Station | EAST | Under Direction of OIC Joe Mazza On site for; - Station checks Grabs @ 13:56 hrs. FCl: 0.04 mg/L TCl: 1.47 mg/L Analyzer Free Chlorine 0.08 mg/L Analyzer Total Chlorine: 1.47 mg/L @ 10:56 hrs. manually stopped pump 3 to switch duty to pump 4 Duty active @11:06 returned pumps 3 and 4 to auto Pumps 1 and 4 active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-18 | Bayview Pumping Station | EAST | Changed the diesel fuel tank high level alarm from 150 to 155 cm. Current level is 153/153 cm or 4073/4087L. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0046895 | 0 | 0
2026-02 | 2026-02-18 | Bayview Pumping Station | EAST | -Received 7000L diesel fuel | FLAG | stage2_low_confidence | 0.0094904 | ML: above threshold (no LLM available) — 0.009 |  | 0.0094904 | 0 | 0
2026-02 | 2026-02-16 | Bayview Pumping Station | EAST | -The power at Bayview Pumping station very unstable and blipped a couple of times tonight - informed Alectra and ran the station under diesel generator - Diesel hours=126.2 Fuel=2024+2074L | FLAG | stage2_low_confidence | 0.016821 | ML: above threshold (no LLM available) — 0.017 |  | 0.016821 | 0 | 0
2026-02 | 2026-02-17 | Bayview Pumping Station | EAST | Generator was running upon arrival. 11:23 placed generator from test mode to auto. Utility power is available. Switched back to utility power with no issues. Pump duty is not active and controlling reservoir is at 81%. Informed ROC. Changed fuel tank low level alarm from 50 to 70 cm. Completed following work orders while on site: Station check JHSC inspection Flood alarm test Ventilation system inspection Dehumidifier cleaning/inspection Sump pump maintenance Chlorine analyzer maintenance Air compressor system maintenance 12:25 grab chlorine analyzer reading, FCL = 0.03 mg/l, TCL = 1.60 mg/l. Chlorine analzyer reading, FCL = 0.09 mg/l, TCL = 1.61 mg/l. 12:51 standardized analyzer reading after maintenance. Monthly generator test is considered to be completed. It was running overnight. Performed post run checks, no issues. Generator stop hour: 138.8 hrs. Fuel level: 772/824 L Diesel fuel order was placed and it is coming in the next few hours. 13:25 Activated duty. P1 and P4 are in duty 1. Pump 2 is OOS for rebuild. Station is back to normal operation. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] | sso [critical]; flood [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-06 | Bayview Pumping Station | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ workbook Grabs @ 13:48 hrs. FCl: 0.06 mg/L TCl: 1.51 mg/L Analyzer: FCl: 0.06 mg/L TCl: 1.48 mg/L Equipment OOS: Pump2 (offsite for rebuild) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-26 | East Vaughan Teston Pumping Station | WEST | -on site to trouble shoot diesel system fault alarm -diesel tank high alarm still outstanding -transfer over more to 89% -alarm not clear -spoke with Dan B electrician - restarted panel - alarm did not clear - | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-09 | Bayview Pumping Station | EAST | Under Direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 13:56 hrs. FCl: 0.06 mg/L TCl: 1.61 mg/L Analyzer Free Chlorine 0.08 mg/L Analyzer Total Chlorine: 1.63 mg/L Duty active Pumps 1 and 3 active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-27 | East Vaughan Teston Pumping Station | WEST | -on site for station check -check trends: all ok -entered readings in PWQ: all ok -verified analyzer 10:00 -analyzer free: 0mg/l grab: 0.05mg/l - zero calibrate and set to 0.05mg/l -analyzer total: 1.93/l grab: 2.03mg/l - adjusted -reagents all ok -flushed sanitary pit -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057018 | 0 | 0
2026-02 | 2026-02-26 | East Vaughan Teston Pumping Station | WEST | -on site to receive 5000L of diesel and verify VNPS free reading -received 3500L - high alarm on tank came in at 85% - filled to 86% -driver silenced alarm -transfer fuel over to day tank until 87% - still unable to clear diesel fault alarm on SCADA -transfer pumps back to auto -diesel fault will be outstanding until bulk tank level drops -verified PD7 free reason 10:15 -analyzer free: 0.14mg/l grab: 0.06mg/l - adjusted | FLAG | stage2_low_confidence | 0.027181 | ML: above threshold (no LLM available) — 0.027 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.027181 | 0 | 0
2026-02 | 2026-02-23 | East Vaughan Teston Pumping Station | WEST | Onsite wife station check Checked residuals mg/l @1353 Total analyzer 2.14 grab 2.06 Free analyzer 0.01 grab 0.03 Reagents ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034402 | 0 | 0
2026-02 | 2026-02-25 | East Vaughan Teston Pumping Station | WEST | -on site to clean lower level -noticed analyzer free reading 0mg/l -took grab 13:00 -analyzer free: 0mg/l grab:0.04/mg/l adjusted -analyzer total: 2.14mg/l grab: 2.04mg/l - adjusted -reagents all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065117 | 0 | 0
2026-02 | 2026-02-02 | East Vaughan Teston Pumping Station | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 10:00 -analyzer free: 0.08mg/l grab: 0.08mg/l -analyzer total: 2.07mg/l grab: 2.03mg/l -reagents all ok -checked free reading on analyzer - flow and trending working correctly -equipment and heating all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062738 | 0 | 0
2026-02 | 2026-02-13 | East Vaughan Teston Pumping Station | WEST | -Responded LoLo pre-total and pre-combined - upon arrival, pre-total analyzer reading=0.14mg/L free=0.12mg/L - Performed grab test, total=1.62mg/L free=0.07mg/L - checked depolox analyzer - reagents, sample flow, grit are all OK - noticed a motor at the total analyzer stopped spinning - called in instrument technician on-call, Parth Patel - review trends - all good - chemical system in manual off | FLAG | stage2_low_confidence | 0.052849 | ML: above threshold (no LLM available) — 0.053 |  | 0.052849 | 0 | 0
2026-02 | 2026-02-11 | East Vaughan Teston Pumping Station | WEST | Informed ROC and operations. Onsite for annual maintenance/calibrations. Used calibration mode. Devices were done as below: WPS_SH1_AIT1 , WPS_SH1_AIT2. Took a multiple grab samples and adjusted analyzers accordingly. AL SH1_AIT1 A- 0.04 mg/l G- 0.04 mg/l AL SH1_AIT2 A- 2.01 mg/l G- 2.03 mg/l Put everything back in service, all the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.002835 | 0 | 0
2026-02 | 2026-02-14 | East Vaughan Teston Pumping Station | WEST | Informed ROC. Onsite to troubleshoot pre injection total and pre injection combined chlorine lo Lo reading issue. Put the device in calibration mode and turned off the power to the analyzer. Noticed the shaft came off loose. Installed new shaft. Turned on the power to the analyzer. Took a multiple grab samples and adjusted analyzer accordingly. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | FLAG | stage2_low_confidence | 0.033097 | ML: above threshold (no LLM available) — 0.033 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.033097 | 0 | 0
2026-02 | 2026-02-18 | East Vaughan Teston Pumping Station | WEST | - on site to receive diesel | FLAG | stage2_low_confidence | 0.011737 | ML: above threshold (no LLM available) — 0.012 |  | 0.011737 | 0 | 0
2026-02 | 2026-02-17 | East Vaughan Teston Pumping Station | WEST | -on site for station check -check trends: all ok -entered readings in PWQ: all ok -verified analyzer 10:55 -analyzer free: 0.01mg/l grab: 0.06mg/l - adjusted -analyzer total: 2.24mg/l grab: 2.28mg/l -reagents all ok -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053151 | 0 | 0
2026-02 | 2026-02-13 | East Vaughan Teston Pumping Station | WEST | -on site to for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer 08:00 -analyzer free: 0.02mg/l grab: 0.02mg/l -analyzer total: 2.02mg/l grab: 2.05mg/l -reagents all ok -flushed sanitary pit | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052512 | 0 | 0
2026-02 | 2026-02-14 | East Vaughan Teston Pumping Station | WEST | -Reviewed the trends during the repair work last night - The chlorine dosage was based on 20 mins average pre-combined, when put the chemical system back to service. The 20 mins average pre-combined was not updated yet which caused a chlorine overdosage - from 0132 to 0137 and 0150 to 0155 two events that combined residual were greater than 3.00mg/L, the highest combined chlorine was 3.62mg/L (total=3.71mg/L free=0.09mg/L) - during that period time, reservoir was filling@250L/s. The high residual water was pushed into the reservoir and mixed with other water - no user was affected - reviewed trends at PD7 pumping station - normal, combined chlorine around 2.00mg/L, highest analyzer reading total=2.23mg/L - not reportable | FLAG | stage2_low_confidence | 0.15083 | ML: above threshold (no LLM available) — 0.151 | repair [maintenance_action] | 0.15083 | 0 | 0
2026-02 | 2026-02-20 | East Vaughan Teston Pumping Station | WEST | - on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 11:45 -analyzer free: 0.03mg/l grab: 0.05mg/l -analyzer total: 2.16mg/l grab: 2.12mg/l -topped KI reagents -flushed sanitary pit -power blip at 12:14 - reset alarms - power source 1 not available - informed on - call electrician - ROC contacting Electra | FLAG | stage2_low_confidence | 0.010085 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010085 | 0 | 0
2026-02 | 2026-02-04 | East Vaughan Teston Pumping Station | WEST | On site to replace network switch with network analyst Aaron Magsakay. All pumps were in manual. Comm failure alarm was triggered due to this. Removed Old switch from VNPSCD PAC panel. Wired 24 VDC power to the new switch and plugged in the ports. Powered up new IE3300 layer 3 switch and checked the comms. Removed unused cat6 cables. Checked with ROC to make sure comms are back and trends are good. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; plugged [infrastructure] | failure [equipment_failure]; alarm [control_system]; plugged [infrastructure] |  | 1 | 0
2026-02 | 2026-02-19 | East Vaughan Teston Pumping Station | WEST | Vibration readings | FLAG | stage2_low_confidence | 0.021831 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021831 | 0 | 0
2026-02 | 2026-02-09 | East Vaughan Teston Pumping Station | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer 09:20 -analyzer free:0.04mg/l grab: 0.03mg/l -analyzer total: 2.06mg/l grab: 2.06mg/l -reagents all ok -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050474 | 0 | 0
2026-02 | 2026-02-05 | East Vaughan Teston Pumping Station | WEST | -on site to complete following work order -hoist inspection: all ok -analyzer verification/maintenance -analyzer verification 09:30 -analyzer free: 0.08mg/l grab: 0.06mg/l -analyzer total: 2.16mg/l grab: 2.14mg/l -reagents all ok/flushed sample lines/adjusted flow/checked motor/pressure/electrolyte - all ok -PD7/PD8 air valve flush: -semi annual diesel test run: power source on site at 10:45 -start time: 235.8 hrs -stop time: 237hrs -diesel level: 2024L 80%, 6290L 47.1% | FLAG | stage2_low_confidence | 0.01497 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action] | 0.01497 | 0 | 0
2026-02 | 2026-02-25 | Holland Landing East Elevated Tank | WEST | Onsite for annual calibrations Tower currently off-line Informed ROC Calibrated FIT and LIT Cleared associated alarms Informed ROC Checked building is armed Left site | FLAG | stage2_low_confidence | 0.013173 | ML: above threshold (no LLM available) — 0.013 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.013173 | 0 | 0
2026-02 | 2026-02-06 | East Vaughan Teston Pumping Station | WEST | -on site to complete PS station check -PD7 and PD8 duties not active -checked equipment -reviewed trends PD7 Pump Hours: #1 = 8137.4 #2 = 6708.9 #3 = 14650.6 #4 = 11617.1 PD8 Pump Hours: #1 = 17858.2 #2 = 18275.7 #3 = 21514.7 #4 = 21211.9 -analyzer reagents ok Verified analyzers: 08:57 - Analyzer readings: Free Chlorine = 0.10 mg/L Total Chlorine = 2.20 mg/L 08:57 - Grabs: Free Chlorine = 0.04/0.03/0.04 mg/L Total Chlorine = 2.04/2.09/2.06 mg/L 09:02 - adjusted free chlorine analyzer to 0.04 mg/L based on average of 3 grabs 09:06 - adjusted total chlorine analyzer to 2.06 mg/L based on average of 3 grabs -no other issues found -completed Sanitary Pit flush | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010807 | 0 | 0
2026-02 | 2026-02-03 | Holland Landing East Elevated Tank | WEST | On site for the following HLETPR, JHSC Health and Safety Inspection, Holland Landing East El HLETPR, Low Temperature Alarm, Test, Holland Landing East, ET (1M) HLETPR, Gasoline Portable Generator, Test, Holland Landing East, ET (1M) No issues on site | FLAG | stage2_low_confidence | 0.0076556 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076556 | 0 | 0
2026-02 | 2026-02-09 | Holland Landing East Elevated Tank | WEST | On site for station check Tower offline, no flow Visual inspection in and around station Verification of equipment and instrumentation. Cleared low temp alarm No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066262 | 0 | 0
2026-02 | 2026-02-27 | Holland Landing Sherwood Pumping Station | WEST | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Outstanding alarms: None Residual Chlorine 1300: FCL = 0.03 mg/l TCL = 1.33 mg/l No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0046768 | 0 | 0
2026-02 | 2026-02-20 | Holland Landing Sherwood Pumping Station | WEST | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine: FCL = 0.05 mg/l TCL = 1.38 mg/l No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0050995 | 0 | 0
2026-02 | 2026-02-13 | Holland Landing Sherwood Pumping Station | WEST | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine: FCL = 0.04 mg/l TCL = 2.08 mg/l No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0050995 | 0 | 0
2026-02 | 2026-02-17 | Holland Landing Sherwood Pumping Station | WEST | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine: FCL = 0.06 mg/l TCL = 1.88 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0070115 | 0 | 0
2026-02 | 2026-02-06 | Holland Landing Sherwood Pumping Station | WEST | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine: FCL = 0.05 mg/l TCL = 1.12 mg/l No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0050995 | 0 | 0
2026-02 | 2026-02-03 | Holland Landing Sherwood Pumping Station | WEST | -on site to perform following work order -diesel test -diesel start: 1430.5hr -diesel stop: 1431.6hr -diesel level: 667L -received hypo at HLETYS 173L - 570L -completed JHSC inspection: all ok -tested low temp: all ok -exercise suction valve: all ok -exercised discharge valve: all ok | FLAG | stage2_low_confidence | 0.0088632 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action] | 0.0088632 | 0 | 0
2026-02 | 2026-02-09 | Holland Landing Sherwood Pumping Station | WEST | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Time: 1122 hrs Residual Chlorine: FCL = 0.05 mg/l TCL = 2.48 mg/l No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0031897 | 0 | 0
2026-02 | 2026-02-25 | Holland Landing Well No. 1 | WEST | Onsite for station check and to collect weekly micro sample W11620194 Activated duty Checked residuals mg/l Influent free @0927 Free analyzer 2.92 grab 2.90 Total grab 3.62 Effluent free @0931 Free analyzer 2.68 grab 2.72 Total grab 3.20 Treated @0937 Total analyzer 3.25 grab 3.20 Free analyzer 0.15 grab 0.16 Sl1000 Mcl grab 2.88 F nh3 grab 0.10 T nh3 grab 0.67 Another total sl1000 grab @0952 Mcl grab 2.81 F nh3 0.09 T nh3 0.64 Increased ammonia p2 max flow from 105 to 115 ml/min Sl1000 grab @1010 Mcl grab 2.78 F nh3 0.07 T nh3 0.62 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00010334 | 0 | 0
2026-02 | 2026-02-23 | Holland Landing Well No. 1 | WEST | On-site for station check Reviewed scada and trends, duty active, ET at 65% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#2 opened @ 34% and dosing at 36 ppd Chlorine dose scada = 15.3 kg/d Chlorinator1 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 47% speed Dosing 49.05 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 115 mL/min Pump discharge pressure: 595 kpa Silicate : pump2 running in duty1 @ 32% Silicate dose = 35.70 mL/min Chlorine grabs: @ 1323 hrs Influent FCL FCL = 2.74mg/l Analyzer reading: FCL = 2.77 mg/l Effluent FCL @ 1340 hrs: FCL = 2.52 mg/l Analyzer: 2.60 mg/l Analyzer adjusted to 2.52 based on 2 repetitive grabs Treated grabs @ 1200 hrs FCL : 0.10 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.04 mg/l TCL : 3.09 mg/l SL1000: @ 1323 hrs with Ammonia pump2 FA = 0.07 mg/ TA = 0.59 mg/l Mono = 2.64 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.001525 | 0 | 0
2026-02 | 2026-02-23 | Holland Landing Well No. 1 | WEST | Restarted the Operator Interface Terminal due to Windows OS updates. The well was off and the Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.00973 | ML: above threshold (no LLM available) — 0.01 |  | 0.00973 | 0 | 0
2026-02 | 2026-02-24 | Holland Landing Well No. 1 | WEST | Onsite to complete the following WOs: - Flow control valve test - Washroom room light cleaning and supplies - Chlorine scrubber inspection - Chemical system inspection ~ ammonia - Chlorinator 2 vacuum gauge troubleshoot - Replace air / vacuum release valve - Relocate sample lines Notified ROC placed well 1 in manual off Notified ROC after completion No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004035 | 0 | 0
2026-02 | 2026-02-27 | Holland Landing Well No. 1 | WEST | On-site for station check Reviewed scada and trends, duty active, ET at 48% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 36 ppd Chlorine dose scada = 14.8 kg/d Chlorinator2 and BP2 in duty Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 44% speed Dosing 49.05 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 115 mL/min Pump discharge pressure: 600 kpa Silicate : pump2 running in duty1 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 0950 hrs Influent FCL FCL = 2.84mg/l Analyzer reading: FCL = 2.85 mg/l Effluent FCL @ 1036 hrs: FCL = 2.72 mg/l Analyzer: 2.71 mg/l Treated grabs @ 1200 hrs FCL : 0.12 mg/l Analyzer reading: FCL : 0.16 mg/l TCL : 3.30 mg/l TCL : 3.29 mg/l SL1000: @ 1033 hrs with Ammonia pump2 FA = 0.07 mg/ TA = 0.56 mg/l Mono = 2.49 mg/l Troubleshoot with ammonia pump1, adjusted Max flow from 100 down to 85 mL/min Ammonia pump1 running @ 61% at a dosage of 61.34 mL/min 1106 hrs: Ammonia pump1 SL1000 grab: FA = 0.05 mg/ TA = 0.60 mg/l Mono = 2.76 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.001182 | 0 | 0
2026-02 | 2026-02-25 | Holland Landing Well No. 1 | WEST | Changed cl2 cylinder with S. Baidy | FLAG | stage2_low_confidence | 0.0097886 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097886 | 0 | 0
2026-02 | 2026-02-02 | Holland Landing Well No. 1 | WEST | On-site for station check Reviewed scada and trends, duty active, ET at 70% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 34% and dosing at 38 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 155 psi (1,069 kpa) Ammonia: Pump1 in duty1 running at 43% speed Dosing 51.15 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1208 hrs Influent FCL FCL = 2.88mg/l Analyzer reading: FCL = 2.87 mg/l Effluent FCL @ 1210 hrs: FCL = 2.70 mg/l Analyzer: 2.72 mg/l Treated grabs @ 1216 hrs FCL : 0.09 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.38 mg/l TCL : 3.37 mg/l SL1000: @ 1200 hrs with Ammonia pump1 FA = 0.07 mg/l TA = 0.62 mg/l Mono = 2.78 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0020383 | 0 | 0
2026-02 | 2026-02-02 | Holland Landing Well No. 1 | WEST | On site to collect weekly bact samples from raw (11:00) and treated (11:05) sample taps (W11568853). Tested chlorine residuals via hach field kit. Free: 0.16 mg/L Total: 3.07 mg/L | FLAG | stage2_low_confidence | 0.010937 | ML: above threshold (no LLM available) — 0.011 |  | 0.010937 | 0 | 0
2026-02 | 2026-02-02 | Holland Landing Well No. 1 | WEST | Filled silicate tanks 176/167 L to 408/396 L | FLAG | stage2_low_confidence | 0.010268 | ML: above threshold (no LLM available) — 0.01 |  | 0.010268 | 0 | 0
2026-02 | 2026-02-20 | Holland Landing Well No. 1 | WEST | On-site for station check Reviewed scada and trends, duty active, ET at 66% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 36 ppd Chlorine dose scada = 14.8 kg/d Chlorinator2 and BP2 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 43% speed Dosing 49.40 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 115 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1150 hrs Influent FCL FCL = 2.72mg/l Analyzer reading: FCL = 2.74 mg/l Effluent FCL @ 1155 hrs: FCL = 2.64 mg/l Analyzer: 2.64 mg/l Treated grabs @ 1200 hrs FCL : 0.07 mg/l Analyzer reading: FCL : 0.16 mg/l TCL : 3.08 mg/l TCL : 3.10 mg/l SL1000: @ 1156 hrs with Ammonia pump2 FA = 0.01 mg/ TA = 0.53 mg/l Mono = 2.62 mg/l Adjusted max flow on ammonia pump2 from 100 to 115% FA = 0.02 mg/l TA = 0.52 mg/l Mono = 2.58 mg/l 1218 hrs: switched ammonia pumps duty, placed p1 in lead duty @ 100 mL/min (49% speed), pump1 was not dosing for some reasons, which caused treated FCL to spike to 1.7 mg/l. switched back to p2 and FCL came back down to normal levels. Placed p1 in manual off will return for further troubleshoot. Adjusted max flow on ammonia pump2 from 100 to 105% FA = 0.05 mg/l TA = 0.54 mg/l Mono = 2.65 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0019134 | 0 | 0
2026-02 | 2026-02-13 | Holland Landing Well No. 1 | WEST | On-site for station check Reviewed scada and trends, duty active, ET at 67% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 37 ppd Chlorine dose scada = 14,8 kg/d Chlorinator2 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 41% speed Dosing 49.53 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 100 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 0840 hrs Influent FCL FCL = 2.78mg/l Analyzer reading: FCL = 2.81 mg/l Made adjustment to influent FCL analyzer reading from 2.85 down to 2.76 based on average of 3 grabs Effluent FCL @ 0943hrs: FCL = 2.62 mg/l Analyzer: 2.66 mg/l Treated grabs @ 0948 hrs FCL : 0.08 mg/l Analyzer reading: FCL : 0.16 mg/l TCL : 3.32 mg/l TCL : 3.35 mg/l SL1000: @ 0948 hrs with Ammonia pump2 FA = 0.04 mg/l TA = 0.57 mg/l Mono = 2.67 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0026562 | 0 | 0
2026-02 | 2026-02-12 | Holland Landing Well No. 1 | WEST | -on site to install new pump head on ammonia pump #1 -installed new pump head and completed drawdown, pump max flow = 77.5 ml/min -adjusted scada max flow setpoint 120 to 85 ml/min -put pump #1 into duty 1 and collected ammonia grab: MCL = 2.55 mg/L TNH3 = 0.54 mg/L FNH3 = 0.03 mg/L -will continue to monitor | FLAG | stage2_low_confidence | 0.0084434 | ML: above threshold (no LLM available) — 0.008 | scada [control_system] | 0.0084434 | 0 | 0
2026-02 | 2026-02-18 | Holland Landing Well No. 1 | WEST | Onsite to top up silicate day tank from 225 to 419 L | FLAG | stage2_low_confidence | 0.010687 | ML: above threshold (no LLM available) — 0.011 |  | 0.010687 | 0 | 0
2026-02 | 2026-02-11 | Holland Landing Well No. 1 | WEST | On-site for station check Reviewed scada and trends, duty active, ET at 57% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 37 ppd Chlorine dose scada = 14,8 kg/d Chlorinator2 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump1 in duty1 running at 41% speed Dosing 48.80 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1104 hrs Influent FCL FCL = 2.76mg/l Analyzer reading: FCL = 2.85 mg/l Made adjustment to influent FCL analyzer reading from 2.85 down to 2.76 based on average of 3 grabs Effluent FCL @ 1114hrs: FCL = 2.58 mg/l Analyzer: 2.58 mg/l Treated grabs @ 1121 hrs FCL : 0.08 mg/l Analyzer reading: FCL : 0.15 mg/l TCL : 3.20 mg/l TCL : 3.22 mg/l SL1000: @ 1520 hrs with Ammonia pump1 FA = 0.03 mg/l TA = 0.50 mg/l Mono = 2.39 mg/l Increased ammonia pump2 max flow from 120 down to 100 mL/min SL1000: @ 1520 hrs with Ammonia pump1 FA = 0.02 mg/l TA = 0.51 mg/l Mono = 2.56 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0016004 | 0 | 0
2026-02 | 2026-02-17 | Holland Landing Well No. 1 | WEST | On-site for station check and collection of weekly bacT and operational samples Reviewed scada and trends, duty active, ET at 88% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#2 opened @ 33% and dosing at 36 ppd Chlorine dose scada = 14.8 kg/d Chlorinator1 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 37% speed Dosing 49.53 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 135 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1132 hrs Influent FCL FCL = 2.74mg/l Analyzer reading: FCL = 2.77 mg/l Effluent FCL @ 1139 hrs: FCL = 2.62 mg/l Analyzer: 2.65 mg/l Treated grabs @ 1152 hrs FCL: 0.09 mg/l Analyzer reading: FCL: 0.14 mg/l TCL: 3.04 mg/l TCL: 3.00 mg/l SL1000: @ 1200 hrs with Ammonia pump2 FA = 0.21 mg/l TA = 0.78 mg/l Mono = 2.86 mg/l Adjusted max flow on ammonia pump2 from 100 to 136% FA = 0.04 mg/l TA = 0.56 mg/l Mono = 2.72 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0011718 | 0 | 0
2026-02 | 2026-02-05 | Holland Landing Well No. 1 | WEST | Onsite for for completion of the following WOs HLW1, Chlorine Gas Detector, Test, Chlorine Analyzers cleaning and maintenance Turbidity Analyzer TU5300, Maintenance and Calibration, Chemical System Inspection - Chlorine , Cl2 Emergency Repair Kit Inspection, Flow Control Valve, Test, Chemical System Inspection - Silicate, rebuilt and installed a release valve Chemical System Inspection - Ammonia System Chlorine Scrubber, Notified ROC before starting WOs Activated duty and monitored station no issues Deactivated duty, notified ROC before leaving site | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; repair [maintenance_action] | emergency [critical]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-09 | Holland Landing Well No. 1 | WEST | On-site for station check Reviewed scada and trends, duty active, ET at 48% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 37 ppd Chlorine dose scada = 14,8 kg/d Chlorinator1 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump1 in duty1 running at 39% speed Dosing 46.86 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 42% Silicate dose = 35.37 mL/min Chlorine grabs: @ 1514 hrs Influent FCL FCL = 2.88mg/l Analyzer reading: FCL = 2.86 mg/l Effluent FCL @ 1518hrs: FCL = 2.48 mg/l Analyzer: 2.48 mg/l Treated grabs @ 1529 hrs FCL : 0.10 mg/l Analyzer reading: FCL : 0.17 mg/l TCL : 3.16 mg/l TCL : 3.20 mg/l SL1000: @ 1520 hrs with Ammonia pump1 FA = 0.04 mg/l TA = 0.54 mg/l Mono = 2.47 mg/ | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0020097 | 0 | 0
2026-02 | 2026-02-06 | Holland Landing Well No. 1 | WEST | On-site for station check Reviewed scada and trends, duty active, ET at 48% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 37 ppd Chlorine dose scada = 14,3 kg/d Chlorinator1 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump1 in duty1 running at 39% speed Dosing 46.86 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 42% Silicate dose = 35.37 mL/min Chlorine grabs: @ 1123 hrs Influent FCL FCL = 2.92mg/l Analyzer: FCL = 2.90 mg/l Effluent FCL @ 1126hrs: FCL = 2.48 mg/l Analyzer: 2.50 mg/l Treated grabs @ 1133 hrs FCL : 0.08 mg/l Analyzer reading: FCL : 0.13 mg/l TCL : 3.04 mg/l TCL : 3.09 mg/l SL1000: @ 1133 hrs with Ammonia pump1 FA = 0.05 mg/l TA = 0.54 mg/l Mono = 2.49 mg/l changed tubing element on silicate pump2, primmed and placed back in service, in duty1 Completed JHSC health and safety inspection | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0014202 | 0 | 0
2026-02 | 2026-02-27 | Holland Landing Well No. 2 | WEST | Reviewed scada and trends, duty active, ET at 65% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1205 hrs Influent FCL FCL = 2.62 mg/l Analyzer reading: FCL = 2.64 mg/l Effluent FCL @ 1220 hrs: FCL = 2.52 mg/l Analyzer: 2.51 mg/l Treated grabs @ 1228 hrs FCL : 0.14 mg/l Analyzer reading: FCL : 0.13 mg/l TCL : 3.10 mg/l TCL : 3.15 mg/l SL1000: @ 0926 hrs with Ammonia pump2 FA = 0.07 mg/l TA = 0.59 mg/l Mono = 2.57 mg/l Adjusted ammonia p2 max flow from 110 to 125 mL/min based on FA grab Chemical pumps: Chlorine: chlorinator#2 opened @ 68% and dosing at 68 ppd Chlorine dose scada = 30.7 kg/d Dosage factor = 155 % Chlorinator1 and BP1 in duty2 Chlorine booster2 pressure: 1,150 kpa Ammonia: Pump2 in duty1 running at 56% speed Dosing 70.09 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 125 mL/min Pump2 discharge pressure: 700 kpa Silicate : pump2 running in duty2 @ 36% Silicate dose = 42:93 mL/min Pump1 in duty2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0018581 | 0 | 0
2026-02 | 2026-02-23 | Holland Landing Well No. 2 | WEST | Reviewed scada and trends, duty active, ET at 73% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1430 hrs Influent FCL FCL = 2.60mg/l Analyzer reading: FCL = 2.65 mg/l Effluent FCL @ 1436 hrs: FCL = 2.50 mg/l Analyzer: 2.53 mg/l Treated grabs @ 1449 hrs FCL : 0.16 mg/l Analyzer reading: FCL : 0.15 mg/l TCL : 3.10 mg/l TCL : 3.06 mg/l SL1000: @ 1449 hrs with Ammonia pump2 FA = 0.02 mg/l TA = 0.50 mg/l Mono = 2.45 mg/l Adjusted ammonia p2 max flow from 113 to 118 mL/min based on FA grab 1015 hrs: Did grab of FA after adjustments: 0.02 mg/l Chemical pumps: Chlorine: chlorinator#2 opened @ 67% and dosing at 65 ppd Chlorine dose scada = 30.5 kg/d Dosage factor = 152 % Chlorinator1 and BP1 in duty1 Chlorine booster2 pressure: 1,150 kpa Ammonia: Pump2 in duty1 running at 59% speed Dosing 70.09 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 118 mL/min Pump2 discharge pressure: 700 kpa Silicate : pump2 running in duty2 @ 36% Silicate dose = 42:93 mL/min Pump1 in duty2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0019707 | 0 | 0
2026-02 | 2026-02-25 | Holland Landing Well No. 2 | WEST | Onsite for station check and to collect weekly micro sample W11620194 Duty running Checked residuals mg/l Influent @1104 Free analyzer 2.70 grab 2.80 Total grab 3.64 Effluent @1109 Free analyzer 2.54 grab 2.46 Total grab 2.80 Treated @1117 Total analyzer 3.06 grab 3.12 Free analyzer 0.14 grab 0.19 Sl 1000 Mcl grab 2.41 F nh3 grab 0.00 T nh3 grab 0.47 Sharon feed @1122 Total grab 2.13 Decreased ammonia p2 max flow from 118 to 100 ml/min Sl1000 grab @1240 Mcl 2.67 F nh3 0.07 T nh3 0.60 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00013643 | 0 | 0
2026-02 | 2026-02-02 | Holland Landing Well No. 2 | WEST | Filled silicate tank 318 L to 531 L | FLAG | stage2_low_confidence | 0.0099012 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099012 | 0 | 0
2026-02 | 2026-02-23 | Holland Landing Well No. 2 | WEST | Restarted the Operator Interface Terminal due to Windows OS updates. The well was off and the Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.00973 | ML: above threshold (no LLM available) — 0.01 |  | 0.00973 | 0 | 0
2026-02 | 2026-02-02 | Holland Landing Well No. 2 | WEST | -on site to complete station check -well running in auto -cl2 booster pump # 2 running at 170 psi -chlorinator # 2 67% open dosing 65 ppd, vac = -270 mbar, DF = 153% -silicate pump # 1 running at 36%, 21.9 rpm -ammonia pump # 1 running at 71%, 80 psi, 128 strokes/min -checked equipment -reviewed trends -CL17 reagents ok 13:12 - Sharon Valve grab: TCL = 2.37 mg/L MCL = 1.91 mg/L TNH3 = 0.47 mg/L FNH3 = 0.09 mg/L -verified chlorine analyzers: 13:14 - Influent FCL Analyzer = 2.38 mg/L 13:14 - Influent grab: Free chlorine = 2.58 mg/L -unable to adjust influent analyzer due to issues with keyboard, work order issued for instrumentation 13:19 - Effluent FCL Analyzer = 2.42 mg/L 13:19 - Effluent grab: Free chlorine = 2.36 mg/L 13:22 - Treated water analyzers: FCL = 0.17 mg/L TCL = 2.93 mg/L 13:22 - Treated water grabs: FCL = 0.19 mg/L TCL = 2.90 mg/L MCL = 2.45 mg/L TNH3 = 0.61 mg/L FNH3 = 0.13 mg/L -increased ammonia pump #1 max flow 95 to 115 ml/min 14:15 - collected treated water grab: MCL = 2.48 mg/L TNH3 = 0.57 mg/L FNH3 = 0.08 mg/L -recorded readings in PWQ sheet -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; work order [maintenance_action] | 0.0020538 | 0 | 0
2026-02 | 2026-02-18 | Holland Landing Well No. 2 | WEST | Onsite to top up silicate day tank from 273 L to 567 L | FLAG | stage2_low_confidence | 0.010811 | ML: above threshold (no LLM available) — 0.011 |  | 0.010811 | 0 | 0
2026-02 | 2026-02-21 | Holland Landing Well No. 2 | WEST | -on site to respond to NTU fault -no flow on unit - confirm flow - sensor not working -disabled and confirmed flow -adjusted heater in chlorine room -restarted well | FLAG | stage2_low_confidence | 0.016932 | ML: above threshold (no LLM available) — 0.017 | fault [equipment_failure]; not working [equipment_failure] | 0.016932 | 0 | 0
2026-02 | 2026-02-13 | Holland Landing Well No. 2 | WEST | In to complete station check. Enter data into PWQ. Analyzer reagent levels good. Span Calibrated Treated TCL cl17 analyzer from 3.00 to 2.90mg/L based on grabs. Disable auto duty All Stop rotate on Ammonia pumps; to test new pump head on Ammonia P1. Dosing appears to be working well. | FLAG | stage2_low_confidence | 0.012465 | ML: above threshold (no LLM available) — 0.012 |  | 0.012465 | 0 | 0
2026-02 | 2026-02-17 | Holland Landing Well No. 2 | WEST | Onsite for station check and collection of weekly of bacT and operational samples Reviewed SCADA and trends, duty active, ET at 86% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1036 hrs Influent FCL FCL = 2.60mg/l Analyzer reading: FCL = 2.63 mg/l Effluent FCL @ 1024 hrs: FCL = 2.70 mg/l Analyzer: 2.68 mg/l Treated grabs @ 1000 hrs FCL: 0.12 mg/l Analyzer reading: FCL: 0.14 mg/l TCL : 3.04 mg/l TCL: 3.00mg/l SL1000: @ 1000 hrs with Ammonia pump2 FA = 0.07 mg/l TA = 0.60 mg/l Mono = 2.67 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 68% and dosing at 69 ppd Chlorine dose scada = 30.9 kg/d Dosage factor = 155 % Chlorinator2 and BP2 in duty2 Chlorine booster1 pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 65% speed Dosing 73.99 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 1139 mL/min Pump discharge pressure: 525 kpa Silicate : pump2 running in duty2 @ 36% Silicate dose = 43:36 mL/min Pump1 in duty2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.001763 | 0 | 0
2026-02 | 2026-02-10 | Holland Landing Well No. 2 | WEST | Onsite to complete the following WOs: JHSC Health and Safety Inspection, Chlorine Gas leak Detector alarm test Chlorine Analyzer Maintenance Chemical System Inspection - Chlorine, Pressure Relief Valve, Maintenance, Chlorine Scrubber, Check, Holland Landing, Low/High Temperature Alarm, Test, Turbidimeter, Maintenance Chemical System Inspection - Silicate, Chemical System Inspection - Ammonia, Pressure Relief Valve, Maintenance, Notified ROC placed well 2 pump in manual off Completed WOs cleared alarms and reset Verified chlorine analyzer as follows Influent FCL @1216 hrs: FCL = 2.98mg/l Analyzer reading: FCL = 2.95 mg/l Effluent FCL @ 1220hrs: FCL = 2.44 mg/l Analyzer: 2.48 mg/l Treated grabs @ 1229 hrs FCL : 0.27 mg/l Analyzer reading: FCL : 0.29 mg/l TCL : 3.10 mg/l TCL : 3.07 mg/l SL1000 FA = 0.02 mg/l TA = 0.47 mg/l Mono = 2.25 mg/l Replaced new liquid head on ammonia pump1 Ammonia pumps require further adjustment, placed well 2 pump in manual off due to time constraints will return tomorrow continue troubleshooting. Notified ROC before leaving site | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | gas leak [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-20 | Holland Landing Well No. 2 | WEST | Reviewed scada and trends, duty active, ET at 57% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 9:55 hrs Influent FCL FCL = 2.54mg/l Analyzer reading: FCL = 2.57 mg/l Effluent FCL @ 9:51 hrs: FCL = 2.66 mg/l Analyzer: 2.64 mg/l Treated grabs @ 0926 hrs FCL : 0.14 mg/l Analyzer reading: FCL : 0.15 mg/l TCL : 3.28 mg/l TCL : 3.29mg/l SL1000: @ 0926 hrs with Ammonia pump2 FA = 0.09 mg/l TA = 0.62 mg/l Mono = 2.69 mg/l Adjusted ammonia p2 max flow from 113 to 120 mL/min based on FA grab 1015 hrs: Did grab of FA after adjustments: 0.04 mg/l Chemical pumps: Chlorine: chlorinator#2 opened @ 67% and dosing at 69 ppd Chlorine dose scada = 30.5 kg/d Dosage factor = 154 % Chlorinator1 and BP2 in duty1 Chlorine booster2 pressure: 1,150 kpa Ammonia: Pump2 in duty1 running at 58% speed Dosing 73.99 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 120 mL/min Pump2 discharge pressure: 700 kpa Silicate : pump2 running in duty2 @ 36% Silicate dose = 43:11 mL/min Pump1 in duty2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.003272 | 0 | 0
2026-02 | 2026-02-19 | Holland Landing Well No. 2 | WEST | On site to complete chlorine overhaul annual. Replaced regulators, ejectors, PE tubing and parker fittings. Replaced 3 chemline ball valves that had not been replaced in 2024 (interconnects). Vacuum tested without issue, backflushed small volume to clear highly chlorinated water and reprime chlorine BP discharge lines. No issues. | FLAG | stage2_low_confidence | 0.017894 | ML: above threshold (no LLM available) — 0.018 |  | 0.017894 | 0 | 0
2026-02 | 2026-02-19 | Holland Landing Well No. 2 | WEST | Onsite to complete the following WOs: - Changed and replaced chlorine regulators - Changed and replaced chlorine injectors - Changed and replaced chlorine lines and fittings tested chlorine system after maintenance, tested chlorine regulators for vacuum, both regulators responded normally Did visual inspection on chlorine system, no issues prepared new batch of ammonia for tank2 1400hrs, backflashed system and started well 2 in manual 1435 hrs; Did grab on influent FCL analyzer when analyzer was reading 2.44 mg/l = grab was 2.40 mg/l SL1000 reading: FA = 0.06 TA = 0.47 Mono = 2.08 Treated = 2.78 FCL = 0.16 mg/l 1520 hrs shut down well and returned to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039528 | 0 | 0
2026-02 | 2026-02-11 | Holland Landing Well No. 2 | WEST | Onsite for station check and collection of weekly bacT samples Reviewed scada and trends, duty active, ET at 53% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1342 hrs Influent FCL FCL = 2.76mg/l Analyzer reading: FCL = 2.74 mg/l Effluent FCL @ 1344 hrs: FCL = 2.50 mg/l Analyzer: 2.54 mg/l Treated grabs @ 1352 hrs FCL : 0.18 mg/l Analyzer reading: FCL : 0.21 mg/l TCL : 3.10 mg/l TCL : 3.05mg/l SL1000: @ 1352 hrs with Ammonia pump2 FA = 0.02 mg/l TA = 0.53 mg/l Mono = 2.54 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 68% and dosing at 69 ppd Chlorine dose scada = 30.9 kg/d Dosage factor = 156 % Chlorinator2 and BP2 in duty2 Chlorine booster1 pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 90% speed Dosing 76.78 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 1139 mL/min Pump discharge pressure: 525 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 43.11 mL/min Pump2 in duty2 troubleshoot with ammonia pump2 with new liquid head run through cal column and adjusted accordingly placed ammonia pump1 in duty1 and started duty adjusted max flow to 85 mL/min, verified pump1 dosage by SL1000 grabs recorded above. no issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0020265 | 0 | 0
2026-02 | 2026-02-05 | Holland Landing Well No. 2 | WEST | -on site to complete station check and to collect samples -sample work order # W11639094 -cl2 booster pump # 1 running at 195 psi -chlorinator # 1 66% open dosing 67 ppd, vac = -660 mbar, DF = 151% -silicate pump # 2 running at 36%, 21.8 rpm -ammonia pump # 2 running at 57%, 80 psi, 100 strokes / min -checked equipment -reviewed trends -CL17 reagents ok 09:17 - Sharon Valve grab: TCL = 1.58 mg/L MCL = 0.67 mg/L TNH3 = 0.32 mg/L FNH3 = 0.19 mg/L -verified chlorine analyzers: 09:18 - Influent FCL Analyzer = 2.83 mg/L 09:18 - Influent grab: Free chlorine = 2.88 mg/L 09:23 - Effluent FCL Analyzer = 2.42 mg/L 09:23 - Effluent grab: Free chlorine = 2.42 mg/L 09:28 - Treated water analyzers: FCL = 0.19 mg/L TCL = 2.97 mg/L 09:28 - Treated water grabs: FCL = 0.16 mg/L TCL = 3.02 mg/L MCL = 2.52 mg/L TNH3 = 0.56 mg/L FNH3 = 0.06 mg/L 09:33 - collected weekly treated water micro sample 09:34 - collected weekly raw water micro sample -recorded readings in PWQ sheet -no issues found -influent analyzer repaired, enabled auto dosing mode and adjusted chlorine residual setpoint from 3.30 mg/L to 2.80 mg/L -returned well to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] | 0.0025936 | 0 | 0
2026-02 | 2026-02-04 | Holland Landing Well No. 2 | WEST | Attending site to check Influent Free chlorine analyzer (W11622780). Push button switches were found to be not functioning. Replaced switches and verified reading. Reading as found = 2.11mg/L, reading as left = 2.28 mg/L Free chlorine based on average of three grabs. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.038296 | ML: above threshold (no LLM available) — 0.038 |  | 0.038296 | 0 | 0
2026-02 | 2026-02-05 | Holland Landing Well No. 2 | WEST | Attending site to complete chlorine analyzer push button replacements (W11622780). Completed repairs on the Treated Total and Effluent Free chlorine analyzers. Analyzer readings were verified after work was completed. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.053375 | ML: above threshold (no LLM available) — 0.053 | repair [maintenance_action] | 0.053375 | 0 | 0
2026-02 | 2026-02-06 | Holland Landing Well No. 2 | WEST | On-site for station check and to respond to combine chlorine hihi interlock alarm @0848 hrs well interlocked and placed in manual off 1330 hrs verified analyzers readings upon arrival: Treated FCL = 0.03 mg/l TCL = 1.84, 1.88 and 1.82 mg/l Analyzer reading FCL = 0.04 mg/l TCL = 2.03 mg/l 1350 hrs Did grab on Influent FCL = 2.50 mg/l Analyzer reading = 2.55 mg/l 1416 hrs Did grab on Effluent FCL = 2.15 mg/l Analyzer = 2.13 mg/l 1403 hrs cleared alarms and reset. Placed well 2 pump back to auto, well started in auto. Chlorine grabs: @ 1429 hrs Influent FCL FCL = 2.88mg/l Analyzer reading: FCL = 2.83 mg/l Effluent FCL @ 1435 hrs: FCL = 2.40 mg/l Analyzer: 2.38 mg/l Treated grabs @ 1446 hrs FCL : 0.12 mg/l Analyzer reading: FCL : 0.18 mg/l TCL : 3.06 mg/l TCL : 3.03mg/l SL1000: @ 1422 hrs with Ammonia pump2 FA = 0.12 mg/l TA = 0.53 mg/l Mono = 2.40 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 68% and dosing at 67 ppd Chlorine dose scada = 30.3 kg/d Dosage factor = 153 % Chlorinator2 and BP2 in dury2 Chlorine booster1 pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 61% speed Dosing 68.88 mL/min P1 MAX flow = 115 mL/min P2 MAX flow = 113 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 43.38 mL/min Reviewed scada and trends, duty active, ET at 53% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Notified ROC before leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0010712 | 0 | 0
2026-02 | 2026-02-03 | Holland Landing Well No. 2 | WEST | -on site to change cylinder 35.6kg- 103kg -no issues | FLAG | stage2_low_confidence | 0.0082898 | ML: above threshold (no LLM available) — 0.008 |  | 0.0082898 | 0 | 0
2026-02 | 2026-02-09 | Holland Landing Well No. 2 | WEST | Reviewed scada and trends, duty active, ET at 69% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1400 hrs Influent FCL FCL = 2.90mg/l Analyzer reading: FCL = 2.87 mg/l Effluent FCL @ 1406 hrs: FCL = 2.50 mg/l Analyzer: 2.48 mg/l Treated grabs @ 1419 hrs FCL : 0.13 mg/l Analyzer reading: FCL : 0.17 mg/l TCL : 3.14 mg/l TCL : 3.10mg/l SL1000: @ 1400 hrs with Ammonia pump2 FA = 0.04 mg/l TA = 0.51 mg/l Mono = 2.38 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 65% and dosing at 67 ppd Chlorine dose scada = 29.6 kg/d Dosage factor = 149 % Chlorinator2 and BP2 in duty2 Chlorine booster1 pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 61% speed Dosing 69.08 mL/min P1 MAX flow = 115 mL/min P2 MAX flow = 113 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 43.10 mL/min Pump2 in duty2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; scada [control_system] | 0.0021844 | 0 | 0
2026-02 | 2026-02-24 | Holland Landing West Elevated Tank | WEST | On site to complete station check and receive 400L of sodium hypochlorite. Readings entered into PWQ sheet. | FLAG | stage2_low_confidence | 0.012861 | ML: above threshold (no LLM available) — 0.013 |  | 0.012861 | 0 | 0
2026-02 | 2026-02-23 | Holland Landing West Elevated Tank | WEST | Attending site to check Hypo and Ammonia tank level transmitters due to erratic behaviour (W11528810). Replaced both transducers. Will monitor SCADA, to see if readings improve. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.032396 | ML: above threshold (no LLM available) — 0.032 | scada [control_system] | 0.032396 | 0 | 0
2026-02 | 2026-02-24 | Holland Landing West Elevated Tank | WEST | Station checked, equipment checked and ok All measurements are in mg/l Time: 9:41 Free grab 0.02 Total grab 1.11, second reading 1.10, third reading 1.11, vs analyzer 1.55. Adjusted pre injection analyzer to match grab average Mono 0.27 Free ammonia 0.15 Total ammonia 0.2 Post injection Time 10:07 Total chlorine grab 3.61, 3.44 seconded grab, 3.41 third grab, vs analyzer 3.32. Adjusted analyzer to match grab average Free chlorine grab 0.00 Mono 2.58 Free ammonia 0.09 Total ammonia 0.60 Bottom of the bowl tower Total chlorine 1.68 Free chlorine 0.08 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0019597 | 0 | 0
2026-02 | 2026-02-27 | Holland Landing West Elevated Tank | WEST | On-site for station check Reviewed scada and trends, duty active, ET @ 78% and filling @ 68 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 32% speed Dose scada: 64:64 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 17% speed Dosing 17:45 mL/min P1 MAX flow = 98 mL/min P2 MAX flow = 98 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 1438 hrs Tank Grabs: Analyzer reading TCL = 1.90 mg/l TCL = mg/l FCL = 0.06 mg/l FCL = mg/l Mono = 0.72 mg/l TA = 0.22 mg/l FA = 0.07mg/l Nitrite = 0.002 mg/l Temp = C Nitrate = Did grabs on Pre. Pre Grabs: @ 1430 hrs: Analyzer TCL = 1.31 TCL = 1.33 mg/l FCL = 0.06 FCL = 0.06 mg/l Mono = 0.53 mg/l TA = 0.27 mg/l FA = 0.13 mg/l Post/ Treated Sample Grab @ 1416 hrs Mono = 2.49 mg/l TA = 0.55 mg/l FA = 0.050 mg/l FCL = 0.03 mg/l Analyzer: FCL = 0.04 mg/l TCL = 3.30mg/l TCL = 3.34 mg/l Deactivated duty No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.00056759 | 0 | 0
2026-02 | 2026-02-26 | Holland Landing West Elevated Tank | WEST | Onsite to investigate and troubleshoot with ammonia pumps Reviewed SCADA, duty was active tower filing at 64 l/s ammonia p2 was in duty1 and running at 11% speed Did grab on post FA = 0.00 mg/l TA = 0.45 mg/l Mono = 2.27 mg/l FCL = 0.10 mg/l Analyzer: FCL = 0.05mg/l TCL = 3.38 mg/l TCL = 3.43 mg/l performed calibration test through the cal column, there was no flow through cal column. Cleaned check valves on both ammonia pumps and replaced tubing and changed pumps orientation, switched ammonia pump duties, placed p1 in duty1 and adjusted ammonia pump1 max flow from 95 down to 85 mL/min Collected another grab again, FA = 0.04 mg/l TA = 0.50 mg/l Mono = 2.46 mg/l No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0040263 | 0 | 0
2026-02 | 2026-02-02 | Holland Landing West Elevated Tank | WEST | On-site for station check Reviewed scada and trends, duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Upon arrival duty was not active, tower at 85% and draining at 68 s/l Chemical pumps: Chlorine: Hypo pump #2 in duty1 and running at 36% speed Dose scada: 68.62 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 14% speed Dosing 23.05 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 1456 hrs Tank Grabs: Analyzer reading TCL = 2.54 mg/l TCL = mg/l FCL = 0.04 mg/l FCL = mg/l Mono = 0.50 mg/l TA = 0.31 mg/l FA = 0.21 mg/l Nitrite = 0.002 mg/l Nitrate = 0.049 Did grabs on Pre. Pre Grabs: @ 1350 hrs: Analyzer TCL = 1.26 TCL = 1.28 mg/l FCL = 0.05 FCL = 0.05 mg/l Mono = 0.26 mg/l TA = 0.32 mg/l FA = 0.29 mg/l Post/ Treated Sample Grab @ 1407 hrs Mono = 2.56 mg/l TA = 0.45 mg/l FA = 0.04 mg/l FCL = 0.04 mg/l Analyzer: FCL = 0.03 mg/l TCL = 3.24 mg/l TCL = 3.28 mg/l Deactivated duty No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.00066416 | 0 | 0
2026-02 | 2026-02-25 | Holland Landing West Elevated Tank | WEST | On-site for station check and collection of weekly bacT samples Reviewed scada and trends, duty active, ET @ 78% and filling @ 64 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 38% speed Dose scada: 43.09 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 8% speed Dosing 11:27 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 125 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 1400 hrs Tank Grabs: Analyzer reading TCL = 2.40 mg/l TCL = mg/l FCL = 0.06 mg/l FCL = mg/l Mono = 0.72 mg/l TA = 0.22 mg/l FA = 0.08 mg/l Nitrite = 0.003 mg/l Temp = 6.9 C Nitrate = Did grabs on Pre. Pre Grabs: @ 1406 hrs: Analyzer TCL = 1.31 TCL = 1.29 mg/l FCL = 0.07 FCL = 0.06 mg/l Mono = 0.49 mg/l TA = 0.27 mg/l FA = 0.17 mg/l Post/ Treated Sample Grab @ 1416 hrs Mono = 2.29 mg/l TA = 0.41 mg/l FA = 0.00 mg/l FCL = 0.06 mg/l Analyzer: FCL = 0.08 mg/l TCL = 3.44 mg/l TCL = 3.48 mg/l Deactivated duty No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.00070303 | 0 | 0
2026-02 | 2026-02-11 | Holland Landing West Elevated Tank | WEST | On-site for station check and collection of weekly bacT and operational samples Reviewed scada and trends, not duty active, ET @ 71% and filling Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 31% speed Dose scada: 58.00 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 12% speed Dosing 15:03 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 125 mL/min Pump discharge pressure: 320 Post/ Treated Sample Grab @ 15:40 hrs Mono = 2.24 mg/l TA = 0.49 mg/l FA = 0.04 mg/l FCL = 0.04 mg/l Analyzer: FCL = 0.02 mg/l TCL = 3.16 mg/l TCL = 3.20 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0048512 | 0 | 0
2026-02 | 2026-02-10 | Holland Landing West Elevated Tank | WEST | Changed duty stop from 88 to 75% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042528 | 0 | 0
2026-02 | 2026-02-20 | Holland Landing West Elevated Tank | WEST | On-site for station check Reviewed scada and trends, duty active, ET @ 80% and filling @ 44 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Changed tower stop level from 88 to 80% for a little deep cycle | FLAG | stage2_low_confidence | 0.012812 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.012812 | 0 | 0
2026-02 | 2026-02-12 | Holland Landing West Elevated Tank | WEST | On site to complete the following WO: Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Sump Pit System Inspection, Manual Valve, Exercise, Sensing Line Heat Trace System, Maintenance Low Temperature Alarm, Test, Ammonia System Inspection Sodium Hypochlorite System Inspection Notified ROC prepared ammonia batch with 2 bags Cleaned and verified depolox 5 analyzers Cleaned hypo board and panel, ran pumps through cal column no adjustment required Tower filling, no issues Notified ROC before leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0035172 | 0 | 0
2026-02 | 2026-02-17 | Holland Landing West Elevated Tank | WEST | On-site for station check and collection of weekly bacT sample Reviewed scada and trends, duty active, ET @ 80% and filling @ 44 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 22% speed Dose scada: 43.09 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 8% speed Dosing 11:27 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 125 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 0844 hrs Tank Grabs: Analyzer reading TCL = 1.90 mg/l TCL = mg/l FCL = 0.07 mg/l FCL = mg/l Mono = 0.61 mg/l TA = 0.25 mg/l FA = 0.13 mg/l Nitrite = 0.003 mg/l Temp = 6.9 C Nitrate = Did grabs on Pre. Pre Grabs: @ 0830 hrs: Analyzer TCL = 1.35 TCL = 1.38 mg/l FCL = 0.07 FCL = 0.02 mg/l Mono = 0.38 mg/l TA = 0.27 mg/l FA = 0.20 mg/l Post/ Treated Sample Grab @ 08:20 hrs Mono = 1.97 mg/l TA = 0.44 mg/l FA = 0.05 mg/l FCL = 0.08 mg/l Analyzer: FCL = 0.03 mg/l TCL = 2.68 mg/l TCL = 2.71 mg/l Deactivated duty No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0005942 | 0 | 0
2026-02 | 2026-02-13 | Holland Landing West Elevated Tank | WEST | On-site for station check Reviewed scada and trends, not duty active, ET @ 71% and filling Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK | FLAG | stage2_low_confidence | 0.013338 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013338 | 0 | 0
2026-02 | 2026-02-06 | Holland Landing West Elevated Tank | WEST | On-site for station check Reviewed scada and trends, not duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Upon arrival duty was active, tower at 43% and draining at 57 s/l Chemical pumps: Chlorine: Hypo pump #2 in duty1 and running at 36% speed Dose scada: 68.62 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 14% speed Dosing 23.05 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 0910 hrs Tank Grabs: Analyzer reading TCL = 1.42 mg/l TCL = mg/l FCL = 0.06 mg/l FCL = mg/l Mono = 0.53 mg/l TA = 0.21 mg/l FA = 0.17 mg/l Nitrite = 0.003 mg/l Nitrate = 0.038 mg/l Did grabs on Pre. Pre Grabs: @ 0850 hrs: Analyzer TCL = 1.33 TCL = 1.32 mg/l FCL = 0.06 FCL = 0.03 mg/l Mono = 0.26 mg/l TA = 0.26 mg/l FA = 0.21 mg/l Post/ Treated Sample Grab @ 0800 hrs Mono = 1.99 mg/l TA = 0.41 mg/l FA = 0.05 mg/l FCL = 0.06 mg/l Analyzer: FCL = 0.02 mg/l TCL = 3.18 mg/l TCL = 3.19 mg/l Deactivated duty No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.00068021 | 0 | 0
2026-02 | 2026-02-09 | Holland Landing West Elevated Tank | WEST | onsite for station check collected grabs on tank, analyze and recorded into pwq data sheet | FLAG | stage2_low_confidence | 0.013818 | ML: above threshold (no LLM available) — 0.014 |  | 0.013818 | 0 | 0
2026-02 | 2026-02-25 | Jefferson Pumping Station & Reservoir | WEST | -on site to complete station check and weekly bacti W11620180 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample east cell 14:50 -free cl: 0.05mg/l -total cl: 1.98mg/l -west cell grab 14:55 -free cl: 0.06mg/l -total cl: 1.99mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049343 | 0 | 0
2026-02 | 2026-02-03 | Holland Landing West Elevated Tank | WEST | On site to collect weekly bact sample (W). Tested chlorine residuals via hach field kit. Free: 0.04 mg/L Total: 1.68 mg/L | FLAG | stage2_low_confidence | 0.0094827 | ML: above threshold (no LLM available) — 0.009 |  | 0.0094827 | 0 | 0
2026-02 | 2026-02-23 | Jefferson Pumping Station & Reservoir | WEST | Onsite for station check P1 oos P2 in man off P3&4 in service Checked residuals mg/l @1145 Total grab 1.85 Free grab 0.03 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-27 | Jefferson Pumping Station & Reservoir | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 08:05 -free cl: 0.07mg/l -total cl: 1.91mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047077 | 0 | 0
2026-02 | 2026-02-02 | Jefferson Pumping Station & Reservoir | WEST | -on site to complete station -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 08:50 -free cl: 0.08mg/l -total cl: 1.91mg/l -equipment and heating all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050301 | 0 | 0
2026-02 | 2026-02-16 | Jefferson Pumping Station & Reservoir | WEST | -Ran the pumping station under generator due to unstable power supply - Diesel hours=658.7 Fuel=6045L | FLAG | stage2_low_confidence | 0.013384 | ML: above threshold (no LLM available) — 0.013 |  | 0.013384 | 0 | 0
2026-02 | 2026-02-16 | Jefferson Pumping Station & Reservoir | WEST | -Reset P3 & P4 fail to start , MV3 & MV4 fail to open alarm - alarm reset and pumps restarted in auto duty 1 | FLAG | stage2_low_confidence | 0.015656 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system] | 0.015656 | 0 | 0
2026-02 | 2026-02-17 | Jefferson Pumping Station & Reservoir | WEST | - on site to complete station for Res/Ps and weekly bacti W11605685 -checked trends: all ok -entered readings in PWQ: all ok -collected west cell sample and chlorine grab 08:55 -free cl: 0.09mg/l -total cl: 1.94mg/l -east cell sample 09:00 -free cl: 0.09mg/l -total cl: 1.98mg/p -equipment all ok -checked PS trends -entered reading in PWQ: all ok -took chlorine grab 09:15 -free cl: 0mg/l -total cl: 2.17mg/l -diesel is still running - informed supervisor diesel at 56% - order being placed -diesel all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032453 | 0 | 0
2026-02 | 2026-02-12 | Jefferson Pumping Station & Reservoir | WEST | On site for station check Check Trends: All okay Station Duty not Active Pump 1 OOS. 15:00- Grabs taken Free Cl2- 0.07 mg/L Total Cl2- 1.88 mg/L Entered values into PWQ sheet. Equipment okay. | FLAG | stage2_low_confidence | 0.0080995 | ML: above threshold (no LLM available) — 0.008 | oos [equipment_failure] | 0.0080995 | 0 | 0
2026-02 | 2026-02-18 | Jefferson Pumping Station & Reservoir | WEST | -delivery did not show up -called driver delayed due to weather condition and went to wrong site | FLAG | stage2_low_confidence | 0.011932 | ML: above threshold (no LLM available) — 0.012 |  | 0.011932 | 0 | 0
2026-02 | 2026-02-20 | Jefferson Pumping Station & Reservoir | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 14:40 -free cl: 0.03mg/l -total cl: 1.96mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046926 | 0 | 0
2026-02 | 2026-02-11 | Jefferson Pumping Station & Reservoir | WEST | -on site to troubleshoot pump 2 valve fail to open -place pump 2 in local -exercise rotors valve -placed in duty 1 and tested: no issues -collected weekly bacti W11588844 and station check -chlorine grab and sample collect from east 08:45 -free cl: 0.06mg/l -total cl: 1.85mg/l -west cell 08:50 -free cl: 0.06mg/l -total cl: 1.90mg/l -equipment all ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-17 | Jefferson Pumping Station & Reservoir | WEST | -on site to place generator back to auto -confirmed with ROC power restored -no issues | FLAG | stage2_low_confidence | 0.010661 | ML: above threshold (no LLM available) — 0.011 |  | 0.010661 | 0 | 0
2026-02 | 2026-02-18 | Jefferson Pumping Station & Reservoir | WEST | -on site to receive diesel delivery | FLAG | stage2_low_confidence | 0.012143 | ML: above threshold (no LLM available) — 0.012 |  | 0.012143 | 0 | 0
2026-02 | 2026-02-11 | Jefferson Pumping Station & Reservoir | WEST | Vibration readings Pump 2 loud Leaving pump 3 in duty | FLAG | stage2_low_confidence | 0.013718 | ML: above threshold (no LLM available) — 0.014 | vibration [equipment_failure] | 0.013718 | 0 | 0
2026-02 | 2026-02-18 | Jefferson Pumping Station & Reservoir | WEST | -on site to receive 4000L of diesel | FLAG | stage2_low_confidence | 0.0092523 | ML: above threshold (no LLM available) — 0.009 |  | 0.0092523 | 0 | 0
2026-02 | 2026-02-09 | Jefferson Pumping Station & Reservoir | WEST | Onsite for station check Duty active P1 oos Checked residuals mg/l @1048 Total grab 1.91 Free grab 0.06 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Jefferson Pumping Station & Reservoir | WEST | -On-site to complete reservoir station check and collect sample -reservoir level = 76%, draining -checked equipment -reviewed trends -collected grab samples: 09:22 - East Cell: Free Chlorine = 0.03 mg/L Total Chlorine = 2.05 mg/L 09:26 - West Cell: Free Chlorine = 0.01 mg/L Total Chlorine = 2.01 mg/L MCL = 1.78 mg/L TNH3 = 0.42 mg/L FNH3 = 0.07 mg/L NO2 = 0.000 mg/L temp = 5.7 09:30 - collected weekly regulatory micro. sample from West Cell - W/O # W11568536 -recorded readings in PWQ sheet -no issues found -completed work orders, informed ROC of work -completed JFRS, Sump Pit System Inspection, Jefferson RES -completed JFRS, Actuated Valve Exercise & Inspection, Jefferson RES -completed JFRS, Air Valve Flush & Inspection, Jefferson RES -completed JFRS, Dehumidifier Inspection & Cleaning, Jefferson RES -completed JFRS, External Venting Screens Inspection, Jefferson RES -completed JFRS, JHSC Health and Safety Inspection, Jefferson RES and BPS -completed JFRS, Ventilation System Inspection, Jefferson Valve House -completed JFRS, Sump Pit System Inspection, Jefferson Valve House -completed JFRS, Flood Alarm Test Jefferson Valve House -completed JFRS, Dehumidifier Inspection & Cleaning, Jefferson, Valve House -completed JFRS, Air Valves Flush & Inspection Jefferson, Valve House -completed JFPS, Standby Power Generator Test Run and Run Hours log, Jefferson WPS -pre inspection ok Start hours = 653.3 Stop hours = 654.5 Run time = 1.2 hours Start fuel = 6257 L Stop fuel = 6188 L Fuel used = 69 L 11:37 - transfer to generator power -activated system duty 12:46 - transfer back to utility power -completed JFPS, Low Temperature Alarm Test, Jefferson WPS -completed JFPS, Sump Pit System Inspection, Jefferson WPS -completed JFPS, Ventilation System Inspection, Jefferson WPS -completed JFPS, Dehumidifier Inspection & Cleaning, Jefferson WPS -completed JFPS, Pump & Motor Inspection, Jefferson WPS -completed JFPS, Actuated Valves Exercise & Inspection, Jefferson WPS -no issues, site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; regulatory [regulatory]; alarm [control_system] | flood [critical]; work order [maintenance_action]; regulatory [regulatory]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-06 | Jefferson Pumping Station & Reservoir | WEST | -on site to complete PS station check -system duty active -pump #1 OOS, pumps 2 and 4 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 14:02 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 2.18 mg/L -no issues found | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-27 | King City Dufferin Booster Pumping Station | WEST | Onsite for station check Check trends: All okay Station duty not active. 09:00- Grabs taken Grab free CL2- 0.04 mg/L Grab Total Cl2- 1.74 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045493 | 0 | 0
2026-02 | 2026-02-23 | King City Dufferin Booster Pumping Station | WEST | Onsite for station check Check trends: All okay Station duty not active. 14:06- Grabs taken Grab free CL2- 0.02 mg/L Grab Total Cl2- 1.712 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045682 | 0 | 0
2026-02 | 2026-02-02 | King City Dufferin Booster Pumping Station | WEST | Onsite for station check Check trends: All okay Station duty active; Pump 1 running 13:40- Grabs taken Grab free CL2- 0.04 mg/L Grab Total Cl2- 1.72 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047903 | 0 | 0
2026-02 | 2026-02-20 | King City Dufferin Booster Pumping Station | WEST | Onsite for station check Check trends: All okay Station duty not active. reset pump 2 VFD fault on MCC panel 14:20- Grabs taken Grab free CL2- 0.02 mg/L Grab Total Cl2- 1.70 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure] | 0.0068848 | 0 | 0
2026-02 | 2026-02-13 | King City Dufferin Booster Pumping Station | WEST | Onsite for station check Check trends: All okay Station duty active; Pump 2 running. 09:00- Grabs taken Grab free CL2- 0.01 mg/L Grab Total Cl2- 1.67 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048103 | 0 | 0
2026-02 | 2026-02-17 | King City Dufferin Booster Pumping Station | WEST | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 12:49 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.87 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036632 | 0 | 0
2026-02 | 2026-02-10 | King City Dufferin Booster Pumping Station | WEST | On site for Scheduled PM work orders given below. Informed ROC about the works being done W11602154 KCPSDS, JHSC Health and Safety Inspection W11602164 KCPSDS, Valve Exercise W11602257 KCPSDS, Critical Air Valve Flush and Inspection | FLAG | stage2_low_confidence | 0.024819 | ML: above threshold (no LLM available) — 0.025 | work order [maintenance_action] | 0.024819 | 0 | 0
2026-02 | 2026-02-06 | King City Dufferin Booster Pumping Station | WEST | Onsite for station check Check trends: All okay Station duty not active 14:35 Grabs taken Grab free CL2- 0.02 mg/L Grab Total Cl2- 1.72 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045119 | 0 | 0
2026-02 | 2026-02-09 | King City Dufferin Booster Pumping Station | WEST | Onsite for station check Check trends: All okay Station duty not active; 13:30- Grabs taken Grab free CL2- 0.04 mg/L Grab Total Cl2- 1.58 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045493 | 0 | 0
2026-02 | 2026-02-25 | King City Dufferin Elevated Tank | WEST | on site to collect weekly bacti W11568288 and station check -checked trends: all ok - Tower draining- 63% -verified analyzer 14:00 -analyzer free: 0.04mg/l grab: 0.02mg/l -analyzer total: 1.70mg/l grab: 1.64mg/l -reagents all ok -entered reading in PWQ -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055459 | 0 | 0
2026-02 | 2026-02-02 | King City Dufferin Elevated Tank | WEST | Replaced Total and Free analyzer reagents | FLAG | stage2_low_confidence | 0.013177 | ML: above threshold (no LLM available) — 0.013 |  | 0.013177 | 0 | 0
2026-02 | 2026-02-17 | King City Dufferin Elevated Tank | WEST | On site to investigate inlet heat trace, chlorine rm exhaust fan, and meter chamber pump. ROC notified. Low temp. heat trace alarms cleared and RTD function verified. Heat trace system operational. Chlorine rm exhaust fan/damper is energized by light switch in addition to exhaust thermostat. Light and exhaust fan now separated and temperature control on heater and exhaust adjusted to avoid conflict. Meter chamber will be investigated in future. | FLAG | stage2_low_confidence | 0.019802 | ML: above threshold (no LLM available) — 0.02 | alarm [control_system]; alarms [control_system] | 0.019802 | 0 | 0
2026-02 | 2026-02-10 | King City Dufferin Elevated Tank | WEST | On site for scheduled PM workorders given below. Informed ROC about the works being done. W11571363 KCETDS, JHSC Health and Safety Inspection W11570892 KCETDS, Manual Valve, Exercise W11570910 KCETDS, Air Valve Flush & Inspection W11570940 KCETDS, Inlet/Outlet Heat Trace System, Inspection System fault, CMU created already W11570971 KCETDS, Actuated Valve, Exercise & Inspection W11571589 KCETDS, Dehumidifier, Cleaning & Inspection W11571862 KCETDS, Ventilation System, InspectionW11572030 KCETDS, Low Temperature Alarm Test Damper fail to close in cl2 room, informed team. W11570921 KCETDS, CL17 Chlorine Analyzer, Maintenance 14:00-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.03 mg/L Total Cl2 Grab- 1.60 mg/L, Analyzer - 1.65 mg/L | FLAG | stage2_low_confidence | 0.049612 | ML: above threshold (no LLM available) — 0.05 | fault [equipment_failure]; alarm [control_system] | 0.049612 | 0 | 0
2026-02 | 2026-02-17 | King City Dufferin Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 57 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 12:30 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.69 mg/L 12:30 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.71 mg/L MCL = 1.64 mg/L TNH3 = 0.37 mg/L FNH3 = 0.05 mg/L temp = 5.9 C 12:37 - collected weekly regulatory micro. sample - W/O # W11605507 -recorded readings in PWQ sheet -no issues found -collected operational ATP and phosphorous samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0036094 | 0 | 0
2026-02 | 2026-02-11 | King City Dufferin Elevated Tank | WEST | Details: on site to collect weekly bacti W11588830 and station check -checked trends: all ok - Tower draining- 71% -verified analyzer 14:05 -analyzer free: 0.03mg/l grab: 0.02mg/l -analyzer total: 1.53mg/l grab: 1.53mg/l -reagents all ok -Heat trace unit reset. -entered reading in PWQ -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044938 | 0 | 0
2026-02 | 2026-02-04 | King City Dufferin Elevated Tank | WEST | on site to collect weekly bacti W11568288 and station check -checked trends: all ok - Tower draining- 54% -verified analyzer 14:05 -analyzer free: 0.03mg/l grab: 0.02mg/l -analyzer total: 1.70mg/l grab: 1.71mg/l -reagents all ok -entered reading in PWQ -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055459 | 0 | 0
2026-02 | 2026-02-09 | King City Dufferin Elevated Tank | WEST | Reset Heat trace Alarm in the Heat trace unit. Unable to clear from Scada. CMU W11650037 created | FLAG | stage2_low_confidence | 0.01279 | ML: above threshold (no LLM available) — 0.013 | scada [control_system]; alarm [control_system] | 0.01279 | 0 | 0
2026-02 | 2026-02-25 | King City Fisher Elevated Tank | WEST | On site for station check, W11620166 Micro Sampling Check Trends- All Okay Tower draining- 66% 13:20- Verified Analyzers Free Cl2 Grab - 0.05mg/L; Analyzer 0.02mg/L Total Cl2 Grab - 1.60 mg/L, Analyzer 1.64 mg/L Reagent all good. Samples collected Equipment Okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053111 | 0 | 0
2026-02 | 2026-02-03 | King City Dufferin Elevated Tank | WEST | -on site to repair chlorine room service water line -leaving line isolated to allow glue to dry | FLAG | stage2_low_confidence | 0.023948 | ML: above threshold (no LLM available) — 0.024 | repair [maintenance_action] | 0.023948 | 0 | 0
2026-02 | 2026-02-20 | King City Fisher Elevated Tank | WEST | Under the direction of Cole Warnica, Worked along side Network Analyst Aaron Magsakay, to replaced a Network switch to Cisco IE3300 inside a Network panel. Provided 24 VDC power to new switch from 24VDC power supply. There is a trend gap on SCADA between 12:30 PM to 12:45 PM due to this work. After the replacement, checked all the ports and reset the comm alarms. | FLAG | stage2_low_confidence | 0.023659 | ML: above threshold (no LLM available) — 0.024 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.023659 | 0 | 0
2026-02 | 2026-02-20 | King City Fisher Elevated Tank | WEST | -on site responding to power outage -site running on generator power | FLAG | stage2_low_confidence | 0.01178 | ML: above threshold (no LLM available) — 0.012 |  | 0.01178 | 0 | 0
2026-02 | 2026-02-17 | King City Fisher Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 62 % -checked equipment -reviewed trends -filled acetate buffer -verified chlorine analyzers: 11:26 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.65 mg/L 11:26 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.60 mg/L SL1000 Readings: MCL = 1.51 mg/L TNH3 = 0.36 mg/L FNH3 = 0.06 mg/L NO2 = 0.000 mg/L temp = 5.3 C 11:34 - collected weekly regulatory micro. sample - W/O # W11605507 -recorded readings in PWQ sheet -no issues found -collected operational ATP and phosphorous samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0035968 | 0 | 0
2026-02 | 2026-02-12 | King City Fisher Elevated Tank | WEST | -on site to complete work orders -informed ROC of work -completed Low Temperature Alarm, Test -completed High & Low Water Level Alarm, Test -completed Inlet/Outlet Heat Trace System, Inspection -completed Sensing Line Heat Trace System, Inspection -completed PRV Valve, Inspection -completed Portable Gasoline Generator, Test -transferred PAC panel power to portable generator, no issues -filled generator fuel -completed JHSC Health and Safety Inspection -completed Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance -verified analyzers after maintenance: 10:24 - Analyzer readings: Free Chlorine = 0.01 mg/L Total Chlorine = 1.58 mg/L 10:24 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.54 mg/L -no issues, site back to normal operation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; alarm [control_system] | 0.0055218 | 0 | 0
2026-02 | 2026-02-10 | King City Fisher Elevated Tank | WEST | Onsite to replace OIT computer. | FLAG | stage2_low_confidence | 0.012692 | ML: above threshold (no LLM available) — 0.013 |  | 0.012692 | 0 | 0
2026-02 | 2026-02-09 | King City Fisher Elevated Tank | WEST | Responded to PAC card alarms found issues with hardware. Replaced PAC power supply. OIT failed while at site. Repointed tag collection to H4AUSSP1 server and informed ROC to disregard historian heartbeat alarm | FLAG | stage2_low_confidence | 0.045082 | ML: above threshold (no LLM available) — 0.045 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.045082 | 0 | 0
2026-02 | 2026-02-11 | King City Fisher Elevated Tank | WEST | On site for station check, W11588830 Micro Sampling Check Trends- All Okay Tower draining- 75% 12:23- Verified Analyzers Free Cl2 Grab - 0.04mg/L; Analyzer 0.01mg/L Total Cl2 Grab - 1.53 mg/L(Avg- 1.50,1.53,1.57); Analyzer 1.40mg/L Adjudged total analyzer value up to 1.53 Reagent all good. Samples collected Equipment Okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058902 | 0 | 0
2026-02 | 2026-02-04 | King City Fisher Elevated Tank | WEST | On site for station check, W11568288 Micro Sampling Check Trends- All Okay Tower draining- 55% 13:30- Verified Analyzers Free Cl2 Grab - 0.02mg/L; Analyzer 0.01mg/L Total Cl2 Grab - 1.60 mg/L; Analyzer 1.63mg/L Reagent all good. Samples collected Equipment Okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052909 | 0 | 0
2026-02 | 2026-02-25 | Kleinburg Elevated Tank | WEST | On site for Station Check, W11620283 Micro Sampling Check Trends: All Okay Tower Draining (86%) 12:25- Grabs Taken FCL- 0.07 mg/L TCL- 1.91 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040941 | 0 | 0
2026-02 | 2026-02-17 | Kleinburg Elevated Tank | WEST | On site for Station Check, W11605699 Micro Sampling Check Trends: All Okay Tower Draining (77%) 12:45- Grabs Taken FCL- 0.05 mg/L TCL- 2.00 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040941 | 0 | 0
2026-02 | 2026-02-18 | Kleinburg Elevated Tank | WEST | On site for the following KLET27, JHSC Health and Safety Inspection, Kleinburg ET (1M) KLET27, Inlet/Outlet Heat Trace System, Inspection, Kleinburg ET (1M) [WINTER] KLET27, Gasoline Generator, Test Run, Kleinburg ET (1M) KLET27, Low Temperature Alarm, Test, Kleinburg ET (1M) [WINTER] KLET27, Dehumidifier, Cleaning & Inspection, Kleinburg ET (1M) No new issues | FLAG | stage2_low_confidence | 0.010838 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010838 | 0 | 0
2026-02 | 2026-02-04 | Kleinburg Elevated Tank | WEST | On site for Station Check, W11568550 Micro Sampling Check Trends: All Okay Tower Draining (73%) 12:35- Grabs Taken FCL- 0.04 mg/L TCL- 2.01 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040941 | 0 | 0
2026-02 | 2026-02-11 | Kleinburg Elevated Tank | WEST | On site for Station Check, W11588947 Micro Sampling Check Trends: All Okay Tower Draining (88%) 14:00- Grabs Taken FCL- 0.04 mg/L TCL- 1.92 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040941 | 0 | 0
2026-02 | 2026-02-27 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1 & 2 active. 12:25-Verified Analyzers Free Cl2 Grab- 0.01mg/L Free Cl2 Analyzer- 0.03mg/L Total Cl2 Grab- 1.92 mg/L Total Cl2 Analyzer- 1.87mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039265 | 0 | 0
2026-02 | 2026-02-23 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1 & 2 active. 12:45-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 1.90 mg/L Total Cl2 Analyzer- 1.84mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039265 | 0 | 0
2026-02 | 2026-02-02 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1& 2 running 13:00-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 2.06 mg/L Total Cl2 Analyzer- 1.99mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039036 | 0 | 0
2026-02 | 2026-02-20 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 2 & 3 active. 12:25-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 1.90 mg/L Total Cl2 Analyzer- 1.86mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039265 | 0 | 0
2026-02 | 2026-02-17 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site for Station Check. Check Trends: All okay Station Duty not Active 12:20-Verified Analyzers Free Cl2 Grab- 0.03mg/L Free Cl2 Analyzer- 0.03mg/L Total Cl2 Grab- 1.96 mg/L Total Cl2 Analyzer- 1.98mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036366 | 0 | 0
2026-02 | 2026-02-12 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site for the following PM workorders, Informed ROC about the works being done W11582972 KLPS27, JHSC Health and Safety Inspection, W11583371 KLPS27, Low Temperature Alarm, Test, W11583417 KLPS27, Header Suction and Discharge Valve, Exercise, W11583526 KLPS27, Pump Suction and Discharge Valve, Exercise W11583691 KLPS27, Kleinburg WPS - KLPS27, Critical Air Valve Flush and Inspection (1M) W11583384 KLPS27, Sump Pit System, Inspection W11583400 KLPS27, Storm Sump Pump, Maintenance W11583667 KLPS27, Bypass Valve Actuator, Exercise & Inspection, W11583776 KLPS27, Pressure Relief Valve, Inspection W11583734 KLPS27, Flood Alarm, Test, Kleinburg, W11584095 KLPS27, Hoist, Inspection, Kleinburg, WPS W11582982 KLPS27, Chlorine Analyzer, Maintenance, Kleinburg W11594142 KLPS27, Kleinburg Booster BPS, Station Check Check Trends: All okay Station Duty not Active Entered values into PWQ sheet. Equipment Okay.13:50-Verified Analyzers Free cl2 Grab- 0.03 mg/L, Analyzer - 0.03 mg/L Total Cl2 Grab- 1.99 mg/L, Analyzer - 1.92 mg/L Topped up both KI and Acetate reagents. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; flood [critical]; oos [equipment_failure]; alarm [control_system] | bypass [critical]; flood [critical]; oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-06 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1& 3 running 13:00-Verified Analyzers Free Cl2 Grab- 0.03mg/L Free Cl2 Analyzer- 0.03mg/L Total Cl2 Grab- 2.04 mg/L Total Cl2 Analyzer- 1.97mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039036 | 0 | 0
2026-02 | 2026-02-09 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1& 2 running 12:10-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 2.04 mg/L Total Cl2 Analyzer- 1.95mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. W11585332- Washroom cleaning complete | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040828 | 0 | 0
2026-02 | 2026-02-23 | Kleinburg Whisper Lane Booster Pumping Station | WEST | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 11:20- Verified Analyzers Grab free Cl2- 0.01 mg/L Analyzer free Cl2- 0.05 mg/L Grab Total Cl2- 1.87 mg/L Analyzer Total Cl2- 1.88 mg/L Reagents all good. entered values into PWQ sheet Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040099 | 0 | 0
2026-02 | 2026-02-27 | Kleinburg Whisper Lane Booster Pumping Station | WEST | On site for station check Check trends: All okay 13:15- Verified Analyzers Grab free Cl2- 0.02 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.85 mg/L (AVG -1.85,1.85,1.83) Analyzer Total Cl2- 1.70 mg/L Adjusted analyzer up to 1.80 mg/L Reagents all good. entered values into PWQ sheet Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043003 | 0 | 0
2026-02 | 2026-02-02 | Kleinburg Whisper Lane Booster Pumping Station | WEST | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 12:00- Verified Analyzers Grab free Cl2- 0.05 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 2.03 mg/L Analyzer Total Cl2- 1.98 mg/L Replaced KI reagent. entered values into PWQ sheet Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004044 | 0 | 0
2026-02 | 2026-02-12 | Kleinburg Whisper Lane Booster Pumping Station | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok - verified analyzer 09:55 -analyzer free: 0.05mg/l grab: 0.07mg/l -analyzer total: 1.81mg/l grab: 1.88mg/l - adjusted -topped up acetate at KLPSWL and KLW3/4 -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059982 | 0 | 0
2026-02 | 2026-02-20 | Kleinburg Whisper Lane Booster Pumping Station | WEST | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 11:20- Verified Analyzers Grab free Cl2- 0.05 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.85 mg/L Analyzer Total Cl2- 1.82 mg/L Reagents all good. entered values into PWQ sheet Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040099 | 0 | 0
2026-02 | 2026-02-09 | Kleinburg Whisper Lane Booster Pumping Station | WEST | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 11:05- Verified Analyzers Grab free Cl2- 0.01 mg/L Analyzer free Cl2- 0.05 mg/L Grab Total Cl2- 2.02 mg/L Analyzer Total Cl2- 1.95 mg/L Reagent all good entered values into PWQ sheet Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039787 | 0 | 0
2026-02 | 2026-02-17 | Kleinburg Whisper Lane Booster Pumping Station | WEST | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 14:10- Verified Analyzers Grab free Cl2- 0.05 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.97 mg/L Analyzer Total Cl2- 1.96 mg/L Topped up Acetate. entered values into PWQ sheet Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040103 | 0 | 0
2026-02 | 2026-02-03 | Kleinburg Whisper Lane Booster Pumping Station | WEST | Onsite for the following PM Work orders. Informed ROC about the works being done. W11571876- High/Low temp Alarm test W11571889 - Flood Alarm test W11572068- Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance 14:35-Verified Analyzer Free cl2 Grab- 0.04 mg/L, Analyzer - 0.06 mg/L Total Cl2 Grab- 1.90 mg/L, Analyzer - 1.84 mg/L | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-06 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | Station check Well 3 and 8 in manual 11.1 l/s Totals well pump 8 - 11 hrs. Total 35137 Well pump 13 - 11 hrs Total 34464 Well 8 RPM 2450 Well 13 RPM 2112 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059514 | 0 | 0
2026-02 | 2026-02-06 | Kleinburg Whisper Lane Booster Pumping Station | WEST | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 11:40- Verified Analyzers Grab free Cl2- 0.05 mg/L (avg-0.05,0.07,0.02) Analyzer free Cl2- 0.12 mg/L Adjusted analyzer down to 0.05 Grab Total Cl2- 1.92 mg/L Analyzer Total Cl2- 1.88 mg/L Reagent all good. entered values into PWQ sheet Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004195 | 0 | 0
2026-02 | 2026-02-25 | Maple North Reservoir | WEST | -on site for station check and weekly bacti W11620190 -checked trends: all ok -entered readings in PWQ: all ok -took sample and chlorine grab east cell 09:55 -free cl: 0.05mg/l -total cl: 1.66mg/l -west cell chlorine grab 10:00 -free cl: 0.07mg/l -total cl: 1.64mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049433 | 0 | 0
2026-02 | 2026-02-10 | Maple North Reservoir | WEST | -on site to complete work orders -informed ROC of work -completed JHSC Health and Safety Inspection -found eyewash booster pump pressure gauge not working, created follow up work order to replace gauge and verify pressure switches. Leaving booster pump off for now -completed Sump Pump, Inside Inspection & Maintenance | FLAG | stage2_low_confidence | 0.052605 | ML: above threshold (no LLM available) — 0.053 | oos [equipment_failure]; not working [equipment_failure]; work order [maintenance_action] | 0.052605 | 0 | 0
2026-02 | 2026-02-17 | Maple North Reservoir | WEST | -On-site to complete station check and collect sample -reservoir level = 66 %, filling -checked equipment -reviewed trends -collected grab samples: 10:40 - East Cell: Free Chlorine = 0.02 mg/L Total Chlorine = 1.70 mg/L 10:43 - West Cell: Free Chlorine = 0.01 mg/L Total Chlorine = 1.65 mg/L MCL = 1.51 mg/L TNH3 = 0.37 mg/L FNH3 = 0.07 mg/L NO2 = 0.001 mg/L temp = 7.0 10:46 - collected weekly regulatory micro. sample from West Cell - W/O # W11605685 -recorded readings in PWQ sheet -no issues found -collected operational ATP and phosphorous samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0021198 | 0 | 0
2026-02 | 2026-02-11 | Maple North Reservoir | WEST | -on site for station check and weekly bacti W11588844 -east cell chlorine grab 10:30 -free cl: 0.05mg/l -total cl: 1.60mg/l -west cell chlorine 10:35 -free cl: 0.08mg/l -total cl: 1.56mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004955 | 0 | 0
2026-02 | 2026-02-18 | Maple North Reservoir | WEST | Check pressure on pump for eyewash | FLAG | stage2_low_confidence | 0.012925 | ML: above threshold (no LLM available) — 0.013 |  | 0.012925 | 0 | 0
2026-02 | 2026-02-04 | Maple North Reservoir | WEST | -on site for station check and weekly bacti W11568536 -checked trends: all ok -entered readings in PWQ: all ok -took grab and sample from West cell 09:45 -free cl: 0.11mg/l -total cl: 1.71mg/l -east cell grab 09:50 -free cl: 0.06mg/l -total cl: 1.67mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046753 | 0 | 0
2026-02 | 2026-02-25 | Maple Pumping Station | WEST | -on site to reset PD8 pump 3 -no issues - alarms reset | FLAG | stage2_low_confidence | 0.010474 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010474 | 0 | 0
2026-02 | 2026-02-23 | Maple Pumping Station | WEST | Onsite for station check Checked residuals mg/l Pd7 @1010 Total analyzer 1.67 grab 1.67 Free grab 0.06 Pd8 Cl2 analyzer isolated trends erratic | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0021632 | 0 | 0
2026-02 | 2026-02-25 | Maple Pumping Station | WEST | Removed spool piece on PD7 pump 4, disassembled check valve on discharge side of pump to determine root cause of the issue. Pump 4 will remain out of service until parts arrive. Ops notified. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-26 | Maple Pumping Station | WEST | -on site to receive 10 000L of diesel -no issues | FLAG | stage2_low_confidence | 0.0081947 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081947 | 0 | 0
2026-02 | 2026-02-27 | Maple Pumping Station | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 13:45 -analyzer free: 0.03mg/l grab: 0.06mg/l -analyzer total: 1.69mg/l grab: 1.69mg/l -PD8 analyzer offline -PD8 pump 4 multin warning alarm - unable to reset W11695175 -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068352 | 0 | 0
2026-02 | 2026-02-02 | Maple Pumping Station | WEST | On site to remove and replace cooling fans for PD8 VFDs 1-3. Tested all VFDs for proper operation. | FLAG | stage2_low_confidence | 0.012423 | ML: above threshold (no LLM available) — 0.012 |  | 0.012423 | 0 | 0
2026-02 | 2026-02-02 | Maple Pumping Station | WEST | -on site for station check -checked trends: -entered readings in PWQ: all ok -verified PD7 analyzer 13:35: -analyzer free: 0.04mg/l grab: 0.07mg/l -analyzer total: 1.73mg/l grab: 1.71mg/l -verified PD8 analyzer 13:45: -analyzer free: 0.04mg/l grab: 0.05mg/l -analyzer total: 1.44mg/l grab: 1.43mg/l -equipment all ok and heating all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005954 | 0 | 0
2026-02 | 2026-02-20 | Maple Pumping Station | WEST | -spoke with Dwayne Lewis who is on site- PD8 suction main isolated - PD8 analyzer will be offline for 2-3 weeks during isolation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062184 | 0 | 0
2026-02 | 2026-02-10 | Maple Pumping Station | WEST | -on site to complete work orders -informed ROC of work -completed Air Handling Units, Inspection & Maintenance -found broken belt in AHU3 blower - removed belt and will source a replacement -completed JHSC Health and Safety Inspection -completed Diesel Flood Alarm, Test -completed Fuel Transfer Pump Control Panel, Test -completed AC Units 1-4 (Backup) Test Run | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; backup [infrastructure] | flood [critical]; work order [maintenance_action]; alarm [control_system]; backup [infrastructure] |  | 1 | 0
2026-02 | 2026-02-18 | Maple Pumping Station | WEST | Pump 4 check valve | FLAG | stage2_low_confidence | 0.0091656 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091656 | 0 | 0
2026-02 | 2026-02-12 | Maple Pumping Station | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified PD7 analyzer 13:10 -analyzer free: 0.04mg/l grab: 0.07mg/l -analyzer total: 1.77mg/l grab: 1.67mg/l - adjusted -verified PD8 analyzer 13:15 -analyzer free: 0.04mg/l grab: 0.08mg/l -analyzer total: 1.41mg/l grab: 1.40mg/l - tested PD7 pumps 1&4 due to high differential switch alarms -flushed transmitter and exercised valves -pump 1 all ok pump 4 oos | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | Maple Pumping Station | WEST | -received call about high PD8 chlorine alarms -informed to disregard - suction header isolated/ analyzer isolated | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0065356 | 0 | 0
2026-02 | 2026-02-18 | Maple Pumping Station | WEST | -on site to troubleshoot PD7 pump pressure differential alarms with Dan Boate -manually and locally started pump 1 - 4 -pump 4 check valve is seized shut - placed in local off -informed team lead and supervisor of incorrect alarming -investigating time delay option | FLAG | stage2_low_confidence | 0.031039 | ML: above threshold (no LLM available) — 0.031 | seized [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.031039 | 0 | 0
2026-02 | 2026-02-20 | Maple Pumping Station | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 10:20 -analyzer free: 0.03mg/l grab: 0.06mg/l -analyzer total: 1.62mg/l grab: 1.69mg/l - adjusted -verified PD8 analyzer 10:25 -analyzer free: 0.05mg/l grab: 0.06mg/l -analyzer total: 1.70mg/l grab: 1.67mg/l -equipment all ok -linear on site draining PD8 header - -PD8 may fail during draining - analyzer not being directed to user | FLAG | stage2_low_confidence | 0.0080103 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080103 | 0 | 0
2026-02 | 2026-02-11 | Maple Pumping Station | WEST | Vibration readings | FLAG | stage2_low_confidence | 0.021831 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021831 | 0 | 0
2026-02 | 2026-02-10 | Maple Pumping Station | WEST | -on site for station checked trends - start time: 482.7/496.5 -stop time: 484/497.7 -diesel level: -sump pit inspection: all ok -hoist inspection: all ok -screen inspection: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006037 | 0 | 0
2026-02 | 2026-02-17 | Maple Pumping Station | WEST | -on site to complete station check -checked equipment -reviewed trends -recorded readings in PWQ sheet Verified analyzers: 09:31 - PD7 Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.63 mg/L 09:31 - PD7 Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.67 mg/L 09:39 - PD8 Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.72 mg/L 09:39 - PD8 Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.61/1.61/1.61 mg/L 09:49 - adjusted PD8 total chlorine analyzer to 1.61 mg/L based on average of 3 grabs -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055058 | 0 | 0
2026-02 | 2026-02-18 | Maple Pumping Station | WEST | On site to troubleshoot pressure differential issues with PD7 P1 and P4. Found check valve stuck closed on P4. Could not find any problem with P1. | FLAG | stage2_low_confidence | 0.024405 | ML: above threshold (no LLM available) — 0.024 | valve stuck [infrastructure] | 0.024405 | 0 | 0
2026-02 | 2026-02-04 | Maple Pumping Station | WEST | Informed ROC. Onsite to perform annual maintenance/calibrations. Devices were done as below: MAP8 AITs, MAP8 Suction and discharge PIT. Used the calibration mode. Took multiple grab samples. No adjustments required. MAP8 Total AIT A - 1.42 mg/l G - 1.43 mg/l. MAP8 Free AIT A- 0.07 mg/l G - 0.07 mg/l. Put all the devices back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0028187 | 0 | 0
2026-02 | 2026-02-06 | Maple Pumping Station | WEST | -on site to complete station check -PD7 and PD8 duties not active -checked equipment -reviewed trends -recorded readings in PWQ sheet Verified analyzers: 12:02 - PD7 Analyzer readings: Free Chlorine = 0.10 mg/L Total Chlorine = 1.62 mg/L 12:02 - PD7 Grabs: Free Chlorine = 0.05/0.04/0.04 mg/L Total Chlorine = 1.69/1.72/1.71 mg/L 12:09 - adjusted PD7 free chlorine analyzer to 0.04 mg/L based on average of 3 grabs 12:12 - adjusted PD7 total chlorine analyzer to 1.71 mg/L based on average of 3 grabs 12:14 - PD8 Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.45 mg/L 12:14 - PD8 Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.44 mg/L -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068738 | 0 | 0
2026-02 | 2026-02-09 | Maple Pumping Station | WEST | -on site to complete station checked trends -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 12:40 -analyzer free: 0.05mg/l grab: 0.05mg/l -analyzer total: 1.60mg/l grab: 1.72mg/l - adjusted -verified PD8 analyzer 12:50 -analyzer free: 0.07mg/l grab: 0.10mg/l -analyzer total:1.63mg/l grab: 1.70mg/l - adjusted -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006706 | 0 | 0
2026-02 | 2026-02-05 | Maple Pumping Station | WEST | Informed ROC. Onsite to perform annual maintenance/calibrations. Devices were done as below: MAP7 and MAP8 FIT, MAP7 AITs, MAP7 Suction and discharge PIT. Used the calibration mode. Took multiple grab samples. adjusted analyzers accordingly. MAP7 Total AIT A - 1.68 mg/l G - 1.67 mg/l. MAP7 Free AIT A- 0.08 mg/l G - 0.09 mg/l. Put all the devices back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0031665 | 0 | 0
2026-02 | 2026-02-06 | Maple Pumping Station | WEST | On site to continue wiring for PD8 VFD remote reset signals. | FLAG | stage2_low_confidence | 0.010396 | ML: above threshold (no LLM available) — 0.01 |  | 0.010396 | 0 | 0
2026-02 | 2026-02-23 | Maple South Reservoir | WEST | Took grab in reservoir of isolated section mg/l @1052 Total grab 1.07 Free grab 0.03 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059294 | 0 | 0
2026-02 | 2026-02-03 | Maple Pumping Station | WEST | On site to investigate wiring and schematical details of connecting each PD8 VFD to a remote scada reset signal. | FLAG | stage2_low_confidence | 0.016945 | ML: above threshold (no LLM available) — 0.017 | scada [control_system] | 0.016945 | 0 | 0
2026-02 | 2026-02-04 | Maple Pumping Station | WEST | On site to continue work on PD8 VFD remote reset signal connections. | FLAG | stage2_low_confidence | 0.010764 | ML: above threshold (no LLM available) — 0.011 |  | 0.010764 | 0 | 0
2026-02 | 2026-02-26 | Maple South Reservoir | WEST | -on site to freshen up isolated metro line -took chlorine grab 11:15- -free cl: 0.03mg/l -total cl: 0.95mg/l -activated BVPS -opened interconnect valve quarter way -opened site valve 6 turns - 15l/s -took chlorine grab 11:45 -free cl: 0.05mg/l -grab: 0.86mg/l -will monitor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037265 | 0 | 0
2026-02 | 2026-02-25 | Maple South Reservoir | WEST | -on site for station check and weekly bacti W11620180 -check trends: all ok -entered reading in PWQ: all ok -took sample and chlorine grab north cell 08:50 -free cl: 0.06mg/l -total cl: 1.69mg/l -verified peel analyzer 08:55 -analyzer 1.71mg/l grab: 1.68mg/l -reagents all ok -verified metro analyzer 09:00 -analyzer free: 0.02mg/l grab: 0.04mg/l -analyzer total: 1.66mg/l grab: 1.67mg/l -construction on going | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051205 | 0 | 0
2026-02 | 2026-02-23 | Maple South Reservoir | WEST | YPFM to PD8 suction chlorine analyzer (WPS SUCH1 AIT1) powered off, isolated and placed OOS. YPFM is isolated from system during shipwell project works, analyzer not currently sampling from system / no sample flow to analyzer. Shelved outstanding alarms associated with analyzer (other than HMA, out of range). | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | sso [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | Maple South Reservoir | WEST | -on site to complete work orders -informed ROC of work -completed Isolating Valve Box Cover, Inspection -completed JHSC health and safety inspection -completed Sump Pump Inspection -tested flood alarm -completed Chlorine Analyzer Maintenance: -filled electrolyte and grit sand in metro depolox analyzer -cleaned Peel CL17 and flushed sample lines -verified analyzers after maintenance: 09:29 - Metro Analyzer readings: Free Chlorine = 0.13 mg/L Total Chlorine = 1.38 mg/L 09:29 - Metro Grabs: Free Chlorine = 0.02/0.02/0.01 mg/L Total Chlorine = 1.63/1.62/1.60 mg/L 09:37 - adjusted metro free chlorine analyzer to 0.02 mg/L based on average of 3 grabs 09:40 - adjusted metro total chlorine analyzer to 1.62 mg/L based on average of 3 grabs 09:41 - Peel TCL analyzer = 1.63 mg/L 09:41 - Peel TCL grab = 1.61 mg/L -completed 3 Tonne Hoist, Inspection -completed Ventilation & Dehumidifier, Maintenance -site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | Maple South Reservoir | WEST | -On-site to complete station check and collect sample -South Cell OOS -reservoir level = 82%, filling -checked equipment -reviewed trends -analyzer reagents ok -verified Peel Total Chlorine Analyzer: 08:55 - Peel TCL analyzer = 1.71 mg/L 08:55 - Peel FCL grab = 0.00 mg/L Peel TCL grab = 1.70 mg/L -verified Metro chlorine analyzers: 08:56 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.69 mg/L 08:56 - Grabs: Free Chlorine = 0.01 mg/L Total Chlorine = 1.72 mg/L -collected grab samples: 09:02 - North Cell: Free Chlorine = 0.02 mg/L Total Chlorine = 1.71 mg/L MCL = 1.62 mg/L TNH3 = 0.37 mg/L FNH3 = 0.05 mg/L NO2 = 0.000 mg/L temp = 3.7 09:05 - collected weekly regulatory micro. sample from North cell - W/O # W11605685 -recorded readings in PWQ sheet -no issues found -collected operational ATP and phosphorous samples | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-11 | Maple South Reservoir | WEST | -on site to complete station check and weekly W11588844 -checked trends: all ok -entered readings in PWQ: all ok -verified peel analyzer 09:50: 1.56mg/l grab:1.54mg/l -reagents all ok -took chlorine grab and sample from north cell 09:55 -free cl: 0.08mg/l -total cl: 1.55mg/l -verified metro analyzer 10:00 -analyzer free: 0.02mg/l grab: 0.04mg/l -analyzer total: 1.56mg/l grab: 1.54mg/l -construction on going | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061768 | 0 | 0
2026-02 | 2026-02-04 | Maple South Reservoir | WEST | -on site for station check and weekly bacti W11568536 -checked trends: all ok -entered readings in PWQ: all ok -verified Peel analyzer 08:30 -analyzer: 1.73mg/l grab: 1.70mg/l -reagents all ok -north cell grab 08:35 -free cl: 0.03mg/l -total cl: 1.66mg/l -verified metro analyzer 08:40 -analyzer free: 0.03mg/l grab: -analyzer total: 1.74mg/l grab: -construction on going -no issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037278 | 0 | 0
2026-02 | 2026-02-06 | Maple South Reservoir | WEST | Onsite for annual calibrations Informed ROC Needed to complete site orientation with Torbear and verify that completed safety training is up to date. Continued with calibrations Completed reservoir inlet FITs South reservoir OOS. Completed LIT calibration Ask ROC for permission to proceed with North reservoir LIT calibration. ROC made some calls and granted permission. Completed North reservoir LIT calibration. Informed ROC immediately after completion Will return to continue calibrations next week Informed ROC. Signed out from Torbear Left site No issues upon leaving | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Maple South Reservoir | WEST | Informed ROC. Onsite to perform annual maintenance/calibrations. Used calibration mode. Devices were done as below : Generator room LITs, RES_INLT1_AIT1, RES_INLT2_AIT1, RES_INLT2_AIT2 Took a multiple grab samples and adjusted analyzers accordingly. AL RES_INLT1_AIT1 A- 1.60 mg/l G- 1.62 mg/l AL RES_INLT2_AIT1 A - 1.62 mg/l G - 1.62 mg/l AL RES_INLT2_AIT2 A - 0.13 mg/l G - 0.13 mg/l Put all devices back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0013404 | 0 | 0
2026-02 | 2026-02-09 | Maple South Reservoir | WEST | On site to test isolation of MARS south cell, south inlet outlet piping for next stage of project works. Linear isolate Keele 900 PD6 isolation to South Cell at t0304-01 and T0564-01. Isolate pipe gallery interconnect valve, confirm isolation of 3? gv on washdown line. Install gauge on south cell inlet outlet air valve to monitor pressure after isolation. Currently at approximately 3psi. | FLAG | stage2_low_confidence | 0.023152 | ML: above threshold (no LLM available) — 0.023 |  | 0.023152 | 0 | 0
2026-02 | 2026-02-25 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 13:35 Verified Depolox (mg/L) Free: Grab 0.02, A 0.02 Total: Grab 2.70, A 2.62 13:45 #11620724 bact. sample | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040091 | 0 | 0
2026-02 | 2026-02-17 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 3:00 Verified Depolox (mg/L) Free: Grab 0.04, A 0.03 Total: Grab 2.86, A 2.83 3:10 #11605447 bact. & operational samples taken Depolox (new KI/distilled) OIT not working | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | not working [equipment_failure] | 0.0067603 | 0 | 0
2026-02 | 2026-02-11 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Station and equipment check Take weekly BacT sample W11589399 and grabs @ 13:15 Total: 2.68 mg/l Free: 0,02 mg/l *standardized analyzer to match grabs Reagents ok All other readings on PD sheets Utilized laptop for data entry ET ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051328 | 0 | 0
2026-02 | 2026-02-04 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Station and equipment check Take weekly BacT sample W11568241 and grabs @ 8:00 am Total: 2.80 mg/l Free: 0.03 mg/l Analyzer Total: 2.96 mg/l Analyzer Free: 0.03 mg/l *standardized analyzer to match grabs Reagents ok ET ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048782 | 0 | 0
2026-02 | 2026-02-03 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Attending site to check chlorine analyzer issue (W11634388). Found leaking at sample pump peristaltic tubing. Replaced all pump tubing and calibrated to 2.77mg/L Total chlorine based on average of three grabs. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.045836 | ML: above threshold (no LLM available) — 0.046 | leak [infrastructure]; leaking [infrastructure] | 0.045836 | 0 | 0
2026-02 | 2026-02-03 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Onsite to complete monthly maximo workorders Informed ROC (Angelica/Connor) Added acetate to Depolox 5 @ 9:00 am Took grabs to verify readings @ 9:10 am Total: 3.00 mg/l Free: 0.03 mg/l hihi analyzer reading came in at approximately 9:12 am possibly from acetate top up and air bubble Readings returned to normal Re took grabs @ 10:00 am Total: 2.80 mg/l Free: 0.02 mg/l *standardized analyzer to match grabs Completed all other workorders no issues ET ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055391 | 0 | 0
2026-02 | 2026-02-07 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Onsite to respond to riser pipe heat trace fault: Ensured continuous flow through riser pipe to prevent freezing Confirmed heat trace active- heater on at 100% No abnormalities with level trending Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0083682 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0083682 | 0 | 0
2026-02 | 2026-02-27 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Top up both Hypo day tanks Took grabs @ 1:45 pm from post (draining) Header Total: 3.30 mg/l Header Free: 0.05 mg/l Alll other readings on PD sheets Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050951 | 0 | 0
2026-02 | 2026-02-23 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Tank draining took grabs from post @ 13:10 Header Total: 3.26 mg/l Header Free: 0.05 mg/l Topped up both hypo day tanks Chemicals/reagents ok Contractor onsite backfilling previously excavated trench, no assistance required from ops Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067515 | 0 | 0
2026-02 | 2026-02-25 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no other issues found) Input data to pwq Verified CL17s (mg/l) Pre: (Header) Free: Grab 0.03, A 0.02 Total: Grab 1,73, A 1.74 Post: (Inlet) Free: Grab 0.03, A 0.02 Total: Grab 1.80, A 1.87 Ammonia Mixer #1 not working Ammonia Tank #2 (new batch) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | not working [equipment_failure] | 0.0057715 | 0 | 0
2026-02 | 2026-02-24 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Receive 350 L of Hypo Ops normal | FLAG | stage2_low_confidence | 0.0080382 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080382 | 0 | 0
2026-02 | 2026-02-02 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Tank filling at time of readings Grabs @ 9:15 am Inlet Total: 2.28 mg/l Inlet Free: 0.04 mg/l All other readings on PD sheets Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045994 | 0 | 0
2026-02 | 2026-02-18 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Informed ROC (Angelica) would be completing monthly Maximo workorders Place ALL analyzers in CAL mode and chemscan unit offline to conduct hot water flush of supply lines to analyzers Also turned manual OFF chlorine/ammonia pumps Tank currently filling Hot water flush from 8:15 am - 9:15 am Returned all analyzers to ?in service? aprox 9:30 am (all readings accurate) Wash down VC1 floor Tested sanitary hi level float ack/reset alarm Teated sanitary sump pumps both ok Visual inspection of hypo pumps and conducted drawdown of ammonia pumps after p1 failed to start (one off) all ok Ops normal | FLAG | stage2_low_confidence | 0.036549 | ML: above threshold (no LLM available) — 0.037 | failed [equipment_failure]; alarm [control_system] | 0.036549 | 0 | 0
2026-02 | 2026-02-13 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Contractor finished temporary domestic water service Opened mainstop at 1:15 pm and flushed temporary service for debris, ran clear right away with air gap Isolated service @ 1:30 pm so that plumber can tie into building services Opened mainstop @ 2:15 pm and flushed all building services for approximately 15 min, all ran clear Took grab @ 2:30 from sink in chlorine room Total: 2.70 mg/l Free: 0.05 mg/l Domestic water back in service Informed ROC Angelica eye wash station test and flush all ok Ops normal | FLAG | stage2_low_confidence | 0.01435 | ML: above threshold (no LLM available) — 0.014 |  | 0.01435 | 0 | 0
2026-02 | 2026-02-12 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to assist with flushing of temporary water service Opened curbstop at aprox. 8:45 am and found small leak at first coupling, turned back off Waiting on plumber Coupling tightened and failed leak test again, will require new coupling Water service remains OFF Ops otherwise normal | FLAG | stage2_low_confidence | 0.031133 | ML: above threshold (no LLM available) — 0.031 | failed [equipment_failure]; leak [infrastructure] | 0.031133 | 0 | 0
2026-02 | 2026-02-13 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Contractors onsite working on upgrades Took grabs from ?Post? as tank filling Inlet Total: 2.20 mg/l Inlet Free: 0.04 mg/l Reagents ok Topped up both hypo day tanks Topped up Ammonia tank 2 Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055162 | 0 | 0
2026-02 | 2026-02-20 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 1:34 PRE Free: Grab 0.04, A 0.01 Total: Grab 1.72, A 1.80 1:50 POST Free: Grab 0.03, A 0.04 Total: Grab 3.13, A 3.19 Ammonia tank #1 (new batch) (may have been switched prematurely (level high but ok)) Hypo tank #2 top up Contractor on site Chemscan (distilled top up) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025232 | 0 | 0
2026-02 | 2026-02-17 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s 12:46 Post/Header (Draining) Free: Grab 0.04, A 0.04 Total: Grab 3.20, A 3.19 12:51 Pre/Outlet (Draining) Free: Grab 0.03, A 0.01 Total: Grab 1.80, A 1.89 13:20 #11605447 bact. & operational samples taken Bulk Hypo delivery accepted | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030689 | 0 | 0
2026-02 | 2026-02-10 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to investigate w/ Ian W (PCS) problem with ups while running Kirby ps diesel generator. During transfer lose comms and analyzer readings Chemical system turned off during test and analyzer readings remained stable, may have to reload trending Could not find an issue with ups, may need new in the near future Complete Maximo workorders Receive Hypo delivery aprox 410 L Top up ammonia tank 1 Top up chemscan reagents as follows: grey, green and muriatic cleaning solution (red) Changed CL17 sc reagent ?inlet total? Removed garbage from site Waiting on update for temporary water service | FLAG | stage2_low_confidence | 0.02118 | ML: above threshold (no LLM available) — 0.021 |  | 0.02118 | 0 | 0
2026-02 | 2026-02-11 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Take weekly BacT sample W11589399 and grabs @ 10:20 am Sample tap Total: 1.69 mg/l Sample tap Free: 0.04 mg/l All other readings on PD sheets, no adjustments required on all analyzers Chemicals/reagents ok Contractors working onsite Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071296 | 0 | 0
2026-02 | 2026-02-05 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to assist contractor with sanitary repair, manually start/stop sump pumps as needed contractor finished repairs at aprox. 10:00 am Informed ROC (Connor S) will be completing maximo workorders Tank currently filling Cleaned all CL17 analyzers in Cal mode aprox.10:30 am - 11:30 am, readings stabilized to normal after clean Will verify readings at next station check Ops normal | FLAG | stage2_low_confidence | 0.024199 | ML: above threshold (no LLM available) — 0.024 | repair [maintenance_action] | 0.024199 | 0 | 0
2026-02 | 2026-02-04 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Take weekly BacT sample W11568241 and grabs from sample tap @ 10:50 am Total: 2.00 mg/l Free: 0.02 mg/l Draining between 17-20 L/s chemical system not active at time of readings Chemicals/reagents ok All other readings on PD sheets Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071085 | 0 | 0
2026-02 | 2026-02-06 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Took grabs and verified ALL CL17 analyzers due to yesterdays cleaning (24 hr stabilization) Inlet @ 13:20 Total: 2.00 mg/l Free: 0.02 mg/l No adjustments required Header @ 13:30 Total: 3.10 mg/l Free: 0.05 mg/l No adjustments required Topped up hypo tanks 1 and 2 Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034911 | 0 | 0
2026-02 | 2026-02-09 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Took grabs @ 10:20 am (filling) Inlet Total: 2.10 mg/l Inlet Free: 0.05 mg/l No adjustments required Changed CL17 reagent inlet free Topped up both hypo day tanks *Contractor onsite digging hit hydro line feeding chemical building @ approximately 10:45 am Informed ROC (Angelica) placed all chemical pumps manual Off and deactivated duty as could not monitor Level. Ian W (pcs) onsite to help with temporary generator hookup Temp power until hydro can be repaired, Verfied all analyzers @ 2:30 pm they are all accurate Ian W onsite until repair conplete | FLAG | stage2_low_confidence | 0.024345 | ML: above threshold (no LLM available) — 0.024 | repair [maintenance_action] | 0.024345 | 0 | 0
2026-02 | 2026-02-09 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to respond to comm failure to tank due to power lines being cut by contractors excavator. Placed PAC panel on generator power while repair was made. Transferred back to normal power one temporary repair was made. | FLAG | stage2_low_confidence | 0.097074 | ML: above threshold (no LLM available) — 0.097 | failure [equipment_failure]; repair [maintenance_action] | 0.097074 | 0 | 0
2026-02 | 2026-02-27 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site to complete station check. Site offline and secure. | FLAG | stage2_low_confidence | 0.013528 | ML: above threshold (no LLM available) — 0.014 |  | 0.013528 | 0 | 0
2026-02 | 2026-02-19 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | Under the direction of Ben Hess, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a Control panel. Provided 24 VDC power to new switch from 24VDC power supply. Pulled the fiber cables from Yorknet panel to control panel. Informed the ROC regarding possible comm fail alarm. After the replacement, checked all the ports and reset the comm alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-12 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site to complete station check with Christian B. Site offline and secure. | FLAG | stage2_low_confidence | 0.014603 | ML: above threshold (no LLM available) — 0.015 |  | 0.014603 | 0 | 0
2026-02 | 2026-02-19 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site for PMs. -Completed JHSC inspection. All good | FLAG | stage2_low_confidence | 0.009187 | ML: above threshold (no LLM available) — 0.009 |  | 0.009187 | 0 | 0
2026-02 | 2026-02-17 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site to perform station check. Site offline and secure. | FLAG | stage2_low_confidence | 0.013546 | ML: above threshold (no LLM available) — 0.014 |  | 0.013546 | 0 | 0
2026-02 | 2026-02-06 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site to complete station check with Christian B. Site offline and secure. | FLAG | stage2_low_confidence | 0.014603 | ML: above threshold (no LLM available) — 0.015 |  | 0.014603 | 0 | 0
2026-02 | 2026-02-24 | Newmarket (Northeast) Davis Drive Elevated Tank | CENTRAL | Onsite for station and equipment check All ok ET remains OFFLINE JHSC inspection complete no issues Ops normal | FLAG | stage2_low_confidence | 0.0087123 | ML: above threshold (no LLM available) — 0.009 |  | 0.0087123 | 0 | 0
2026-02 | 2026-02-12 | Newmarket (Northeast) Davis Drive Elevated Tank | CENTRAL | Station and equipment check ET remains OFFLINE Ops normal | FLAG | stage2_low_confidence | 0.0098372 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098372 | 0 | 0
2026-02 | 2026-02-05 | Newmarket (Northeast) Davis Drive Elevated Tank | CENTRAL | Station and equipment check ET remains OFFLINE No issues noted Ops normal | FLAG | stage2_low_confidence | 0.0088311 | ML: above threshold (no LLM available) — 0.009 |  | 0.0088311 | 0 | 0
2026-02 | 2026-02-25 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 14:15 Verified Depolox (mg/L) Free: Grab 0.05, A 0.07 Total: Grab 2.90, A 2.91 14:25 #11620724 bact. sample Portable generator returned and secured | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040043 | 0 | 0
2026-02 | 2026-02-02 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Responding to call from ROC (Adam B) Total chlorine hihi alarm On arrival took grabs @ 11:45 am Total: 2.80 mg/l Free: 0.05 mg/l Analyzer false reading due to low flow, adjusted prv to give flow to analyzer and readings returned to normal Will monitor ET ops normal | FLAG | stage2_low_confidence | 0.0073738 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073738 | 0 | 0
2026-02 | 2026-02-17 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 8:37 Verified Depolox (mg/L) (after instrumentation repair) Free: Grab 0.12, A 0.11 Total: Grab 2.69, A 2.19 (adjusted to match grabs) 8:56 #11605447 bact. and operational samples 10:10 Return for a High Free on the analyzer. (Performed zero cal and standard cal to 0.06mg/l to match grabs) | FLAG | stage2_low_confidence | 0.011475 | ML: above threshold (no LLM available) — 0.011 | repair [maintenance_action] | 0.011475 | 0 | 0
2026-02 | 2026-02-12 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Work orders #11603775 JHS #11604938 flood #11605125 heat tr #11605176 manual valves #11608067 port. gen (at HW ET) #11603736 Depolox maint. 9:45 verified (mg/l) Free: Grab 0.06, A 0.05 Total: Grab 3.00, A 3.23 (adjusted to match grabs) Acetate top up | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action] | flood [critical]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-11 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station and equipment check Take weekly BacT sample W11589399 and grabs @ 8:10 am Total: 2.90 mg/l Free: 0.04 mg/l As previously reported by oncall operator analyzer reading hihi on total. Analyzer Total: 3.48 mg/l Analyzer Free: 0.04 mg/l *standardized analyzer back down to match grabs, will monitor Reagents ok ET ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063848 | 0 | 0
2026-02 | 2026-02-17 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Onsite to troubleshoot Hi-Hi total & combined chlorine readings. Informed ROC. Put the device in calibration mode. Noticed that there was no flow to the chlorine analyzer causing false HI-HI total and combined chlorine readings. Found the problem with the PRV at the sample inlet. Removed it from the process and dismantled it. Cleaned it and relubricated all the gaskets and fittings. Put the PRV back in the process and checked for the flow. No issues. Put the analyzer back in service. Readings came back to normal. All the related alarms were cleared. Joe Williams took a grab samples adjusted the analyzer. Informed ROC and left the site. | FLAG | stage2_low_confidence | 0.029488 | ML: above threshold (no LLM available) — 0.029 | alarm [control_system]; alarms [control_system] | 0.029488 | 0 | 0
2026-02 | 2026-02-17 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | -Responded HiHi combine chlorine residual - upon arrival analyzer reading total=9.99mg/L - performed grab test total=2.98mg/L - checked the analyzer - noticed no sample flow to the total analyzer - called instrument technician on call Parth P. - he will come to clean the pressure sustaining valve first thing in the morning - reviewed trends - the total chlorine at the upstream, Aurora South Reservoir, is always around 3.20mg/L - the hihi total analyzer reading is a false reading - not reportable | FLAG | stage2_low_confidence | 0.081781 | ML: above threshold (no LLM available) — 0.082 |  | 0.081781 | 0 | 0
2026-02 | 2026-02-04 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station and equipment check Take weekly BacT sample W11568214 and grabs @ 9:05 am Total: 2.93 mg/l Free: 0.05 mg/l Analyzer readings matched grabs, reagents ok ET ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065067 | 0 | 0
2026-02 | 2026-02-26 | Newmarket (West) Bathurst Tank | CENTRAL | Work Orders #11607360 Depolox maint (new reagents, & electrolyte top up) 11:25 Verified (mg/l) Free: Grab 0.05, A 0.05 Total: Grab 1.80, A 1.74 #11607476 jhs #11608497 Dechlor Sump pump not running (found tripped breaker (#16), reset and runs) | FLAG | stage2_low_confidence | 0.025818 | ML: above threshold (no LLM available) — 0.026 | tripped [equipment_failure]; trip [equipment_failure]; not running [equipment_failure]; work order [maintenance_action]; pump not running [infrastructure] | 0.025818 | 0 | 0
2026-02 | 2026-02-25 | Newmarket (West) Bathurst Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 12:40 Verified Depolox (mg/L) Free: Grab 0.06, A 0.06 Total: Grab 2.88, A 2.90 Depolox (New acetate jug) 12:50 #11620724 bact. sample | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037718 | 0 | 0
2026-02 | 2026-02-02 | Newmarket (West) Bathurst Tank | CENTRAL | Onsite to trial isolate bathurst tank while feeding water from Orchard Heights ET. Isolated bathurst tank at 10:35 am Reversed the isolation of bathurst tank at 12:05, tank back into service. Station ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006002 | 0 | 0
2026-02 | 2026-02-17 | Newmarket (West) Bathurst Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 11:30 Verified Depolox (mg/L) Free: Grab 0.05, A 0.06 Total: Grab 2.72, A 2.77 Depolox (Acetate & Electrolyte top up) 11:45 #11605447 bact. & operational samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042848 | 0 | 0
2026-02 | 2026-02-04 | Newmarket (West) Bathurst Tank | CENTRAL | Station and equipment check Take weekly BacT sample W11568214 and grabs @ 10:05 am from Outlet sample tap Total: 2.80 mg/l Free: 0.05 mg/l No adjustments necessary, reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069635 | 0 | 0
2026-02 | 2026-02-11 | Newmarket (West) Bathurst Tank | CENTRAL | Station and equipment check Take weekly BacT sample W11589399 and grabs @ 9:10 am Total: 2.77 mg/l Free: 0.05 mg/l Analyzer Total: 2.72 mg/l Analyzer Free: 0.06 mg/l Reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048527 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check All ops normal | FLAG | stage2_low_confidence | 0.010978 | ML: above threshold (no LLM available) — 0.011 |  | 0.010978 | 0 | 0
2026-02 | 2026-02-27 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check Ops normal | FLAG | stage2_low_confidence | 0.010753 | ML: above threshold (no LLM available) — 0.011 |  | 0.010753 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Kirby Pumping Station | CENTRAL | Restarted the Operator Interface Terminal due to Windows OS updates. The Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.0088279 | ML: above threshold (no LLM available) — 0.009 |  | 0.0088279 | 0 | 0
2026-02 | 2026-02-02 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check Suction pressure: 75 kPa Discharge pressure: 334 kPa Flow: 20 L/s Tank level: 50% All pumps available Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005333 | 0 | 0
2026-02 | 2026-02-20 | Newmarket Kirby Pumping Station | CENTRAL | Station Check (no issues found) Input data to PWQ | FLAG | stage2_low_confidence | 0.011449 | ML: above threshold (no LLM available) — 0.011 |  | 0.011449 | 0 | 0
2026-02 | 2026-02-12 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check All pumps available FCV: 17% @ 19.9 L/s Ops normal *security aware swipe card not working | FLAG | stage2_low_confidence | 0.012134 | ML: above threshold (no LLM available) — 0.012 | not working [equipment_failure] | 0.012134 | 0 | 0
2026-02 | 2026-02-18 | Newmarket Kirby Pumping Station | CENTRAL | Station check (no issues found) Input data to PWQ | FLAG | stage2_low_confidence | 0.011449 | ML: above threshold (no LLM available) — 0.011 |  | 0.011449 | 0 | 0
2026-02 | 2026-02-06 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check All ok No issues Duty not active Ops normal | FLAG | stage2_low_confidence | 0.0072977 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072977 | 0 | 0
2026-02 | 2026-02-10 | Newmarket Kirby Pumping Station | CENTRAL | Onsite to complete monthly Maximo workorders Diesel test run, ran ok Stop hours: 33.40 On transfer lost analyzers in chemical building PCS Ian W on way to investigate Will log into chemical building elog Also swipe cards not working around station or chemical building, CPD looking into issue Pump station otherwise ok | FLAG | stage2_low_confidence | 0.02218 | ML: above threshold (no LLM available) — 0.022 | not working [equipment_failure] | 0.02218 | 0 | 0
2026-02 | 2026-02-09 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check Ops normal Duty 1 active FCV 17% All pumps standby and ready All ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062208 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 9:48 Grab: 2.64 mg/L Analyzer: 2.67 mg/L Effluent Free Chlorine @ 9:41 Grab: 2.72 mg/L Analyzer: 2.67 mg/L Treated Free Chlorine @ 9:37 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 9:37 Grab: 3.04 mg/L Analyzer: 3.07 mg/L -Placed well 15 in manual-on -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00083807 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Well 1 & 2 | CENTRAL | Changed reagents for effluent free and treated free chlorine analyzers | FLAG | stage2_low_confidence | 0.015032 | ML: above threshold (no LLM available) — 0.015 |  | 0.015032 | 0 | 0
2026-02 | 2026-02-25 | Newmarket Well 1 & 2 | CENTRAL | On site with Christian B to complete station check and weekly bacti samples (W11619950). -Verified analyzers: Influent Free Chlorine @ 9:54 Grab: 2.54 mg/L Analyzer: 2.63 mg/L Effluent Free Chlorine @ 9:58 Grab: 2.60 mg/L Analyzer: 2.62 mg/L Treated Free Chlorine @ 10:02 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 10:05 Grab: 2.90 mg/L Analyzer: 3.02 mg/L -Entered data into PD Sheet -Checked trends -Topped up Well 2 mineral oil -Returned wells to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00092623 | 0 | 0
2026-02 | 2026-02-24 | Newmarket Well 1 & 2 | CENTRAL | Deliver 1.5 load of silicate Alex B onsite | FLAG | stage2_low_confidence | 0.008468 | ML: above threshold (no LLM available) — 0.008 |  | 0.008468 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Well 1 & 2 | CENTRAL | Attending site for silicate pump 1 uncommanded stop (W11683625). Cycled power on pump which tripped the circuit breaker. Tried again and the breaker tripped again. Replaced pump and configured. Performed drawdown and entered 240mL/min as maximum pump output in SCADA. Left pump#1 in duty 1 to test performance. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.10736 | ML: above threshold (no LLM available) — 0.107 | tripped [equipment_failure]; trip [equipment_failure]; scada [control_system] | 0.10736 | 0 | 0
2026-02 | 2026-02-24 | Newmarket Well 1 & 2 | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Completed JHSC inspection: all good -Completed ammonia system inspection: flood alarm functional, performed drawdowns: pump 2 max flow setpoint on SCADA changed from 200 to 190 mL/min -Deactivated duty, placed wells in manual-off to complete PMs -Completed chlorine leak detection test: all good -Completed chlorine system inspection: Prior to work, added dechlor to waste chamber and opened waste valve slightly. Returned system to normal after work completed. All good. -Completed CL17 chlorine analyzer maintenance and verified as follows: Influent Free Chlorine @ 12:58 Grab: 2.54 mg/L Analyzer: 2.55 mg/L Effluent Free Chlorine @ 12:53 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Free Chlorine @ 12:44 Grab: 0.07 mg/L Analyzer: 0.09 mg/L Treated Total Chlorine @ 12:44 Grab: 2.62 mg/L Analyzer: 2.56 mg/L Exit button on influent free CL17 nonfunctional ? Restarted analyzer after cleaning via power cycle. Created WO W11688098 for instrumentation to address fixing the button. -Returned wells to auto | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | flood [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-26 | Newmarket Well 1 & 2 | CENTRAL | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Placed wells in manual-off -Performed maintenance on well 1 deep well exhaust valve -Performed maintenance on well 2 deep well exhaust valve -Performed maintenance on and calibrated turbidimeter. Analyzer read 0.039 NTU afterwards. -Performed maintenance on and inspection of silicate system. Placed well 2 in local, well 1 in manual. Added dechlor to waste chamber, opened waste valve slightly. Ran hot water flush through chemical board and lines. Isolated influent side of contact tank and depressurized raw main. Pulled and cleaned injection points. Performed drawdowns. Pump 1 SCADA max flow setpoint changed from 240 to 220 mL/min. -Placed wells in manual-on to test silicate dosing. Activated area duty. Lo total and combined chlorine alarm and effluent lo alarm during well startup due to having drawn back distribution water via opened waste valve during all silicate work. Switched silicate pumps at 14:29. Silicate dosing all good. -Topped up ammonia tank 1 -Returned wells to auto | FLAG | stage2_low_confidence | 0.18102 | ML: above threshold (no LLM available) — 0.181 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.18102 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Well 1 & 2 | CENTRAL | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off during the updates and the Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.010733 | ML: above threshold (no LLM available) — 0.011 |  | 0.010733 | 0 | 0
2026-02 | 2026-02-27 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 11:36 Grab: 2.70 mg/L Analyzer: 2.74 mg/L Effluent Free Chlorine @ 11:33 Grab: 2.42 mg/L Analyzer: 2.34 mg/L Treated Free Chlorine @ 11:30 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:30 Grab: 2.64 mg/L Analyzer: 2.66 mg/L -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00077506 | 0 | 0
2026-02 | 2026-02-02 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check with Christian B. -Placed wells in manual-on for duration of work -Verified analyzers: Influent Free Chlorine @ 9:29 Grab: 2.52 mg/L Analyzer: 2.56 mg/L Effluent Free Chlorine @ 9:26 Grab: 2.58 mg/L Analyzer: 2.57 mg/L Treated Free Chlorine @ 9:22 Grab: 0.15 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:22 Grab: 2.92 mg/L Analyzer: 3.00 mg/L -Entered data into PD sheet -Checked trends -Returned wells to auto -Placed wells 13/16 in manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00064248 | 0 | 0
2026-02 | 2026-02-10 | Newmarket Well 1 & 2 | CENTRAL | Silicate Top Up Before: 38.6cm/350.0L After: 101.0cm/916.0L | FLAG | stage2_low_confidence | 0.0075934 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075934 | 0 | 0
2026-02 | 2026-02-13 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 10:53 Grab: 2.52 mg/L Analyzer: 2.45 mg/L Effluent Free Chlorine @ 10:48 Grab: 2.62 mg/L Analyzer: 2.59 mg/L Treated Free Chlorine @ 10:43 Grab: 0.10 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:43 Grab: 2.94 mg/L Analyzer: 2.97 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 1 -Topped up well 2 mineral oil | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00076214 | 0 | 0
2026-02 | 2026-02-17 | Newmarket Well 1 & 2 | CENTRAL | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Placed wells in manual, added dechlor to waste chamber. Opened waste valve slightly -Found SCADA speed deviation issue with silicate pump 1, created WO W11670844 for instrumentation -Ran hot water flush through silicate pump and injection point 2. Reprimed line with silicate after. Ended flow to waste valve | FLAG | stage2_low_confidence | 0.029351 | ML: above threshold (no LLM available) — 0.029 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.029351 | 0 | 0
2026-02 | 2026-02-17 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check with Christian B and collect weekly bacti samples (W11606270). -Placed wells in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 10:26 Grab: 2.60 mg/L Analyzer: 2.58 mg/L Effluent Free Chlorine @ 10:31 Grab: 2.54 mg/L Analyzer: 2.58 mg/L Treated Free Chlorine @ 10:34 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 10:38 Grab: 2.88 mg/L Analyzer: 2.96 mg/L -Placed NMW15 in manual, returned NMW12 to auto -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010032 | 0 | 0
2026-02 | 2026-02-19 | Newmarket Well 1 & 2 | CENTRAL | Attending site to check silicate pump#1 - SCADA speed control not working (W11670844). - Found pump input/output module not responding to speed reference signal injected directly from a digital multimeter. Replaced I/O module. - Found that after I/O module replacement, pump was able to be controlled from a multimeter but was still not able to follow speed command from SCADA. Found speed reference wiring leaving PAC panel was not connected correctly and completely loose. Re-terminated wire and checked all other analog outputs on that card for correct termination. Suspect that intermittent connection to pump had caused the pump I/O module to fail. - Once pump was able to be controlled by SCADA, found that pump would not discharge silicate - even with very little back pressure. - Replaced pump roller with a used spare part, which corrected the issue, and was able to perform drawdowns on pump#1. - Entered pump#1 maximum flow of 210 mL/min, as determined by drawdown tests. - Left silicate pump#1 in duty#1. - Notified Ben Hess and Alex Bell ROC was notified before and after maintenance activities. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; not responding [equipment_failure]; not working [equipment_failure]; scada [control_system] | oos [equipment_failure]; not responding [equipment_failure]; not working [equipment_failure]; scada [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check with Christian B and collect weekly bacti samples W11588614. -Verified analyzers: Influent Free Chlorine @ 14:27 Grab: 2.66 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 14:24 Grab: 2.42 mg/L Analyzer: 2.39 mg/L Treated Free Chlorine @ 14:21 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 14:21 Grab: 2.84 mg/L Analyzer: 2.88 mg/L -Entered data into PD sheet -Checked trends -Returned wells 1/2 to auto -Returned well 15 to auto after confirming silicate injection point 1 dosing effectively | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012733 | 0 | 0
2026-02 | 2026-02-20 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 9:12 Grab: 2.64 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 9:09 Grab: 2.60 mg/L Analyzer: 2.59 mg/L Treated Free Chlorine @ 9:06 Grab: 0.15 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:06 Grab: 3.00 mg/L Analyzer: 2.95 mg/L -Topped up ammonia tank 2 -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00072063 | 0 | 0
2026-02 | 2026-02-10 | Newmarket Well 1 & 2 | CENTRAL | turbidity spike went above 0.200 NTU rotated silicate P2 into duty 1. Silicate P1 OOS until operator can troubleshoot | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-18 | Newmarket Well 1 & 2 | CENTRAL | Changed chlorine cylinder bank A with Joe Williams. | FLAG | stage2_low_confidence | 0.01389 | ML: above threshold (no LLM available) — 0.014 |  | 0.01389 | 0 | 0
2026-02 | 2026-02-04 | Newmarket Well 1 & 2 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 0 bags of ammonia in inventory Weekly bacti samples taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0829 G:2.72 A:2.61mg/L Effluent Free@0835 G:2.46 A:2.56mg/L Treated Free@0836 G:0.14 A:0.13mg/L Treated Total@0839 G:2.96 A:2.96mg/L Mono-2.50 FA-0.04 TA-0.54 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040019 | 0 | 0
2026-02 | 2026-02-09 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check and address silicate pump 1 leak alarm. -Verified analyzers: Influent Free Chlorine @ 10:15 Grab: 2.54 mg/L Analyzer: 2.55 mg/L Effluent Free Chlorine @ 10:12 Grab: 2.74 mg/L Analyzer: 2.69 mg/L Treated Free Chlorine @ 9:57 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:57 Grab: 3.06 mg/L Analyzer: 3.01 mg/L -Entered data into PD sheet -Checked trends -Replaced tubing for and cleaned silicate pump 1. Ran hot water through chemical board to loosen PRV and PSV. Performed drawdown, SCADA max flow setpoint changed from 180 mg/L to 220 mg/L. Observed pressure was normal through injection point when running to system briefly. Returned silicate pump 1 to auto. Observed silicate pump pressure while wells running. Confirmed effective dosing. | FLAG | stage2_low_confidence | 0.012684 | ML: above threshold (no LLM available) — 0.013 | oos [equipment_failure]; scada [control_system]; alarm [control_system]; leak [infrastructure] | 0.012684 | 0 | 0
2026-02 | 2026-02-06 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 10:53 Grab: 2.64 mg/L Analyzer: 2.59 mg/L Effluent Free Chlorine @ 10:59 Grab: 2.62 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 11:04 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 11:09 Grab: 3.08 mg/L Analyzer: 2.97 mg/L -Changed influent free chlorine analyzer reagents -Topped up ammonia tank 2 -Changed cylinder bank B with Will M. -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00081943 | 0 | 0
2026-02 | 2026-02-26 | Newmarket Well 14 | CENTRAL | #11624577 main flushed for 90mins. | FLAG | stage2_low_confidence | 0.0098053 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098053 | 0 | 0
2026-02 | 2026-02-19 | Newmarket Well 14 | CENTRAL | Onsite for station check. Tower offline. Building secure. No issues. | FLAG | stage2_low_confidence | 0.012407 | ML: above threshold (no LLM available) — 0.012 |  | 0.012407 | 0 | 0
2026-02 | 2026-02-25 | Newmarket Well No. 15 | CENTRAL | On site with Dan Boate to investigate possible well motor overheating. Well running upon arrival. ROC contacted to stop well pump and notified about work being conducted. Well de-energized. Found motor operating within nameplate temperature and current range. Reenergized motor and returned to normal operation. ROC notified. | FLAG | stage2_low_confidence | 0.010557 | ML: above threshold (no LLM available) — 0.011 |  | 0.010557 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Well No. 15 | CENTRAL | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 10:57 Grab: 2.86 mg/L Analyzer: 2.89 mg/L Effluent Free Chlorine @ 10:52 Grab: 2.82 mg/L Analyzer: 2.86 mg/L Treated Free Chlorine @ 10:44 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:05 Grab: 3.46 mg/L Analyzer: 3.56 mg/L Adjusted analyzer to match average of 3 grabs. Analyzer read 3.44mg/L afterwards. -Replaced Influent free chlorine CL17 analyzer reagents -Returned well to auto -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010859 | 0 | 0
2026-02 | 2026-02-24 | Newmarket Well No. 15 | CENTRAL | On site to reprime silicate lines after they ran dry due to low chemical storage. Notified ROC of relevant alarms. -Placed dechlor in waste chamber, opened waste valve slightly -Identified silicate injection point 1 check valve was completely passing -Switched to injection point 2, ran both silicate pumps manually -Placed well in manual-on to observe silicate dosing -Returned wells to auto after confirming injection point 2 works | FLAG | stage2_low_confidence | 0.024287 | ML: above threshold (no LLM available) — 0.024 | alarm [control_system]; alarms [control_system] | 0.024287 | 0 | 0
2026-02 | 2026-02-19 | Newmarket Well No. 15 | CENTRAL | Under the direction of Ben Hess, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a Control panel. Provided 24 VDC power to new switch from 24VDC power supply. Pulled the fiber cables from Yorknet panel to control panel. Informed the ROC regarding possible comm fail alarm. Well were Manual off. After the replacement, checked all the ports and reset the comm alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-23 | Newmarket Well No. 15 | CENTRAL | Restarted the Operator Interface Terminal due to Windows OS updates. The well was off during the updates and the Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.010631 | ML: above threshold (no LLM available) — 0.011 |  | 0.010631 | 0 | 0
2026-02 | 2026-02-27 | Newmarket Well No. 15 | CENTRAL | On site to complete station check. -Put well into manual -Verified analyzers: Influent Free Chlorine @ 12:30 Grab: 3.02 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 12:25 Grab: 2.84 mg/L Analyzer: 2.86 mg/L Treated Free Chlorine @ 12:21 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:21 Grab: 3.32 mg/L Analyzer: 3.40 mg/L -Entered data into PD Sheet -Checked trends -Topped up well 15 mineral oil -Put well back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00054733 | 0 | 0
2026-02 | 2026-02-25 | Newmarket Well No. 15 | CENTRAL | On site with Christian B to complete station check and weekly bacti samples (W11619950). -Put well into manual-on -Verified analyzers: Influent Free Chlorine @ 11:24 Grab: 2.96 mg/L Analyzer: 2.92 mg/L Effluent Free Chlorine @ 11:27 Grab: 2.48 mg/L Analyzer: 2.59 mg/L Treated Free Chlorine @ 11:31 Grab: 0.14 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 11:34 Grab: 3.20 mg/L Analyzer: 3.29 mg/L -Entered data into PD Sheet -Checked trends -Changed chlorine bank B with Will M -Put well back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00075955 | 0 | 0
2026-02 | 2026-02-24 | Newmarket Well No. 15 | CENTRAL | Silicate Fill 85.8 L to 384 L Also slight drip from silicate injection point 1, was able to stop drip keep an eye Ops normal Well manual off for now | FLAG | stage2_low_confidence | 0.015348 | ML: above threshold (no LLM available) — 0.015 | drip [infrastructure] | 0.015348 | 0 | 0
2026-02 | 2026-02-02 | Newmarket Well No. 15 | CENTRAL | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 10:53 Grab: 2.52 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 11:06 Grab: 0.02mg/L Analyzer: 0.03 mg/L Treated Free Chlorine @ 11:16 Grab: 0.01 mg/L Analyzer: 0.01mg/L Treated Total Chlorine @ 11:23 Grab: 1.22 mg/L Analyzer: 1.24 mg/L Responded to high turbidity alarm. -Well in manual off. Placed well in local. Added dechlor to waste chamber. Isolated contact chamber on influent side. Depressurized raw main. Cleaned silicate injection points. Repressurized raw main. Tested silicate pumps to sight glass ? pump 2 good, pump 1 issue with drawing silicate from tank. Reprimed silicate injection lines via pump 2. Ran well in manual testing both injection points sequentially. Injection point 1 left in service. Neither dosed as well as would be expected, further troubleshooting needed. -Returned well to auto -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065739 | 0 | 0
2026-02 | 2026-02-10 | Newmarket Well No. 15 | CENTRAL | turbidity went hi while silicate P2 was running. Silicate P1 already OOS. Put well to manual off until operator can troubleshoot silicate P1 and P2. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-11 | Newmarket Well No. 15 | CENTRAL | On site to complete station check, collect weekly bacti samples (W11588614), and troubleshoot silicate dosing problems with Christian B. ?Placed well in local. Added dechlor to waste chamber. Depressurized raw main by isolating influent side of contact tank and opening waste valve. Pulled and cleaned injection points. Lo and Lolo influent chlorine alarms caused by loss of flow to analyzer from isolating on influent side of contact tank. Ran hot water through chemical board to loosen PRV and PSV, ran through injection points. Cleaned foot valves. Raised silicate supply lines up from bottom of tank. Performed drawdowns, SCADA max flow setpoints not changed. Repressurized raw main and primed silicate injection points while backflushing slightly to waste. Placed silicate pumps back in auto. Placed well 15 back in manual. Turned well 15 on to confirm effective dosing. -Turned Newmarket well 13 on for Will M. to complete sampling -Topped up ammonia tank 1 -Verified analyzers: Influent Free Chlorine @ 13:16 Grab: 2.78 mg/L Analyzer: 2.81 mg/L Effluent Free Chlorine @ 13:19 Grab: 2.62 mg/L Analyzer: 2.56 mg/L Treated Free Chlorine @ 13:25 Grab: 0.14 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 13:29 Grab: 3.14 mg/L Analyzer: 3.17 mg/L -Put Newmarket wells 1/2 in manual-on -Switched to injection point 1 @ 13:54 after confirming injection point 2 doses effectively -Entered data into PD sheet -Checked trends | FLAG | stage2_low_confidence | 0.036352 | ML: above threshold (no LLM available) — 0.036 | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.036352 | 0 | 0
2026-02 | 2026-02-10 | Newmarket Well No. 15 | CENTRAL | Silicate Top Up Before: 32.7cm/149.0L After: 84.2cm/384.0L | FLAG | stage2_low_confidence | 0.0075593 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075593 | 0 | 0
2026-02 | 2026-02-17 | Newmarket Well No. 15 | CENTRAL | On site to complete station check with Christian B and collect weekly bacti samples (W11606270). -Verified analyzers: Influent Free Chlorine @ 11:21 Grab: 3.02 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 11:24 Grab: 3.00 mg/L Analyzer: 2.88 mg/L Treated Free Chlorine @ 11:27 Grab: 0.13 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:30 Grab: 3.41 mg/L Analyzer: 3.36 mg/L -Topped up mineral oil for well 15 -Returned well to auto -Completed JHSC inspection: all good -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00097264 | 0 | 0
2026-02 | 2026-02-10 | Newmarket Well No. 15 | CENTRAL | On site to complete station check with Christian B. -Placed well in manual for duration of check -Verified analyzers: Influent Free Chlorine @ 8:52 Grab: 2.60 mg/L Analyzer: 2.58 mg/L Effluent Free Chlorine @ 8:49 Grab: 0.15 mg/L Analyzer: 0.13 mg/L Treated Free Chlorine @ 8:46 Grab: 0.04 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 8:46 Grab: 2.68 mg/L Analyzer: 2.77 mg/L -Topped up mineral oil well 15 -Entered data into PD sheet -Checked trends -Returned well 15 to auto -Placed well 16 in manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00073162 | 0 | 0
2026-02 | 2026-02-18 | Newmarket Well No. 15 | CENTRAL | Attending site to check chlorine analyzer fault (W11674000). Analyzer had a motor error. Replaced optical sensor. Verified reading at 1.82 mg/L Total. Analyzer reading 1.76mg/L. Adjusted analyzer to 1.82mg/L Total, based on 3 dpd grabs. Placed well back to Auto, as requested by Alex Bell. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.038552 | ML: above threshold (no LLM available) — 0.039 | fault [equipment_failure] | 0.038552 | 0 | 0
2026-02 | 2026-02-13 | Newmarket Well No. 15 | CENTRAL | On site to complete station check with Christian B. -Placed Newmarket well 13 in duty 1 and Newmarket well 16 in duty 2 -Verified analyzers: Influent Free Chlorine @ 13:16 Grab: 2.78 mg/L Analyzer: 2.81 mg/L Effluent Free Chlorine @ 13:19 Grab: 2.62 mg/L Analyzer: 2.56 mg/L Treated Free Chlorine @ 13:25 Grab: 0.14 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 13:29 Grab: 3.14 mg/L Analyzer: 3.17 mg/L -Changed reagents for treated free and treated total chlorine analyzers -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00092768 | 0 | 0
2026-02 | 2026-02-19 | Newmarket Well No. 15 | CENTRAL | Attending site to check Influent Free chlorine analyzer buttons (W11673928). Replaced all push buttons as existing ones were not functioning. Verified readings after maintenance work - analyzer did not require any adjustments. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.032048 | ML: above threshold (no LLM available) — 0.032 |  | 0.032048 | 0 | 0
2026-02 | 2026-02-18 | Newmarket Well No. 15 | CENTRAL | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Inspected ammonia system, performed pump drawdowns and tested flood alarm; all good -Placed well in manual-off -Inspected chlorine system: added dechlor to waste chamber and performed inspection while waste valve slightly open. System operating well ? vacuum releasing slightly fast, so made W11673879 to revisit in a few weeks and reassess -Performed maintenance on and calibrated turbidimeter. Analyzer read 0.050 NTU afterwards. -Performed maintenance on CL17 analyzers Verified analyzers: Influent Free Chlorine @ 12:05 Grab: 2.70 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 12:08 Grab: 0.17 mg/L Analyzer: 0.17 mg/L Treated Free Chlorine @ 12:11 Grab: 0.08 mg/L Analyzer: 0.08 mg/L Could not verify treated total analyzer due to persistent motor error. Contacted Eric S from instrumentation who is on his way to troubleshoot. Treated and Combined lo and lolo alarms are thus caused by analyzer error. Leaving well in manual-off and notifying ROC. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | Newmarket Well No. 15 | CENTRAL | On site to complete station check. -Placed well in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 10:31 Grab: 3.04 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 10:26 Grab: 2.82 mg/L Analyzer: 2.75 mg/L Treated Free Chlorine @ 10:19 Grab: 0.12 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 10:19 Grab: 3.44 mg/L Analyzer: 3.44 mg/L -Topped up ammonia tank 2 -Returned well to auto -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00060547 | 0 | 0
2026-02 | 2026-02-19 | Newmarket Well No. 15 | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Completed chlorine leak detection test: all good -Inspected and performed maintenance on deep well exhaust valve: all good | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; leak [infrastructure] | alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-04 | Newmarket Well No. 15 | CENTRAL | On-site for a station and equipment check No issues found. Chemical levels and systems ok 6 cylinders and 4 bags of ammonia in inventory Weekly bacti samples taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0928 G:2.90 A:2.92mg/L Effluent Free@0932 G:2.94 A:2.89mg/L Treated Free@0936 G:0.18 A:0.14mg/L Treated Total@0939 G:3.44 A:3.34mg/L Mono-2.91 FA-0.04 TA-0.62 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040019 | 0 | 0
2026-02 | 2026-02-25 | Newmarket Wells 13-16 | CENTRAL | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Added dechlor to well 13 waste chamber -Performed chlorine inspection: all good except water noticed in chlorinator 2 vacuum gauge, created WO -Performed well 13 PRV inspection and maintenance: used PRV to backflush slightly to minimize excess chlorine from chlorine inspection -Inspected well 13 deep well exhaust valve and reviewed operations via trends and inspection during other station checks -Returned well 13 to auto | FLAG | stage2_low_confidence | 0.033172 | ML: above threshold (no LLM available) — 0.033 | alarm [control_system]; alarms [control_system] | 0.033172 | 0 | 0
2026-02 | 2026-02-25 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check with Christian B and collect weekly bacti samples (W11619950). -Topped up ammonia tank 2 -Topped up well 13 mineral oil -Verified analyzers: Influent Free Chlorine @ 8:08 Grab: 2.80 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 8:05 Grab: 2.38 mg/L Analyzer: 2.40 mg/L Treated Free Chlorine @ 8:01 Grab: 0.08 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 8:01 Grab: 2.70 mg/L Analyzer: 2.73 mg/L -Performed drawdown, changed ammonia pump 2 SCADA max flow setpoint from 230 to 220 mL/min due to low free ammonia SL1000 grabs -Placed wells 1 and 2 in manual -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0015081 | 0 | 0
2026-02 | 2026-02-27 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 14:25 Grab: 2.40 mg/L Analyzer: 2.43 mg/L Effluent Free Chlorine @ 14:22 Grab: 0.13 mg/L Analyzer: 0.15 mg/L Treated Free Chlorine @ 14:17 Grab: 0.10 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 14:17 Grab: 2.40 mg/L Analyzer: 2.32 mg/L -Replaced reagents for influent free and treated total chlorine analyzers -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00090121 | 0 | 0
2026-02 | 2026-02-24 | Newmarket Wells 13-16 | CENTRAL | Silicate load 1648 L - 2527 L Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058313 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Wells 13-16 | CENTRAL | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off during the updates and the Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.010733 | ML: above threshold (no LLM available) — 0.011 |  | 0.010733 | 0 | 0
2026-02 | 2026-02-24 | Newmarket Wells 13-16 | CENTRAL | Attending site to check Treated Free chlorine analyzer analog output (W11664335). Adjusted Treated Free analog output so that SCADA better matches the analyzer display value. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.031714 | ML: above threshold (no LLM available) — 0.032 | scada [control_system] | 0.031714 | 0 | 0
2026-02 | 2026-02-02 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 8:39 Grab: 2.70 mg/L Analyzer: 2.72 mg/L Effluent Free Chlorine @ 8:35 Grab: 2.46 mg/L Analyzer: 2.45 mg/L Treated Free Chlorine @ 8:29 Grab: 0.11 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 8:29 Grab: 2.82 mg/L Analyzer: 2.79 mg/L -Took pH raw sample for well 13 -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00080327 | 0 | 0
2026-02 | 2026-02-23 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 8:34 Grab: 2.76 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 8:31 Grab: 2.42 mg/L Analyzer: 2.38 mg/L Treated Free Chlorine @ 8:28 Grab: 0.07 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 8:28 Grab: 2.80 mg/L Analyzer: 2.72 mg/L -Changed treated free chlorine analyzer reagents -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00091329 | 0 | 0
2026-02 | 2026-02-02 | Newmarket Wells 13-16 | CENTRAL | Returned wells to auto. Water Resources on site. | FLAG | stage2_low_confidence | 0.012884 | ML: above threshold (no LLM available) — 0.013 |  | 0.012884 | 0 | 0
2026-02 | 2026-02-20 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 8:08 Grab: 2.62 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 8:05 Grab: 2.40 mg/L Analyzer: 2.39 mg/L Treated Free Chlorine @ 8:02 Grab: 0.11 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 8:02 Grab: 2.78 mg/L Analyzer: 2.70 mg/L -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00076323 | 0 | 0
2026-02 | 2026-02-10 | Newmarket Wells 13-16 | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Placed wells in manual-off -Performed chlorine gas detector test: all good -Performed turbidimeter analyzer maintenance and calibrated using standard. Read 0.046 NTU afterwards. -Performed CL17 chlorine analyzer maintenance, verified analyzers afterwards: Influent Free Chlorine @ 11:17 Grab: 2.42 mg/L Analyzer: 2.46 mg/L Effluent Free Chlorine @ 11:14 Grab: 1.32 mg/L Analyzer: 1.36 mg/L Treated Free Chlorine @ 11:20 Grab: 0.02 mg/L Analyzer: 0.05 mg/L Treated Total Chlorine @ 11:20 Grab: 2.46 mg/L Analyzer: 2.44 mg/L -Performed JHSC inspection: all good -Returned well 16 to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0019961 | 0 | 0
2026-02 | 2026-02-17 | Newmarket Wells 13-16 | CENTRAL | On site to disconnect Well 16 motor. ROC notified. Well 16 starter locked/tagged out. Motor feeder and level probe disconnected. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066417 | 0 | 0
2026-02 | 2026-02-17 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check with Christian B and collect weekly bacti samples (W11606270). -Placed well 16 in manual. Electricians Kyle and Sean on site, locked out well 16 electrically. I isolated well 16 via valve 00041307, LOTO?d the valve. Isolated FCV (00041305) bonnet via two ball valves on the FCV. Placed LOTO tag and made visually obvious via a sign. Added dechlor to waste chamber and opened waste valve to depressurize main and confirm full isolation. Reported LOTO to other central operators. -Well 16 level lo and lolo alarms caused by LOTO of electronics -Verified analyzers: Influent Free Chlorine @ 9:03 Grab: 2.74 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 9:07 Grab: 2.32mg/L Analyzer: 2.38 mg/L Treated Free Chlorine @ 9:11 Grab: 0.13 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:14 Grab: 2.62 mg/L Analyzer: 2.68 mg/L -Topped up well 13 mineral oil -Rotated ammonia pumps so pump 1 active -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0069291 | 0 | 0
2026-02 | 2026-02-12 | Newmarket Wells 13-16 | CENTRAL | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Added dechlor to waste chamber, isolated contact tank on influent side in order to depressurize raw main. Pulled injection points, ran hot water through chemical boards and injection points. Returned system to normal. Influent chlorine lo and lolo alarms caused by lack of flow during raw main isolation. Flushed from waste valve to remove excess silicate from main. Closed waste valve and fully reopened influent contact tank valve. -Changed chlorine cylinder bank A with Jason G. -Completed ammonia inspection. Containment flood alarm tested. Performed drawdowns on both pumps ? no change needed. No issues found -Completed silicate pump drawdowns. Max flow setpoints on SCADA changed for pump 1 to 290 mL/min and for pump 2 to 265 mL/min -Returned wells to auto | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; containment [safety] | flood [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-10 | Newmarket Wells 13-16 | CENTRAL | -on site to troubleshoot the well 13 faults. I called roc at 1330 to stop w16 and I started well 13 1350 witnessed a waste cycle and no major issue was noted transferring to system. During did have the a high chlorine alarm 1400. Stopped well with Ben and back flushed the contact tank till reading a suitable level on analyzers. We placed well back to remote Ben started and I witnessed another waste cycle no faults while running to system. Ben H. Placed well back to duty and we will monitor for more faults. Under direction of oic. | FLAG | stage2_low_confidence | 0.15088 | ML: above threshold (no LLM available) — 0.151 | fault [equipment_failure]; alarm [control_system] | 0.15088 | 0 | 0
2026-02 | 2026-02-13 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check with Christian B. -Found silicate pump 1 in hand, returned to remote and cleared fail to start alarm. Rotated it into duty 1 at 8:58 to test dosing effectiveness -Verified analyzers: Influent Free Chlorine @ 9:08 Grab: 2.64 mg/L Analyzer: 2.71 mg/L Effluent Free Chlorine @ 9:03 Grab: 2.50 mg/L Analyzer: 2.49 mg/L Treated Free Chlorine @ 9:00 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:00 Grab: 2.90 mg/L Analyzer: 2.87 mg/L -Switched from ammonia pump 1 to 2 at 9:27 due to high ammonia dosing. Confirmed dosing high across both pumps. Adjusted chlorine:ammonia ratio from 4.20 to 4.30 -Rotated duty for the wells so well 16 is in duty 1 and well 13 is in duty 2 to allow well 16 to continue to run after IWS visited site and I manually rotated the wells to allow well 16 to be inspected while running -Based on turbidity rising slowly while running silicate pump 1, adjusted max flow SCADA setpoint back from 290 mL/min to 280 mL/min (dose prior to yesterday?s adjustment) -Topped up ammonia tank 1 -Entered data into PD sheet -Checked trends | FLAG | stage2_low_confidence | 0.0087328 | ML: above threshold (no LLM available) — 0.009 | scada [control_system]; alarm [control_system] | 0.0087328 | 0 | 0
2026-02 | 2026-02-11 | Newmarket Wells 13-16 | CENTRAL | On-site for a station and equipment check No issues found Weekly bacti samples taken Chemical levels and systems ok 12 cylinders and 2 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1350 G:2.52 A:2.54mg/L Effluent Free@1306 G:2.36 A:2.39mg/L Treated Free@1406 G:0.08 A:0.12mg/L Treated Total@1410 G:2.74 A:2.72mg/L Mono-2.33 FA-0.08 TA-0.54mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040853 | 0 | 0
2026-02 | 2026-02-09 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check and respond to well 13 pump fault alarm. -Verified analyzers: Influent Free Chlorine @ 8:44 Grab: 2.74 mg/L Analyzer: 2.77 mg/L Effluent Free Chlorine @ 8:40 Grab: 2.48 mg/L Analyzer: 2.51 mg/L Treated Free Chlorine @ 8:36 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 8:36 Grab: 2.84 mg/L Analyzer: 2.87 mg/L -Collected operational samples -Entered data into PD sheet -Checked trends -Cleared well 13 fault alarm with no issues. However, upon manually starting the well, the fault returned after a few minutes of the well running to waste (confirmed via masl drawdown). Created work order W11649808 for maintenance to address possible waste valve fail to close or other cause of fault. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; work order [maintenance_action]; alarm [control_system]; pump fault [infrastructure] | fault [equipment_failure]; work order [maintenance_action]; alarm [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-02 | 2026-02-04 | Newmarket Wells 13-16 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok Topped up ammonia day tank 2 12 cylinders and 0 bags of ammonia in inventory Weekly bacti samples taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1040 G:2.60 A:2.67mg/L Effluent Free@1043 G:2.42 A:2.41mg/L Treated Free@1046 G:0.08 A:0.12mg/L Treated Total@1047 G:2.62 A:2.68mg/L Mono-2.30 FA-0.04 TA-0.50 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038076 | 0 | 0
2026-02 | 2026-02-06 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 8:58 Grab: 2.62 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 9:05 Grab: 2.40 mg/L Analyzer: 2.34 mg/L Treated Free Chlorine @ 9:16 Grab: 0.10 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:22 Grab: 2.72 mg/L Analyzer: 2.75 mg/L -Topped up mineral oil well 13 -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0007966 | 0 | 0
2026-02 | 2026-02-23 | Nobleton Booster Pumping Station | WEST | Station Check (no issues found) Pump running | FLAG | stage2_low_confidence | 0.011181 | ML: above threshold (no LLM available) — 0.011 |  | 0.011181 | 0 | 0
2026-02 | 2026-02-02 | Nobleton Booster Pumping Station | WEST | On site for station check. Pump running, chamber dry - site all ok | FLAG | stage2_low_confidence | 0.0097304 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097304 | 0 | 0
2026-02 | 2026-02-17 | Nobleton Booster Pumping Station | WEST | On site for station check. Pump running, completed jhsc inspection - site all ok | FLAG | stage2_low_confidence | 0.010354 | ML: above threshold (no LLM available) — 0.01 |  | 0.010354 | 0 | 0
2026-02 | 2026-02-13 | Nobleton Booster Pumping Station | WEST | -on site to complete station check -unable to access site due to snow, visual inspection only | FLAG | stage2_low_confidence | 0.013258 | ML: above threshold (no LLM available) — 0.013 |  | 0.013258 | 0 | 0
2026-02 | 2026-02-25 | Nobleton North Elevated Tank | WEST | In to Complete Station Check and to collect bacti sample w11620002 Residuals free Grab 1.15mg/L Analyzer 1.13mg/L Total Grab: 1.58mg/L, Analyzer: 1.56mg/L Topped up both reagents on site ki and acetate No new known issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00656 | 0 | 0
2026-02 | 2026-02-11 | Nobleton North Elevated Tank | WEST | In to Complete Station Check and to collect bacti sample w11588666 Residuals free Grab 1.23mg/L Analyzer 1.18mg/L Total Grab: 1.78mg/L, Analyzer: 1.86mg/L Collected in house lab sample No new known issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060715 | 0 | 0
2026-02 | 2026-02-17 | Nobleton North Elevated Tank | WEST | In to Complete Station Check and to collect bacti sample w11605377 Residuals free Grab 1.42mg/L Analyzer 1.37mg/L Total Grab: 1.86mg/L, Analyzer: 1.90mg/L No new known issues on site | FLAG | stage2_low_confidence | 0.0075976 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075976 | 0 | 0
2026-02 | 2026-02-12 | Nobleton North Elevated Tank | WEST | On site for the following NBET27, JHSC Health and Safety Inspection, Nobleton North ET (1M NBET27, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Nobleton North ET (1M) NBET27, Inlet/Outlet Heat Trace System, Inspection, Nobleton North ET [WINTER] (1M) NBET27, High & Low Water Level Alarm, Test, Nobleton North ET (2M) NBET27, Low Temperature Alarm, Test, Nobleton North, ET (1M) NBET27, Nobleton North ET - Portable Gasoline Generator Test (1M) No new issues on site | FLAG | stage2_low_confidence | 0.011043 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011043 | 0 | 0
2026-02 | 2026-02-04 | Nobleton North Elevated Tank | WEST | In to Complete Station Check and to collect bacti sample w11568074 Residuals free Grab 1.44mg/L Analyzer 1.41mg/L Total Grab: 1.95mg/L, Analyzer: 1.99mg/L No new known issues on site | FLAG | stage2_low_confidence | 0.0075976 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075976 | 0 | 0
2026-02 | 2026-02-25 | Nobleton South Elevated Tank | WEST | In to Complete Station Check and to collect bacti sample w11620002 Residuals free Grab 1.33mg/L Analyzer 1.31mg/L Total Grab: 1.89mg/L, Analyzer: 1.85mg/L No new known issues on site | FLAG | stage2_low_confidence | 0.0075976 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075976 | 0 | 0
2026-02 | 2026-02-26 | Nobleton South Elevated Tank | WEST | On site to replace unit heater | FLAG | stage2_low_confidence | 0.011932 | ML: above threshold (no LLM available) — 0.012 |  | 0.011932 | 0 | 0
2026-02 | 2026-02-17 | Nobleton South Elevated Tank | WEST | In to Complete Station Check and to collect bacti sample w11605377 Residuals free Grab 1.42mg/L Analyzer 1.41mg/L Total Grab: 1.89mg/L, Analyzer: 1.83mg/L No new known issues on site | FLAG | stage2_low_confidence | 0.0075976 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075976 | 0 | 0
2026-02 | 2026-02-12 | Nobleton South Elevated Tank | WEST | On site for the following NBET, JHSC Health and Safety Inspection, Nobleton South ET (1M) NBET, Sump Pit System, Inspection, Nobleton South ET (1M) NBET, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Nobleton South, ET (1M) - adjusted total from 1.60-1.90mg/L after multiple grabs Topped up acetate NBET, Inlet/Outlet Heat Trace System, Inspection, Nobleton South ET [WINTER] (1M) - system was in alarm - cleared alarms - all ok NBET, Sensing Line Heat Trace System, Inspection, Nobleton South, ET LWINTER_ (1M) NBET, Low Temperature Alarm, Test, Nobleton South, ET (1M) NBET, Gasoline Generator, Test Run, Nobleton South ET (1M) | FLAG | stage2_low_confidence | 0.022997 | ML: above threshold (no LLM available) — 0.023 | alarm [control_system]; alarms [control_system] | 0.022997 | 0 | 0
2026-02 | 2026-02-11 | Nobleton South Elevated Tank | WEST | In to Complete Station Check and to collect bacti sample w11588666 Residuals free Grab 1.45mg/L Analyzer 1.50mg/L Total Grab: 1.65mg/L, Analyzer: 1.63mg/L Replaced KI solution Gate on site is broken - informed TL Collected in house lab sample No new known issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003847 | 0 | 0
2026-02 | 2026-02-04 | Nobleton South Elevated Tank | WEST | In to Complete Station Check and to collect bacti sample w11568074 Residuals free Grab 1.48mg/L Analyzer 1.50mg/L Total Grab: 1.78mg/L, Analyzer: 1.74mg/L Reagents all ok Heater not working created work order W11639030 and informed TL No new known issues on site | FLAG | stage2_low_confidence | 0.017189 | ML: above threshold (no LLM available) — 0.017 | not working [equipment_failure]; work order [maintenance_action] | 0.017189 | 0 | 0
2026-02 | 2026-02-20 | Nobleton Well 2 | WEST | Onsite for station check Well running Checked residuals mg/l Influent @1244 Free analyzer 1.89 grab 2.02 Effluent @1241 Free analyzer 1.84 grab 1.84 Total grab 2.15 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013834 | 0 | 0
2026-02 | 2026-02-25 | Nobleton Well 2 | WEST | In to Complete Station Check and bactisample w11620002 Residuals Effluent free Grab: 1.60mg/L, Analyzer: 1.54mg/L Total grab 1.92mg/L Influent free Grab: 1.92mg/L, Analyzer: 1.93mg/L Reagents - all okay No new known issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037994 | 0 | 0
2026-02 | 2026-02-23 | Nobleton Well 2 | WEST | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 10:40 Influent Free: Grab 1.92, A 1.87 10:30 Treated Free: Grab 1.90, A 1.87 Total: Grab 2.66 10:45 operational samples taken 11:00 Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025771 | 0 | 0
2026-02 | 2026-02-27 | Nobleton Well 2 | WEST | In to Complete Station Check Residuals Effluent free Grab: 1.45mg/L, Analyzer: 1.45mg/L Influent free Grab: 1.58mg/L, Analyzer: 1.59mg/L No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004515 | 0 | 0
2026-02 | 2026-02-02 | Nobleton Well 2 | WEST | Attending site to check Effluent Chlorine analyzer (W11611597). Push button switches were found to be inoperable. Replaced bush buttons and verified reading. Also checked Chlorinator #1 due to leak at stem (W11625398). Greased stem as the existing grease was clumping and dry. Notified Operations to try it out next time they are on site. It was left in Manual. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.050365 | ML: above threshold (no LLM available) — 0.05 | leak [infrastructure] | 0.050365 | 0 | 0
2026-02 | 2026-02-24 | Nobleton Well 2 | WEST | Onsite to troubleshoot AIT1 (Influent) buttons not working Informed ROC. ROC asked us to confirm with operations as duty was just about to start. All OK. ROC placed duty to manual off. Replaced main board and colorimeter. Took grabs. No adjustments required G = 1.81mg/L A = 1.83mg/L Cleared associated alarms Asked ROC to return duty to auto. Well 2 started. Monitored for a while. All OK Armed building and left site | FLAG | stage2_low_confidence | 0.062759 | ML: above threshold (no LLM available) — 0.063 | sso [critical]; not working [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.062759 | 0 | 0
2026-02 | 2026-02-02 | Nobleton Well 2 | WEST | In to Complete Station Check Residuals Effluent free Grab: 1.78mg/L, Analyzer: 1.76mg/L Influent free Grab: 1.86mg/L, Analyzer: 1.81mg/L Reagents - all okay Chlorinator 1 still oos work order has been created No other issues on site | FLAG | stage2_low_confidence | 0.012953 | ML: above threshold (no LLM available) — 0.013 | oos [equipment_failure]; work order [maintenance_action] | 0.012953 | 0 | 0
2026-02 | 2026-02-18 | Nobleton Well 2 | WEST | Onsite to perform annual maintenance/Rebuild both chlorinators. Informed ROC and Cole was on site, isolated gas cylinders and purged the lines. We rebuilt both the chlorinators. performed vacuum test by running booster pumps in local mode. No leak found. Performed gas calibration and Performed verification and Put chlorinators back in service. No issues. Cole was onsite and back flushed the lines and started well in auto mode. No issues. Informed ROC, armed the building and left the site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; leak [infrastructure] | oos [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-18 | Nobleton Well 2 | WEST | On site to assist INST with chlorinator overhauls. Repair minor leak on cl2 tubing/parker fitting from regulator 1 to PVC ball valve. Replace 4 inlet ball valves to chlorinators, will replace remaining ball valves and label (last changed 2024, some in good condition, some fair). Tested and both chlorine systems holding vacuum, chlorinator 2 vacuum much higher than 1, could be related to issue with corp stop ball valve and lance (due for replacement). | FLAG | stage2_low_confidence | 0.086274 | ML: above threshold (no LLM available) — 0.086 | repair [maintenance_action]; leak [infrastructure] | 0.086274 | 0 | 0
2026-02 | 2026-02-11 | Nobleton Well 2 | WEST | -On site to complete station check and collect weekly micro. samples -sample work order # W11588666 -well running in manual -cl2 booster pump # 2 running at 208 psi -chlorinator # 2 43% open dosing 23.5 ppd, vac = - 620 mbar, DF = 87.0% -silicate pump #2 running at 46%, 55.9 ml/min, 90 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 08:44 - Effluent Analyzer = 1.70 mg/L 08:44 - Effluent grab: Free chlorine = 1.76 mg/L Total chlorine = 2.12 mg/L 08:49 - collected weekly treated water micro. sample 08:50 - collected weekly raw water micro. sample -recorded readings in PWQ sheet -completed work orders, informed ROC of work -completed Dechlorination Puck Dispenser Inspection and Cleaning -completed Chemical System Inspection - Silicate -cleaned and flushed injection points -ran pumps into graduated cylinder: Pump #1 max flow = 117 ml/min Pump #2 max flow = 110 ml/min -reinstalled injection points, silicate system back to normal operation -completed Chemical System Inspection - Chlorine -found vacuum leak upstream of chlorinators, created follow up work order to troubleshoot -backflushed for several minutes as a precaution -completed Chlorine Analyzer, Maintenance -cleaned analyzers, flushed sample lines -replaced effluent sample line -verified analyzers after maintenance: 12:26 - Effluent Analyzer = 2.35 mg/L 12:26 - Effluent grab: Free chlorine = 2.42 mg/L 12:27 - Influent Analyzer = 1.86 mg/L 12:27 - Influent grab: Free chlorine = 1.91 mg/L -completed JHSC Health and Safety Inspection -completed Turbidimeter, Maintenance -cleaned and verified turbidimeter -completed Deep Well Exhaust Valve, Test -completed Pressure Relief Valve, Test -completed Chlorine Leak Detector, Test -started well in manual, tested all chemical systems in auto -site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure] | oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-18 | Nobleton Well 2 | WEST | Backflush well 2 to remove highly chlorinated water after calibrations. Place Cl2 booster pumps, w2 back to auto. Monitor startup, no issues. | FLAG | stage2_low_confidence | 0.020202 | ML: above threshold (no LLM available) — 0.02 | oos [equipment_failure] | 0.020202 | 0 | 0
2026-02 | 2026-02-13 | Nobleton Well 2 | WEST | -on site to complete station check -well running in manual -cl2 booster pump # 2 running at 208 psi -chlorinator # 2 42% open dosing 22.5 ppd, vac = - 620 mbar, DF = 85.0% -silicate pump #2 running at 46%, 55.8 ml/min, 90 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 08:20 - Effluent Analyzer = 1.75 mg/L 08:20 - Effluent grab: Free chlorine = 1.76 mg/L Total chlorine = 2.11 mg/L 08:28 - Influent Analyzer = 1.82 mg/L 08:28 - Influent grab: Free chlorine = 1.77 mg/L -recorded readings in PWQ sheet -no issues found -well back into auto - off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.0040842 | 0 | 0
2026-02 | 2026-02-17 | Nobleton Well 2 | WEST | In to Complete Station Check and bactisample w11605377 Residuals Effluent free Grab: 1.81mg/L, Analyzer: 1.85mg/L Total grab 2.02mg/L Influent free Grab: 1.91mg/L, Analyzer: 1.85mg/L Reagents - all okay No new known issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037994 | 0 | 0
2026-02 | 2026-02-09 | Nobleton Well 2 | WEST | In to Complete Station Check Residuals Effluent free Grab: 1.62mg/L, Analyzer: 1.67mg/L Influent free Grab: 1.79mg/L, Analyzer: 1.80mg/L Reagents - replaced effluent reagents Collected sample for in house lab No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030444 | 0 | 0
2026-02 | 2026-02-04 | Nobleton Well 2 | WEST | In to Complete Station Check and bactisample w11568074 Residuals Effluent free Grab: 1.75mg/L, Analyzer: 1.76mg/L Total grab 1.92mg/L Influent free Grab: 2.12mg/L, Analyzer: 2.07mg/L Reagents - all okay Raw pH 7.99 Placed chlorinator 1 back online - all seems okay will continue to monitor No new known issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0027508 | 0 | 0
2026-02 | 2026-02-25 | Nobleton Wells 3 & 7 | WEST | In to Complete Station Check and to collect bacti sample w11620002 Residuals Effluent free Grab: 1.56mg/L, Analyzer: 1.57mg/L Effluent total Grab 1.82mg/L Influent free Grab: 2.30mg/L, Analyzer: 2.23mg/L Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041094 | 0 | 0
2026-02 | 2026-02-23 | Nobleton Wells 3 & 7 | WEST | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 11:35 Influent: Free: Grab 2.08, A 2.12 11:40 Treated: Free: Grab 1.63, A 1.63 Total Grab 1.90 Reagent change for both Influent and Treated cl17s Hypo tanks top up Operational samples collected | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.002652 | 0 | 0
2026-02 | 2026-02-24 | Nobleton Wells 3 & 7 | WEST | On site to receive Sodium Hypochlorite. | FLAG | stage2_low_confidence | 0.012376 | ML: above threshold (no LLM available) — 0.012 |  | 0.012376 | 0 | 0
2026-02 | 2026-02-02 | Nobleton Wells 3 & 7 | WEST | In to Complete Station Check Residuals Effluent free Grab: 1.48mg/L, Analyzer: 1.41mg/L Influent free Grab: 1.80mg/L, Analyzer: 1.86mg/L Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034443 | 0 | 0
2026-02 | 2026-02-11 | Nobleton Wells 3 & 7 | WEST | In to Complete Station Check and to collect bacti sample w11588666 Topped up hypo tanks Residuals Effluent free Grab: 1.78mg/L, Analyzer: 1.77mg/L Effluent total Grab 1.98mg/L Influent free Grab: 2.18mg/L, Analyzer: 2.16mg/L Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031496 | 0 | 0
2026-02 | 2026-02-13 | Nobleton Wells 3 & 7 | WEST | On site for station check Check trends: all okay Duty not active Verified Analyzers 10:20-Effluent free Grab: 1.49mg/L, Analyzer: 1.45mg/L 10:25-Influent free Grab: 1.52mg/L, Analyzer: 1.49mg/L Reagents all good entered values in PWQ sheet Equipment all okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049842 | 0 | 0
2026-02 | 2026-02-20 | Nobleton Wells 3 & 7 | WEST | Onsite for station check Well running Checked residuals mg/l Effluent @11:28 Free analyzer 1.69 grab 1.61 Total grab 1.91 Influent @11:30 Free analyzer 2.15 grab 2.19 Total grab 3.14 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012558 | 0 | 0
2026-02 | 2026-02-17 | Nobleton Wells 3 & 7 | WEST | In to Complete Station Check and to collect bacti sample w11588666 Topped up hypo tanks Residuals Effluent free Grab: 1.57mg/L, Analyzer: 1.44mg/L Effluent total Grab 1.89mg/L Adjusted effluent free from 1.44-1.57 after multiple grabs Influent free Grab: 2.02mg/L, Analyzer: 2.04mg/L Accepted chlorine hypo delivery Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0023067 | 0 | 0
2026-02 | 2026-02-05 | Nobleton Wells 3 & 7 | WEST | On site for the following NBW3, Deep Well Exhaust Valve, Test, Nobleton Well 3 (1M) NBW3, Sodium Hypochlorite System Maintenance, Nobleton Well 3 (1M) NBW3, Surge Relief Valve, Exercise, Nobleton Well 3 (6M) NBW3, Pressure Relief Valve, Test, Nobleton Well 3 (1M) NBW3, Diesel Generator Test Run, Nobleton Well 3 (1M) Hours start 371.1 stop 372.3hrs Fuel start 850 stop 844L NBW3, Chlorine Analyzer Maintenance, Nobleton Well 3 (1M) NBW3, Low/High Temperature Alarm, Test, Nobleton Well 3 (1M) NBW3, Ventilation System, Inspection, Nobleton Well 3 (1M) NBW3, Turbidimeter, Maintenance, Nobleton Well 3 (1M) NBW3, Check Valve, Inspection, Nobleton Well 3 (6M) NBW3, Sodium Hypochlorite System Inspection, Nobleton Well 3 (1M) NBW3, Chemical System Inspection - Silicate, Nobleton Well 3 (1M) Completed JHSC inspection No new issues on site | FLAG | stage2_low_confidence | 0.016405 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system] | 0.016405 | 0 | 0
2026-02 | 2026-02-03 | Nobleton Wells 3 & 7 | WEST | On site to receive sodium hypochlorite. | FLAG | stage2_low_confidence | 0.012376 | ML: above threshold (no LLM available) — 0.012 |  | 0.012376 | 0 | 0
2026-02 | 2026-02-06 | Nobleton Wells 3 & 7 | WEST | In to Complete Station Check Residuals Effluent free Grab: 1.62mg/L, Analyzer: 1.60mg/L Influent free Grab: 1.74mg/L, Analyzer: 1.78mg/L Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034443 | 0 | 0
2026-02 | 2026-02-06 | Nobleton Wells 3 & 7 | WEST | In to Complete Station Check Residuals Effluent free Grab: 1.48mg/L, Analyzer: 1.50mg/L Influent free Grab: 1.54mg/L, Analyzer: 1.51mg/L Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034443 | 0 | 0
2026-02 | 2026-02-04 | Nobleton Wells 3 & 7 | WEST | In to Complete Station Check and to collect bacti sample w11568074 Well locked out on low influent. Residual came up after well shut down. Inspected hypo lines for leaks and primed hypo pump 2 no issues noticed restarted well with hypo pump 2 Raw pH 8.08 Residuals Effluent free Grab: 1.60mg/L, Analyzer: 1.55mg/L Effluent total Grab 1.78mg/L Influent free Grab: 2.44mg/L, Analyzer: 2.53mg/L Reagents - all okay No other issues on site | FLAG | stage2_low_confidence | 0.0074995 | ML: above threshold (no LLM available) — 0.007 | leak [infrastructure] | 0.0074995 | 0 | 0
2026-02 | 2026-02-09 | Nobleton Wells 3 & 7 | WEST | On site for station check Residuals Effluent free Grab: 1.61mg/L, Analyzer: 1.65mg/L Influent free Grab: 1.56mg/L, Analyzer: 1.55mg/L Topped up hypo tanks - logged in pwq Collected in house lab sample No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035246 | 0 | 0
2026-02 | 2026-02-25 | Nobleton Wells 5 & 6 | WEST | In to troubleshoot NBW5 following low influent lockout yesterday, hours after placing online following chlorine system overhaul (ejector regulator, fittings, lines). Started back flushing to sanitary sewer. Tested Chlorinator 2 system. Vacuum is good, capacity is good, no obvious issues. Operating vacuum -80mmHg. Broke chlorinator 1 rotameter during vacuum purge, will replace. Start w5 manual on after backflush to test cl2 dosing and system performance. Observed yesterday on startup that raw water to exhaust was very odorous (sulfur etc). Not as odorous on startup today. Residual dropped off during runtime after first hour yesterday, will monitor performance. Lower NBW5 flow setpoint from 28L/s to 21L/s to allow higher chlorine dose if aquifer demand is increased or unstable. Residuals: mg/L 1138 Influent G FCl 3.48 A FCl 0.76 (Wait for analyzer sample / average to catch up to grab residuals) 1142 Influent G FCl 3.24 A FCl 3.27 Adjust chlorinator DFs from 195 to 180 based on residuals and dosing change when lowering flow to 21L/s. Increase residual SP from 2.60 to 2.80mg/L while monitoring performance. | FLAG | stage2_low_confidence | 0.024464 | ML: above threshold (no LLM available) — 0.024 |  | 0.024464 | 0 | 0
2026-02 | 2026-02-09 | Nobleton Wells 3 & 7 | WEST | -Filled silicate tank 45.69 cm to 77.97 cm -Installed and set up replacement silicate pump #1 -ran pump from scada into calibration column - max flow = 155 ml/min, adjusted scada max flow setpoint 130 to 150 ml/min -started well in manual and tested silicate pump 1 in auto - no issues -noticed pump 1 discharge pressure high - stopped well and replaced injection point check valve -tested pump again - ok | FLAG | stage2_low_confidence | 0.023521 | ML: above threshold (no LLM available) — 0.024 | scada [control_system] | 0.023521 | 0 | 0
2026-02 | 2026-02-25 | Nobleton Wells 5 & 6 | WEST | In to Complete Station Check and to collect bacti sample w11620002 Residuals Effluent free Grab: 1.55 mg/L, Analyzer: 1.62mg/L Effluent total Grab 2.09mg/L Influent free Grab: 3.14mg/L, Analyzer: 3.30mg/L Primed Nasi p1 and p2 are air in line Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034423 | 0 | 0
2026-02 | 2026-02-27 | Nobleton Wells 5 & 6 | WEST | In to Complete Station Check Residuals Effluent free Grab: 1.89mg/L, Analyzer: 1.95mg/L Influent free Grab: 2.62mg/L, Analyzer: 2.66mg/L Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034443 | 0 | 0
2026-02 | 2026-02-26 | Nobleton Wells 5 & 6 | WEST | Changed cl2 cylinder with J.Muzzin | FLAG | stage2_low_confidence | 0.0097674 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097674 | 0 | 0
2026-02 | 2026-02-23 | Nobleton Wells 5 & 6 | WEST | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/l) 1:25 Influent Free: Grab 0.076, A 0.72 1:30 Effluent Free: Grab 1.78, A 1.83 Total Grab 2.60 Station manual off due to suspected Chlorination issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031097 | 0 | 0
2026-02 | 2026-02-24 | Nobleton Wells 5 & 6 | WEST | On site with Sean Peoples to replace battery on generator. ROC notified. New battery installation complete. Generator controller removed from Auto. Generator run locally to ensure battery function. ROC notified. Generator run complete. Generator controller returned to Auto. ROC notified. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061746 | 0 | 0
2026-02 | 2026-02-24 | Nobleton Wells 5 & 6 | WEST | Onsite to work on chlorination system Purged system Changed out regulators and injectors Changed out tubing and Parker fittings Tested for vacuum on both chlorinators and booster pumps Primed lines Started well Influent grabs @1518 Free analyzer 3.68 grab 3.34 @1536 Free analyzer 2.88 grab 2.90 Left cl2 booster pumps in local off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.00264 | 0 | 0
2026-02 | 2026-02-27 | Nobleton Wells 5 & 6 | WEST | -replaced chlorinator #1 rotameter -attempted to vacuum test chlorinator however found ejector #1 not producing vacuum -replaced ejector, however service water line is too short, leaving chlorinator #1 OOS until can collect materials | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-13 | Nobleton Wells 5 & 6 | WEST | -on site to complete station check -well running in manual -well #6 offline and isolated from distribution system -chlorinator #1 OOS -cl2 booster pump # 2 running at 180 psi -chlorinator # 2 87% open dosing 43 ppd, vac = - 80 mbar, DF = 189% -silicate pump #2 running at 58%, 11.6 rpm, 105 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 08:53 - Effluent Analyzer = 2.34 mg/L 08:53 - Effluent grab: Free chlorine = 2.40 mg/L Total chlorine = 2.82 mg/L 08:57 - Influent Analyzer = 2.61 mg/L 08:57 - Influent grab: Free chlorine = 3.04/3.08/3.02 mg/L 09:02 - adjusted influent analyzer to 3.05 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no other issues found -silicate pump #1 OOS due to high turbidity, primed pump and tested in auto - no issues observed, pumping at max flow of 114 ml/min. Will leave pump in auto duty 2 -completed JHSC Health and Safety Inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Nobleton Wells 5 & 6 | WEST | In to Complete Station Check Residuals Effluent free Grab: 2.16mg/L, Analyzer: 2.22mg/L Influent free Grab: 1.82mg/L, Analyzer: 1.88mg/L Reagents - changed out influent free reagents No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038752 | 0 | 0
2026-02 | 2026-02-13 | Nobleton Wells 5 & 6 | WEST | Insulate hot water pipes Test backflow preventer Passed | FLAG | stage2_low_confidence | 0.0098455 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098455 | 0 | 0
2026-02 | 2026-02-12 | Nobleton Wells 5 & 6 | WEST | Work on hot water line for flushing silicate lines | FLAG | stage2_low_confidence | 0.013902 | ML: above threshold (no LLM available) — 0.014 |  | 0.013902 | 0 | 0
2026-02 | 2026-02-10 | Nobleton Wells 5 & 6 | WEST | On site with Total Power generator technician to conduct annual generator maintenance and load bank test. Generator not in auto. ROC notified. 2 hr load bank test completed. Generator returned to auto. 15 min station transfer test completed. Station returned to Utility supply. ROC notified. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047279 | 0 | 0
2026-02 | 2026-02-11 | Nobleton Wells 5 & 6 | WEST | In to Complete Station Check and to collect bacti sample w11588666 Residuals Effluent free Grab: 2.18mg/L, Analyzer: 2.17mg/L Effluent total Grab 2.52mg/L Influent free Grab: 2.52mg/L, Analyzer: 2.52mg/L Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041094 | 0 | 0
2026-02 | 2026-02-20 | Nobleton Wells 5 & 6 | WEST | Onsite for station check Started duty to have well running for station check Checked residuals mg/l Influent @1007 Free analyzer 2.67 grab 2.66 Total grab 3.00 Effluent @1009 Free analyzer 1.88 grab 1.86 Total grab 2.24 Adjusted flow to ntu analyzer causing spike Primed silicate p1 Chlorinator 1 oos | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | Nobleton Wells 5 & 6 | WEST | In to Complete Station Check and to collect bacti sample w11605377 Residuals Effluent free Grab: 2.02mg/L, Analyzer: 1.90mg/L Effluent total Grab 2.64mg/L Influent free Grab: 2.70mg/L, Analyzer: 2.68mg/L Primed Nasi p2 air in line Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003246 | 0 | 0
2026-02 | 2026-02-21 | Nobleton Wells 5 & 6 | WEST | -on site to respond to low effluent switch lockout -started backflushing/dechlor 15:15 -checked chlorine system - chlorinated/vaccum and booster pump all ok -tighten fitting -checked trends: influent dropped and chlorinated not able to keep ?? -verified effluent analyzer 15:35: 1.53mg/l grab:1.50mg/l -verified influent analyzer 15:34: 0.36mg/l grab: 0.32mg/l -stopped backflushing at 16:00 -place well back into duty and started well -chlorinated maxing out with an influent of 1.70- 1.80mg/l -man/stopped well - will keep well as backup for the rest of the weekend | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; backup [infrastructure] | oos [equipment_failure]; backup [infrastructure] |  | 1 | 0
2026-02 | 2026-02-10 | Nobleton Wells 5 & 6 | WEST | On site for the following NBW56, Air Release, Valve Flushing, Nobleton, Well 5/6 (1M) NBW5, Sodium Silicate Feed Peristaltic Pump Inspection, Nobleton Well 5 (1200 Hrs.) NBW56, Turbidimeter Maintenance, Nobleton Well 5/6 (1M) NBW56, Chlorine Analyzer, Maintenance, Nobleton Well 5/6 (1M) NBW56, Chlorine Cylinder Emergency Repair Kit Inspection, Nobleton, Well 5/6 (1M) NBW56, Chlorine Leak Detector, Test, Nobleton, Well 5/6 (1M) NBW56, High/Low Alarm, Test, Nobleton, Well 5/6 (1M) NBW56, Chemical System Inspection - Silicate, Nobleton W5/6 (1M) NBW56, Diesel Generator Test Run, Nobleton, Well 5/6 (1M) - contractor (TotalPower) on site with electrician for annual testing generator ran 2 hours on load and transferred to site - all ok. Start hours 258:42 stop hours 261:10 Start fuel 91/89cm stop fuel 85/83cm NBW56, Diesel Fuel Spill Alarm, Test, Nobleton Well 5/6 (1M) NBW5, Dehumidifier, Cleaning & Inspection, Nobleton Well 5 (1M) NBW56, Pressure Relief Valve, Inspection, Nobleton Well 5/6 (1M) NBW56, Chemical System Inspection - Chlorine, Nobleton W5/6 (1M) NBW56, Chlorine Scrubber, Check, Nobleton, Well 5/6 (1M) | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; emergency [critical]; repair [maintenance_action]; alarm [control_system]; leak [infrastructure] | spill [critical]; emergency [critical]; repair [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-09 | Nobleton Wells 5 & 6 | WEST | In to Complete Station Check Checked chlorinator 1 seems to be an issue. Rotates bouncing when in service. No vacuum leak. Will place in manual off and inform TL. Residuals Effluent free Grab: 1.62mg/L, Analyzer: 1.58mg/L Influent free Grab: 2.60mg/L, Analyzer: 2.64mg/L Collected sample for in house lab No other issues on site | FLAG | stage2_low_confidence | 0.0072219 | ML: above threshold (no LLM available) — 0.007 | leak [infrastructure] | 0.0072219 | 0 | 0
2026-02 | 2026-02-09 | Nobleton Wells 5 & 6 | WEST | On site with Dave T to change chlorine cylinder 1 from 0-68kg Troubleshooting chlorinator one. Think the issue is with the ejector, will speak with TL. Troubleshooting caused a low influent. Backflushed well; placed dechlor in chamber. Leaving chlorinator 1 and booster pump 1 in manual off for the night will inform oncall | FLAG | stage2_low_confidence | 0.030538 | ML: above threshold (no LLM available) — 0.031 | oos [equipment_failure] | 0.030538 | 0 | 0
2026-02 | 2026-02-04 | Nobleton Wells 5 & 6 | WEST | In to Complete Station Check and to collect bacti sample w11568074 Residuals Effluent free Grab: 2.12mg/L, Analyzer: 2.02mg/L Effluent total Grab 2.42mg/L Influent free Grab: 2.66mg/L, Analyzer: 2.72mg/L Reagents - all okay Raw pH 8.07 Cleaned turbidimeter No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0023105 | 0 | 0
2026-02 | 2026-02-09 | Nobleton Wells 5 & 6 | WEST | Install water heater for flushing silicate lines Called away to Keswick for emergency | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-02 | 2026-02-08 | Nobleton Wells 5 & 6 | WEST | Onsite to respond to well being locked out due to low effluent cl2 Checked residuals mg/l @1036 Free analyzer 0.44 grab 0.48 Started back flush @1041 Grab @1046 Analyzer 0.49 grab 0.77 Flushed ntu analyzer @1101 Effluent free analyzer 1.48 grab 1.42 @1102 Influent free analyzer 0.31 grab 0.42 @1113 Influent analyzer 0.49 grab 0.80 Stopped back flush @1115 Approximately 41m3 Restated well @1117 Primed silicate p2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00035455 | 0 | 0
2026-02 | 2026-02-25 | Queensville Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Weekly bacti samples taken Verified analyzers and entered all readings and grabs into PWQ sheet INLET- Free@1054 G:0.06 A:0.02mg/L Total@1056 G:2.68 A:2.65mg/ Mono-2.54 FA-0.03 FA-0.53 NO2-0.0 OUTLET Free@1057 G:0.03 A:0.08mg/L Total@1100 G:2.34 A:2.41mg/L Mono-2.06 FA-0.06 TA-0.47 NO2-0.001 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0014867 | 0 | 0
2026-02 | 2026-02-06 | Nobleton Wells 5 & 6 | WEST | In to Complete Station Check Residuals Effluent free Grab: 1.89mg/L, Analyzer: 1.90mg/L Influent free Grab: 1.88mg/L, Analyzer: 1.81mg/L Reagents - all okay No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034443 | 0 | 0
2026-02 | 2026-02-23 | Queensville Elevated Tank | CENTRAL | Restarted the Operator Interface Terminal due to Windows OS updates. The Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.0088279 | ML: above threshold (no LLM available) — 0.009 |  | 0.0088279 | 0 | 0
2026-02 | 2026-02-19 | Queensville Elevated Tank | CENTRAL | Onsite to trouble shoot lower readings on outlet analyzer Informed ROC (Adam B) of ongoings, Deactivated duty at Ivsbridge so that QVET would be filling during maintenance Placed outlet analyzer in Cal mode at 13;30 Cleaned debris from all parts of analyzer and took grabs at 14:05 Out Total: 2.20 mg/l Out Free: 0.08 mg/l Outlet analyzer now reading accurately back in service ET ops normal | FLAG | stage2_low_confidence | 0.009891 | ML: above threshold (no LLM available) — 0.01 |  | 0.009891 | 0 | 0
2026-02 | 2026-02-17 | Queensville Elevated Tank | CENTRAL | On-site for a station and equipment check Filling/Draining Operational sample taken Bacti sample taken Verified analyzers, entered all grabs and readings into PWQ sheet Inlet Free@0927 G:0.05 A:0.01mg/L Inlet Total@0931 G:2.26 A:2.55mg/L Outlet Free@0936 G:0.07 A:0.07mg/L Outlet Total@0938 G:1.71 A:1.68mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053238 | 0 | 0
2026-02 | 2026-02-11 | Queensville Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Took weekly bacti sample Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1218 G:0.04 A:0.01mg/L Inlet Total@1220 G:2.90 A:2.80mg/L Outlet Free@1223 G:0.09 A:0.06mg/L Outlet Total@1227 G:1.98 A:1.92mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058312 | 0 | 0
2026-02 | 2026-02-06 | Queensville Elevated Tank | CENTRAL | Tested high and low level alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0071873 | 0 | 0
2026-02 | 2026-02-03 | Queensville Elevated Tank | CENTRAL | on-site for various work orders; Dechlor puck dispenser cleaned and re-stocked JHSC inspection completed inlet/outlet heat trace inspection completed Air valve inspection completed Actuated vales exercised portable generator testing completed Comprehensive housekeeping completed | FLAG | stage2_low_confidence | 0.01557 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action] | 0.01557 | 0 | 0
2026-02 | 2026-02-05 | Queensville Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Changed reagent KI in outlet analyzer Took weekly bacti sample Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@0911 G:0.03 A:0.01mg/L Inlet Total@0914 G:2.84 A:2.75mg/L Outlet free@09:15 G:0.05 A:0.06mg/L Outlet Total@0917 G:2.07 A:2.01mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058301 | 0 | 0
2026-02 | 2026-02-27 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Cylinder change bank B wit J Zhang Topped up NaSi tanks Topped up ammonia day tank 2 Changed treated total reagents Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1250 G:2.66 A:2.71mg/L Effluent Free@1251 G:0.11 A:0.12mg/L Treated Free@1251 G:0.07 A:0.09mg/L Treated Total@1255 G:2.76 A:2.74mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053398 | 0 | 0
2026-02 | 2026-02-23 | Queensville Wells No. 1 and 2 | CENTRAL | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off and the Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.0098221 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098221 | 0 | 0
2026-02 | 2026-02-25 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Weekly bacti samples taken Chemical levels and systems ok 18 cylinders and 4 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1311 G:2.88 A:2.91mg/L Effluent Free@1319 G:2.82 A:2.74mg/L Treated Free@1326 G:0.13 A:0.21mg/L Treated Total@1330 G:3.42 A:3.47mg/L Mono-2.81 FA-0.05 TA-0.61mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040853 | 0 | 0
2026-02 | 2026-02-24 | Queensville Wells No. 1 and 2 | CENTRAL | Onsite to complete chlorine system overhaul PM. 10:10 Notified ROC of work being completed. 10:20 Activiated duty 1 to top up QVETQS before working on chlorine system. 11:45. Deactivated duty and locked out wells 1 and 2. Purged chlorine system with William M. replaced injector 1 and 2. Replaced PE tubing downstream of chlorinators. Tested chlorine system. Briefly bqckflushed with dechlorination pucks at outfall. No issues foujnd. 13:28 Placed wells back to auto. Notified ROC of work complete. | FLAG | stage2_low_confidence | 0.027813 | ML: above threshold (no LLM available) — 0.028 |  | 0.027813 | 0 | 0
2026-02 | 2026-02-02 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check. No issues found Cylinder bank 2 change with J Silva Contractor on-site for generator load test Topped up oil on well pump 2 15 cylinders and 4 bags of ammonia in inventory Hot flush both silicate pumps and lines. Primed and back flushed Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1056 G:2.82 A:2.96mg/L Effluent Free@1102 G:0.26 A:0.21mg/L Treated Free@1104 G:0.08 A:0.13mg/L Treated Total@1107 G:3.02 A:3.07mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060596 | 0 | 0
2026-02 | 2026-02-23 | Queensville Wells No. 1 and 2 | CENTRAL | Onsite for station check and operational samples Recordings in PWQ sheet adjusted effluent free chlorine analyzer from 2.45 mg/L to 2.80 mg/L free ammonia was 0.00 mg/L before the effluent chlorine analyzer change, after it was reading 0.07 mg/L batched ammonia tank 1. station ok | FLAG | stage2_low_confidence | 0.012068 | ML: above threshold (no LLM available) — 0.012 |  | 0.012068 | 0 | 0
2026-02 | 2026-02-17 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check Noticed that silicate pump motor spins but pump does not. Locked out at panel, work order W11670454 Weekly bacti and operational samples taken Topped ammonia day tank 2 Chemical levels and systems ok 9 cylinders and 6 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@1110 G:2.94 A:2.92mg/L Effluent Free@1112 G:2.46 A:2.49mg/L Treated Free@1114 G:0.25 A:0.21mg/L Treated Total@1117 G:3.50 A:3.42mg/L Mono-2.62 FA-0.02 TA-0.53mg/L | FLAG | stage2_low_confidence | 0.01068 | ML: above threshold (no LLM available) — 0.011 | work order [maintenance_action] | 0.01068 | 0 | 0
2026-02 | 2026-02-12 | Queensville Wells No. 1 and 2 | CENTRAL | -When reviewing SCADA trends, notice treated total was a flat line at 3.47mg/L since yesterday - treated total analyzer was still in cleaning mode - stopped the well and put the total analyzer back to service - verified the analyzer: grab=2.98mg/L analyzer=3.02mg/L - put wells back to auto - there is no user between the wall house and Queensville ET - reviewed trends at Queensville ET - inlet total was always above 2.30mg/L, treated free at the well house was always above 0.05mg/L which well was running, and effluent free readings were in normal operating range - CT requirement was always met | FLAG | stage2_low_confidence | 0.15462 | ML: above threshold (no LLM available) — 0.155 | scada [control_system] | 0.15462 | 0 | 0
2026-02 | 2026-02-10 | Queensville Wells No. 1 and 2 | CENTRAL | On site to reconnect generator with Freguson Electric | FLAG | stage2_low_confidence | 0.013067 | ML: above threshold (no LLM available) — 0.013 |  | 0.013067 | 0 | 0
2026-02 | 2026-02-11 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 12 cylinders and 4 bags of ammonia in inventory Took weekly bacti samples Cleaned analyzers Spanned effluent free analyzer 2.86 to 2.45 based on 3 grabs-2.48,2.46,2.42 Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1048 G:2.52 A:2.54mg/L Effluent Free@1059 G:2.45 A:2.45 Treated Free@1101 G:0.28 A:0.23mg/L Treated Total@1109 G:3.48 A:3.53 Mono-2.84 FA-0.04 TA-0.60mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035243 | 0 | 0
2026-02 | 2026-02-12 | Queensville Wells No. 1 and 2 | CENTRAL | on-site for various work orders contractors on-site as well -deep well exhaust valves inspected (both wells) -Cl2 leak detection and system inspection completed -ammonia system inspection and drawdowns completed -ammonia pump diaphragms inspected -NTU calibration verification completed -JHSC inspection completed -dechlor puck dispenser ok -Silicate pumps inspeected | FLAG | stage2_low_confidence | 0.023628 | ML: above threshold (no LLM available) — 0.024 | work order [maintenance_action]; leak [infrastructure] | 0.023628 | 0 | 0
2026-02 | 2026-02-13 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found. Chemical levels and systems ok Topped up NaSi day tanks Topped up ammonia day tank 1 Changed cylinder bank B with J Zhang Changed reagents in effluent free analyzer Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1333 G:2.72 A:2.77mg/L Effluent Free@1335 G:1.37 A:1.43mg/L Treated Free@1337 G:0.07 A:0.07mg/L Treated Total@1341 G:2.60 A:2.65mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056061 | 0 | 0
2026-02 | 2026-02-20 | Queensville Wells No. 1 and 2 | CENTRAL | Station Check (no issues found) Input data to PWQ 8:35 Verified CL17s (mg/l) Influent Free: Grab 2.66, A 2.71 Effluent Free: Grab 1.86, A 1.86 Treated: Free: Grab 0.04, A 0.06 Total: Grab 2.70, A 2.71 Influent CL17 (new reagents) Silicate day tank top up Chlorine cylinder change with JZ Chlorine bulk shipment accepted | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034043 | 0 | 0
2026-02 | 2026-02-18 | Queensville Wells No. 1 and 2 | CENTRAL | On site with Sean Peoples to investigate Well 2 fail to start alarms. ROC notified. Found solenoid on waste valve to be missing fastening cap. Cap for solenoid, timer relay and control relay for waste cycle have now been replaced. With assistance from Ben Hess, Well 2 operation tested. Initial run signal sent to starter before being energized, causing fail to start and uncommanded stop. After resetting, well ran without incident. Well 2 placed in Auto and returned to normal operation. ROC notified. | FLAG | stage2_low_confidence | 0.036115 | ML: above threshold (no LLM available) — 0.036 | alarm [control_system]; alarms [control_system]; incident [safety] | 0.036115 | 0 | 0
2026-02 | 2026-02-10 | Queensville Wells No. 1 and 2 | CENTRAL | Under direction of OIC William Mather. Worked with contractors to reconnect and test station generator. Notified ROC of events. Once station was on gen power then Wel1 was commanded to run for 1hr on standby power. After testing completed ROC helped shut down the well and we transfer power back to utility. Everything was put back to remote auto. | FLAG | stage2_low_confidence | 0.019592 | ML: above threshold (no LLM available) — 0.02 |  | 0.019592 | 0 | 0
2026-02 | 2026-02-09 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Topped up NaSi day tanks. Topped up ammonia day tank 2 Topped up mineral oil for both wells Changed Total Free reagents and cleaned unit Changed cylinder bank 1 with J Zhang 12 cylinders and 4 bags of ammonia in inventory Took operational sample Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1040 G:2.98 A:2.92mg/L Effluent Free@1045 G:2.86 A:2.89mg/L Treated Free@1053 G:0.24 A:0.22mg/L Treated Total@1055 G:3.48 A3.56mg/L Mono-2.93 FA-0.02 TA-0.60 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036693 | 0 | 0
2026-02 | 2026-02-05 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Contractors onsite Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Topped up NaSi day tanks Topped up ammonia day tank 1 Weekly bacti samples taken PH taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0809 G:3.06 A:3.01mg/L Effluent Free@0819 G:2.72 A:2.77mg/L Treated Free@0821 G:0.25 A:0.21mg/L Treated Total@0823 G:3.50 A:3.44mg/L Mono-2.83 FA-0.05 TA-0.61 PH-8.07 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0024319 | 0 | 0
2026-02 | 2026-02-23 | Queensville Wells No. 3 and 4 | CENTRAL | Back onsite because of funny analyzer readings Ran well 3 in manual Put chlorine dose in manual to stabilize chlorine residual Treated chlorine analyzer still jumping around. Will notify Eric S that treated total chlorine analyzer needs more troubleshooting leaving Well 3 and 4 manual off | FLAG | stage2_low_confidence | 0.012334 | ML: above threshold (no LLM available) — 0.012 |  | 0.012334 | 0 | 0
2026-02 | 2026-02-06 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 15 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1031 G:2.78 A:2.76mg/L Effluent Free@1032 G:0.91 A:0.92mg/L Treated Free@1033 G:0.08 A:0.09mg/L Treated Total@1038 G:2.84 A:2.83 mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065254 | 0 | 0
2026-02 | 2026-02-27 | Queensville Wells No. 3 and 4 | CENTRAL | Attending site to continue to troubleshoot erratic readings from Total chlorine analyzer (W11685985). Replaced all internal chlorine analyzer components and issue still persists. Changed signal average from 2 to 4, and reading looks much more stable. Will check the trend on Monday and determine if we will be required to replace it with a CL17sc analyzer. Had wells placed in auto for the weekend via ROC. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.072088 | ML: above threshold (no LLM available) — 0.072 |  | 0.072088 | 0 | 0
2026-02 | 2026-02-25 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Weekly bacti samples taken Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Left wells in manual off for next day step test Influent Free@0824 G:2.82 A:2.78mg/L Effluent Free@0831 G:2.32 A:2.29mg/L Treated Free@0906 G:0.14 A:0.11mg/L Treated Total@0909 G:3.12 A:2.98mg/L | FLAG | stage2_low_confidence | 0.0075461 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075461 | 0 | 0
2026-02 | 2026-02-23 | Queensville Wells No. 3 and 4 | CENTRAL | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off and the Remote Operations Center was notified prior to doing the work. | FLAG | stage2_low_confidence | 0.0098221 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098221 | 0 | 0
2026-02 | 2026-02-27 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found. Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1328 G:2.82 A:2.70mg/L Effluent Free@1332 G:0.97 A:1.01mg/L Treated Free@1334 G:0.05 A:0.04mg/L Treated Total@1336 G:2.59 A:2.42mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065123 | 0 | 0
2026-02 | 2026-02-24 | Queensville Wells No. 3 and 4 | CENTRAL | Onsite to troubleshoot AIT4 (Treated Total) Erratic readings Informed ROC and operations. Well was already in manual off. Replaced main board and colorimeter. Replaced reagents and tubings. Took grabs. adjusted analyzer accordingly. G = 2.34 mg/L A = 2.37 mg/L Cleared associated alarms. No issues. Informed ROC,Armed building and left site | FLAG | stage2_low_confidence | 0.0089027 | ML: above threshold (no LLM available) — 0.009 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.0089027 | 0 | 0
2026-02 | 2026-02-26 | Queensville Wells No. 3 and 4 | CENTRAL | On-site to aide in maintenance step test of well 3 Received diesel for generator. Cleaned, hot flushed and primed NaSi lines. | FLAG | stage2_low_confidence | 0.0097343 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097343 | 0 | 0
2026-02 | 2026-02-25 | Queensville Wells No. 3 and 4 | CENTRAL | Attending site to check erratic readings from Total chlorine analyzer (W11685985). Tried many things to get the readings to stabilize but the only thing that had any effect was changing the tubing and buffer/reagent. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.030415 | ML: above threshold (no LLM available) — 0.03 |  | 0.030415 | 0 | 0
2026-02 | 2026-02-23 | Queensville Wells No. 3 and 4 | CENTRAL | Onsite for station check and operational samples Recordings in PD sheet Treated total analyzer readings jumping, cleaned analyzer adjusted flow. Readings still not normal, notified Eric S. Cleaned turbidimeter | FLAG | stage2_low_confidence | 0.016253 | ML: above threshold (no LLM available) — 0.016 |  | 0.016253 | 0 | 0
2026-02 | 2026-02-23 | Queensville Wells No. 3 and 4 | CENTRAL | Attending site to check Total chlorine analyzer (W11683435). Found moisture on colorimeter circuit board. Replaced colorimeter and verified analyzer reading. No adjustments were required. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.026875 | ML: above threshold (no LLM available) — 0.027 |  | 0.026875 | 0 | 0
2026-02 | 2026-02-02 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels are systems ok 15 cylinder and 4 bags of ammonia in inventory Hot flush silicate lines, primed and back flushed Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1250 G:2.48 A:2.50mg/L Effluent Free@1256 G:0.70 A:0.75mg/L Treated Free@1258 G:0.03 A:0.04mg/L Treated Total@1303 G:2.38 A:2.42mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067962 | 0 | 0
2026-02 | 2026-02-02 | Queensville Wells No. 3 and 4 | CENTRAL | Attending site to check Treated Free chlorine analyzer (W11621115). Push button switches were found to be inoperable. Replaced bush buttons and verified reading. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.023563 | ML: above threshold (no LLM available) — 0.024 |  | 0.023563 | 0 | 0
2026-02 | 2026-02-19 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for various work orders. Completed CL2 system inspection. Dechlor and and back flushed. Verified ammonia pumps dosing and volumes. Ok Ensured treated total is reading in signal average 2 and changed reagents. Trend is very variable, will continue to monitor remotely Trouble shooting well/generator with T Zimmerman-Jones | FLAG | stage2_low_confidence | 0.036484 | ML: above threshold (no LLM available) — 0.036 | work order [maintenance_action] | 0.036484 | 0 | 0
2026-02 | 2026-02-11 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Well 3 running in schedule mode Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Took weekly bacti samples Topped up mineral oil well 4 Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0909 G:2.56 A:2.54mg/L Effluent Free@0915 G:2.46 A:2.58mg/L Treated Free@0916 G:0.10 A:0.14mg/L Treated Total@0920 G:3.10 A:3.16mg/L Mono-2.55mg/L FA-0.07mg/L FA-0.57mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032318 | 0 | 0
2026-02 | 2026-02-10 | Queensville Wells No. 3 and 4 | CENTRAL | Onsite to investigate influence chlorine analyzer. 13:00 free analyzer reading 0.00 mg/l. Grab matching at 0.00. Will Mather?s onsite and cleaned silicate injections points. Total reading 0.61 mg/l. Contact tank has been back flushed briefly earlier. Replaced analyzer pinch tubes. Tested chlorine system to ensure dosing is correct. Back flushed contact tank after putting dechlore pucks in outfall. Once influence grabs reaching 0.94 mg/l total chlorine completed backflush. Ran well 3 in manual at 50 L/s. 15:10 verified influence chlorine grab 2.48. Analyzer at 2.50. 15:15 Been Hess onsite to relieve me. | FLAG | stage2_low_confidence | 0.016294 | ML: above threshold (no LLM available) — 0.016 |  | 0.016294 | 0 | 0
2026-02 | 2026-02-17 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Cleaned and confirmed flow to treated total analyzer after sporadic values this weekends trends. Will monitor Took weekly bacti and operational samples Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@1421 G:2.18 A:2.12mg/L Effluent Free@1424 G:2.60 A:2.48mg/L Treated Free@1427 G:0.18 A:0.15mg/L Treated Total@1430 G:3.48 A:3.42mg/L Mono-2.56 FA-0.03 TA-0.53mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061555 | 0 | 0
2026-02 | 2026-02-13 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check Standing water and damaged door noted in PAC room for well 3. Sent to SR Team lead Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Put NaSi pump 2 back in service Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1019 G:2.62 A:2,72mg/L Effluent Free@1021 G:0.15 A:0.14mg/L Treated Free@1024 G:0.07 A:0.06mg/L Treated Total@1028 G:2.62 A:2.74mg/L | FLAG | stage2_low_confidence | 0.0085549 | ML: above threshold (no LLM available) — 0.009 |  | 0.0085549 | 0 | 0
2026-02 | 2026-02-11 | Queensville Wells No. 3 and 4 | CENTRAL | -on site with total power to do the annual maintenance on generator. Placed unit in manual and notified ROC of alarms that will be present from our work (0900) finished test and placed unit back to auto and breaker closed 1500 let roc know and cleared alarms. Under direction of oic. | FLAG | stage2_low_confidence | 0.029236 | ML: above threshold (no LLM available) — 0.029 | alarm [control_system]; alarms [control_system] | 0.029236 | 0 | 0
2026-02 | 2026-02-19 | Queensville Wells No. 3 and 4 | CENTRAL | -on site to assist investigation of well 4 ESTOP alarm. As per Dan B email the Vfd panel did have a blown fuse. I replaced it and test ran it with Will m to confirm operation. We then did a gen test to see if we could replicate that problem from yesterday but had no luck in that. Both wells ran fine on generator power. Left site with both pumps in manual with Will. Under direction of oic. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for; Silicate hot flush, prime and backflush -JHSC -Refill eyewash fluid -Deep well exhaust inspections -Flow controls flushed and cleaned -CL2 leak detection completed during generator test, unable to run well 3 switched well duties and notified Tyler Generator tested under load fuel start 950L hours start 712.43 end 714 600 volts 60.0hz oil temp160'F oil pressure 85psi coolant 160'f | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | leak [infrastructure] | 0.0040096 | 0 | 0
2026-02 | 2026-02-18 | Queensville Wells No. 3 and 4 | CENTRAL | Onsite responding to both well 3 and well 4 fail to start/OOS. Able to get Well 3 to run by pressing ?auto? on the VFD beside the motor. Well 4 has an ?emergency stop alarm? without the E-stop being pressed. On the VFD it?s error is ?Run Enable Missing? check parameter 20.12 Leaving Well 4 OOS for the night will notify electricians. Well 3 running in Auto duty-ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; oos [equipment_failure]; alarm [control_system] | emergency [critical]; oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-12 | Queensville Wells No. 3 and 4 | CENTRAL | -on site to address the generator rad leak (1200) called roc to let them know we are on site and might cause alarms during troubleshooting. Tyler smith and myself found that the rad hose was loose and causing fluid to leak. We tightened connection and monitored. We test ran unit to confirm that the unit was not continuously leaking. I also changed the breaker that feeds the block heater as that seems to have failed. Cleared alarms and placed unit back to auto. Under direction of oic. | FLAG | stage2_low_confidence | 0.21202 | ML: above threshold (no LLM available) — 0.212 | failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | 0.21202 | 0 | 0
2026-02 | 2026-02-10 | Queensville Wells No. 3 and 4 | CENTRAL | On site to remove and replace Well 4 motor in response to vibration issues. Test ran to waste. | FLAG | stage2_low_confidence | 0.022353 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.022353 | 0 | 0
2026-02 | 2026-02-20 | Queensville Wells No. 3 and 4 | CENTRAL | On site to respond to power issue with Queensville wealth for Control cabinet. Tested voltage and amp draw. Checked for correct fuse size installation. Seems to be OK now. | FLAG | stage2_low_confidence | 0.022838 | ML: above threshold (no LLM available) — 0.023 |  | 0.022838 | 0 | 0
2026-02 | 2026-02-20 | Queensville Wells No. 3 and 4 | CENTRAL | Station Check (no issues found) Input data to PWQ 10:17 Verified CL17s (mg/l) Influent Free: Grab 2.60, A 2.66 Effluent Free: Grab 0.12, A 0.14 Treated: Free Grab 0.04, A 0.06 Total: 2.58, A 2.66 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047913 | 0 | 0
2026-02 | 2026-02-05 | Queensville Wells No. 3 and 4 | CENTRAL | On site to commission well 4 with Dan boate, Kyle Rae and William Mather Updated Ethernet cards with latest firmware Tested well 4 VFD in SCADA manual and checked if PID tuning works. Tested Well 3 VFD analog data and comms, set up well 3 vfd parameters for comms Wells are back in auto and no alarms present | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; alarms [control_system] | scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | Queensville Wells No. 3 and 4 | CENTRAL | Was onsite earlier to finish up getting Wells 3 and 4 running. Put chlorine dosing into manual during startup. Had Influent and effluent free chlorine analyzers in signal average 1 on initial startup. Once system seemed balanced, put the chlorine dosing back to auto and the analyzers signal average back to 2. Leaving the well manual running until it passes through the contact tank | FLAG | stage2_low_confidence | 0.010463 | ML: above threshold (no LLM available) — 0.01 |  | 0.010463 | 0 | 0
2026-02 | 2026-02-05 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 4 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1335 G:2:72 A:2.60mg/L Effluent Free@1338 G:0.41 A:0.40 mg/L Treated Free@1339 G:0.08 A:0.05mg/L Treated Total@1343 G:2.52 A:2.44mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064882 | 0 | 0
2026-02 | 2026-02-05 | Queensville Wells No. 3 and 4 | CENTRAL | On site to commission new VFD for W4. Also worked with PCS to get Ethernet connection working with W3. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-06 | Queensville Wells No. 3 and 4 | CENTRAL | -on site with water maintenance team to investigate the vibration issues. We tested p3 for a cycle and noticed the vibration and pressure that it is pumping out. Once the ct tank had finished pumping we then ran p4 to test first test at 1300 we found that the waste valve faulted the pump. We tried putting the pump to manual speed and closing the discharge valve to see if the vibration changed but noticed no difference. We then had it test in auto speed and closing the valve but noticed change in vibration was noted. We finished our test 1430 once the ct tank finished and left the pump in manual for the weekend. We would like to do more testing Monday. I let Justin Q know and he is going to notify the oncall operator. Under direction of oic. | FLAG | stage2_low_confidence | 0.29725 | ML: above threshold (no LLM available) — 0.297 | fault [equipment_failure]; faulted [equipment_failure]; vibration [equipment_failure] | 0.29725 | 0 | 0
2026-02 | 2026-02-06 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0947 G:2.54 A:2.58mg/L Effluent Free@0951 G:0.16 A:0.14mg/L Treated Free@0951 G:0.05 A:0.05mg/L Treated Total@0955 G:2.34 A:2.38mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064789 | 0 | 0
2026-02 | 2026-02-09 | Queensville Wells No. 3 and 4 | CENTRAL | -on site to troubleshoot well 4 vibration. With iws we tested the pump running to system (1000) called roc to inform them of work being done. We ran the well at about 70l/s for about 30mins for testing to see if we could replicate the vibration of the motor. We also ran the motor at various speeds. No major alarms were noted. Did have an hi turbidity alarm come in we acknowledged it at 1115. We did run the motor decoupled to the pump for further testing. Our tests determined we should try replacing the motor. We left the motor decoupled and in manual off for the evening. Under direction of oic. | FLAG | stage2_low_confidence | 0.19724 | ML: above threshold (no LLM available) — 0.197 | vibration [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.19724 | 0 | 0
2026-02 | 2026-02-05 | Queensville Wells No. 3 and 4 | CENTRAL | On-site to collect weekly bacti samples. Will return to complete full station and equipment check after delivery of samples. | FLAG | stage2_low_confidence | 0.018229 | ML: above threshold (no LLM available) — 0.018 |  | 0.018229 | 0 | 0
2026-02 | 2026-02-09 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found. Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Tyler and crew on-site to trouble wells. Frozen waste, managed to get thawed and flows Took operational sample Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1313 G:2.68 A:2.73 Effluent Free@1321 G:2.58 A:2.61 Treated Free@1323 G:0.12 A:0.14 Treated Total @1324 G:3.40 A:3.34 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058542 | 0 | 0
2026-02 | 2026-02-06 | Queensville Wells No. 3 and 4 | CENTRAL | Check vibrating motor number 4 | FLAG | stage2_low_confidence | 0.0096479 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096479 | 0 | 0
2026-02 | 2026-02-27 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | - on site to complete station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 09:05 -free cl: 0.06mg/l -total cl: 1.90mg/l -man/start pump 2 -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044454 | 0 | 0
2026-02 | 2026-02-25 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site to complete station check and collect weekly bacti W11620180 -checked trends: -entered readings in PWQ -took grab and sample from east cell 14:15 -free cl: 0.04mg/l -total cl: 1.38mg/l -west cell grab 15:20 -free cl: 0.06mg/l -total cl: 1.42mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004681 | 0 | 0
2026-02 | 2026-02-25 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | Onsite to try and repair limitorque valve actuator in resevoir pipe gallery. Could not make any progress. Valve actuator still out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; repair [maintenance_action] | out of service [equipment_failure]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-26 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site to repair malfunctioning actuator with replacement control board. Tested ok. Actuator back on service, left in open position in local mode. | FLAG | stage2_low_confidence | 0.036092 | ML: above threshold (no LLM available) — 0.036 | repair [maintenance_action] | 0.036092 | 0 | 0
2026-02 | 2026-02-23 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | Onsite for station check Checked residuals mg/l @1435 Total grab 1.82 Free grab 0.01 P1 in local oos | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 09:20 -free cl: 0.07mg/l -total cl: 1.75mg/l -equipment and heating all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049594 | 0 | 0
2026-02 | 2026-02-11 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site to complete station check and weekly bacti W11588844 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample east cell 14:10 -free cl: 0.0.6mg/l -total cl: 1.62mg/l - west cell grab 14:15 -free cl: 0.10mg/l -total cl: 1.60mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049879 | 0 | 0
2026-02 | 2026-02-18 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site for station check -checked trends all ok -entered reading in PWQ: all ok -took chlorine grab 13:30 -free cl: 0.07mg/l -total cl: 1.83mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046731 | 0 | 0
2026-02 | 2026-02-20 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 14:05 -free cl: 0.03mg/l -total cl: 1.65mg/l -man/start to pump 2 to listen pump - minimal cavitation -will leave pump running for 30 minutes | FLAG | stage2_low_confidence | 0.010353 | ML: above threshold (no LLM available) — 0.01 | cavitation [equipment_failure] | 0.010353 | 0 | 0
2026-02 | 2026-02-16 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -wrong entry | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051267 | 0 | 0
2026-02 | 2026-02-10 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site attending comm fail -reservoir 4.64 M -power restored -historian heart outstanding -Ian Williams will clear -site is trending- confirmed with ROC | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-17 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site for station check and weekly bacti W11605685 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample west cell 12:55 -free cl: 0.11mg/l -total cl: 1.43mg/l -east cell grab 13:00 -free cl: 0.12mg/l -total cl: 1.52mg/l -adjusted top floor heater- area was over 30C -no other issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048844 | 0 | 0
2026-02 | 2026-02-13 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 11:10 -free cl: 0.09mg/l -total cl: 1.72mg/l -ran pump 3 to check cavitation -took video- placed pump in man/off | FLAG | stage2_low_confidence | 0.0093988 | ML: above threshold (no LLM available) — 0.009 | cavitation [equipment_failure] | 0.0093988 | 0 | 0
2026-02 | 2026-02-03 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | Locked out pump 1 and unwired motor. This pump and motor set with be coming out for a complete refurbishment. Isolated inlet and began draining. | FLAG | stage2_low_confidence | 0.016419 | ML: above threshold (no LLM available) — 0.016 |  | 0.016419 | 0 | 0
2026-02 | 2026-02-07 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | Attended station with security to investigate intrusion alarm- noticed pumping station bay doors not locked properly, lock not connected to latch causing the door to rattle. Placed a temporary lock and zip ties to prevent door from rattling- station fully secured. Will inform maintenance to fix latch. Informed ROC. No outstanding alarms onsite. | FLAG | stage2_low_confidence | 0.040228 | ML: above threshold (no LLM available) — 0.04 | alarm [control_system]; alarms [control_system] | 0.040228 | 0 | 0
2026-02 | 2026-02-09 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | Tested flood alarm Deactivated Jefferson duty Ran pumps Inspected actuated valves and check calves of pumps 2&3 Reactivated duty after Tested hi/lo temp in reservoir Deactivated duty Exercised actuated valve to cell 1 Cell 2 cable faulted with no power tried flipping breaker Exercised manual valves Tested sump Completed jhsc | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] | flood [critical]; fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-04 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -On-site to complete reservoir station check and collect sample -reservoir level = 85%, filling -checked equipment -reviewed trends -found RES_MV1 with no power to actuator, created work order for CMS -collected grab samples: 08:34 - East Cell: Free Chlorine = 0.03 mg/L Total Chlorine = 1.53 mg/L 08:37 - West Cell: Free Chlorine = 0.02 mg/L Total Chlorine = 1.52 mg/L MCL = 1.33 mg/L TNH3 = 0.34 mg/L FNH3 = 0.08 mg/L NO2 = 0.000 mg/L temp = 7.6 08:40 - collected weekly regulatory micro. sample from West Cell - W/O # W11568536 -recorded readings in PWQ sheet -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; regulatory [regulatory] | 0.004631 | 0 | 0
2026-02 | 2026-02-06 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site to complete PS station check -pumps manual off, pump #1 OOS -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 13:36 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.78 mg/L -no issues found | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-25 | Richmond Hill Bloomington Elevated Tank | CENTRAL | Deleted entry. This entry was intended for coons tower. | FLAG | stage2_low_confidence | 0.014258 | ML: above threshold (no LLM available) — 0.014 |  | 0.014258 | 0 | 0
2026-02 | 2026-02-25 | Richmond Hill Bloomington Elevated Tank | CENTRAL | On-site for station check and sampling. MBHP - W11620030. 13:28 Tower level 62% and filling at 78 l/s. 13:30 Verified inlet analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.95 Analyzer: 1.95. 13:38 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.04. Total chlorine grab: 1.84. analyzer: 1.87. Free ammonia: 0.09 Total ammonia: 0.41 Monochloramine: 1.64. Nitrite: 0.003. pH: 7.98. Recorded readings into PD sheets. Station and equipment: No issues identified. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0021985 | 0 | 0
2026-02 | 2026-02-11 | Richmond Hill Bloomington Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s(mg/L) 3:15 oultlet: Free: Grab 0.05 Total: Grab 1.78, A 1.82 3:20 Inlet: Free: Grab 0.06 Total: Grab 1.92, A 1.99 3:25 #11588694 bact. & operational samples Heat trace (inlet and outlet) cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025868 | 0 | 0
2026-02 | 2026-02-18 | Richmond Hill Bloomington Elevated Tank | CENTRAL | Informed ROC (Angelica) onsite to complete monthly Maximo workorders CL17 maintenance/cleaning in CAL mode start @ 12:55 pm Took grabs @ 1:30 pm to verify analyzers Inlet Total: 1.90 mg/l Outlet Total: 1.80 mg/l Cl17?s both back in seevice No adjustment necessary JHSC inspection - no issues Housekeeping Valve excercise Low temp alarm test - ok Heat trace inspection - ok Recirc pump excercise complete ET ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0049433 | 0 | 0
2026-02 | 2026-02-17 | Richmond Hill Bloomington Elevated Tank | CENTRAL | On-site for station check and sampling. MBDW - W11605549. 10:22 Tower level 69% and draining at 92 l/s. 10:24 Verified inlet analyzer (mg/l): Free chlorine grab: 0.07. Total chlorine grab: 2.05. Analyzer: 1.99. 10:34 Verified outlet analyzer (mg/l) and collected sample. (correction to add when sample was collected). free chlorine grab: 0.05. Total chlorine grab: 1.74. analyzer: 1.77 Free ammonia: 0.08 Total ammonia: 0.40. Monochloramine: 1.59. Nitrite: 0.000. Temperature: Celsius. pH: 7.99 Recorded readings into PD sheets. Station and equipment: No issues identified. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025684 | 0 | 0
2026-02 | 2026-02-04 | Richmond Hill Bloomington Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Weekly bacti sample taken while draining Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Total@1304 G:1.71 A:1.79mg/L Outlet Total@1307 G:1.82 A:178mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065208 | 0 | 0
2026-02 | 2026-02-25 | Richmond Hill Coon's Elevated Tank | CENTRAL | On-site for station check and sampling. W11620030 14:17 Tower level 66% and filling at 115 l/s. 14:18 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.96. Analyzer: 2.01. 14:25 verified outlat analyzer and collected sample. free chlorine grab: 0.08. Total chlorine grab: 1.80. Analyzer: 1.81. Ph: 8.03 Free ammonia: 0.09 Total ammonia: 0.41 Monochloramine: 1.66. ?Nitrite: 0.003. Temperature: 7.0 celsius. Recorded data in process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030853 | 0 | 0
2026-02 | 2026-02-26 | Richmond Hill Coon's Elevated Tank | CENTRAL | Onsite to complete monthly Maximo workorders Informed ROC (Carter D) of ongoings Cleaned both Inlet/Outlet CL17 analyzers in Cal mode from 9 am - 9:30 am Took grabs @ 9:30 am Inlet Total: 1.95 mg/l Outlet Total: 1.85 mg/l Standardized outlet only to match grabs Reagents ok JHSC inspection no issues found General housekeeping complete ET ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005647 | 0 | 0
2026-02 | 2026-02-11 | Richmond Hill Coon's Elevated Tank | CENTRAL | Station Check (no other issues found) Input data to PWQ 13:30 Verified CL17s (mg/l) Inlet: Free Grab: 0.05 Total: Free Grab 1.92, A 1.99 Outlet: Free Grab 0.05 Total: Grab 1.88, A 1.90 13:40 # 11588694 bact. and operational samples Inlet heat trace active alarm (will monitor) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0044623 | 0 | 0
2026-02 | 2026-02-17 | Richmond Hill Coon's Elevated Tank | CENTRAL | On-site for station check and sampling. MBHP - W11605549 Outstanding inlet riser heat trace low temp alarm. Cleared alarm with no issues. Heat trace is on. 09:14 Tower level 65% and draining at 89 l/s. 09:17 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.88. Analyzer: 1.96. 09:29 verified outlat analyzer and collected sample. free chlorine grab: 0.05. Total chlorine grab: 1.77. Analyzer: 1.76. Ph: 7.98 Free ammonia: 0.09 Total ammonia: 0.40 Monochloramine: 1.56 ?Nitrite: 0.003. Temperature: 5.6 Celsius. Recorded data in process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0030593 | 0 | 0
2026-02 | 2026-02-04 | Richmond Hill Coon's Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Took weekly bacti sample while draining Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Total@1342 G:1.76 A:1.81mg/L Outlet Total@1444 G:1.75 A:1.75mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065194 | 0 | 0
2026-02 | 2026-02-26 | Richmond Hill Pugsley Pumping Station | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 14:58 FCl: 0.03 mg/L TCl: 1.57 mg/L Duty active , pumps 1,4 Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-23 | Richmond Hill Pugsley Pumping Station | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 09:13 FCl: 0.04 mg/L TCl: 1.55 mg/L Duty not active Equipment OOS: Cell 2 valve (RSR2_MV1) - refer to central team for details Facility OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.002797 | 0 | 0
2026-02 | 2026-02-02 | Richmond Hill Pugsley Pumping Station | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 13:55 FCl: 0.08 mg/L TCl: 1.57 mg/L Pump 1 and 4 active in duty 1 Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Richmond Hill Pugsley Pumping Station | EAST | Check air pressure in check valves Add air to check valves 1 2 and 3 | FLAG | stage2_low_confidence | 0.0096655 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096655 | 0 | 0
2026-02 | 2026-02-20 | Richmond Hill Pugsley Pumping Station | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks - Comprehensive house cleaning - Control panel lights inspection Data in PWQ Workbook Grabs @ 14:28 FCl: 0.06 mg/L TCl: 1.56 mg/L Pump 2 and 3 active in duty 1 Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-19 | Richmond Hill Pugsley Pumping Station | EAST | Under direction of OIC Dan Zhou On site for; - Generator test - JHSC Health and Safety Inspection - Flood alarm test - Surge anticipator test (PRV) test - Flood Alarm test - Hoist inspection - Station check - butterfly valve exercise 1,2,3,4 Generator Test: @ 13:04 placed pump 2 in manual, and pump 1,3,4 in manual off Start hours: 377.6 Start time: 13:13 hrs. Stop Hours: 378.9 (includes cool down time) Stop Time: 14:33 hrs. Run Time: 1 hr. 20. mins. Start Fuel: 6431 L Stop Fuel: 6500 L (LIT not accurate) Pre run checks; Battery Cell Levels: NA Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 13:39 hrs. Put pump 2 in Manual On (Active), Generator under load @ 14:09 hrs. put pump 2 in manual off Operating Current: 29 amps Operating Frequency: 60 Hz Operating Voltage: 600 Volts, Engine speed: 1798 RPM Water/coolant Temp: 160 f Oil Pressure: 65 psi kPa Oil temp: 176 f Grab Samples taken @ 13:58 hrs. FCl: 0.05 mg/L TCl: 1.57 mg/L Surge anticipators; - Discharge side surge anticipators function - Control panel for suction side surge anticipators does not function, informed lead hand Dan Zhou, and they had created a work order @ 14:34 returned pumps 1,2,3,4 to auto Pumps 3,4 active in duty 1 Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | flood [critical]; fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-13 | Richmond Hill Pugsley Pumping Station | EAST | Under Direction of OIC Joe Mazza On Site for; - Station checks Data in PWQ Workbook Grabs @ 11:55 hrs. FCl: 0.06 mg/L TCl: 1.64 mg/L Pump 4 and 3 active in duty 1 Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Richmond Hill Pugsley Pumping Station | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 14:38 FCl: 0.07 mg/L TCl: 1.58 mg/L Pump 2 and 3 active in duty 1 Equipment OOS: RSR2_MV1 for cell 2, contact central for details Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-06 | Richmond Hill Pugsley Pumping Station | EAST | Under direction fo OIC Dan Zhou On site for; - Station checks Data in PWQ workbook Grabs @ 14:46 FCl:0.08 mg/L TCl: 1.58 mg/L Duty active pumps 2,3 in duty 1 Equipment OOS: Cell 2 valve in local open due to power failure Feb. 5 2026, disregard fail to open alarm, work order has been created. Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] | failure [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-03 | Richmond Hill Pugsley Pumping Station | EAST | Vibration readings | FLAG | stage2_low_confidence | 0.021831 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021831 | 0 | 0
2026-02 | 2026-02-25 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Trends checked and ok, equipment checked and ok All measurements are in mg/l HL - time :9:45 Free grab 0.05 Total grab 3.50 vs analyzer 3.55 Mono 2.10 Bact sample grabbed - 10:20 Reservoir - time 10:30 Free grab 0.01 Total grab 3.80 vs 3.76 analyzer Mono 3.60 Post injection time 10:45 Free grab 0.03 Total grab 2.33 vs analyzer 2.28 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012661 | 0 | 0
2026-02 | 2026-02-12 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Under the direction of Jacob Muzzin, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a network panel for SHTP3 and Control panel for Well 2 building. Provided 24 VDC power to new switch from 24VDC power supply. Informed the ROC regarding possible comm fail alarm. After the replacement, checked all the ports and reset the comm alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Changed cl2 cylinder with J. Bloye | FLAG | stage2_low_confidence | 0.0097856 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097856 | 0 | 0
2026-02 | 2026-02-23 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Trends checked and ok, equipment checked and ok All measurements are in mg/l High lift - time: 9:57 Free grab 0.03 Total grab 3.39 vs 3.48 analyzer Mono 2.96 Reservoir - time 10:10 Free grab 0.06 Total grab 3.66 vs analyzer 3.71 Mono 3.08 Post filter - time 10:27 Free grab 0.02 Total grab 2:18 vs analyzer 2:26 Topped up KMNO tank to 82.3 cm (369 L) - 2:45 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012202 | 0 | 0
2026-02 | 2026-02-27 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite for station check Checked residuals mg/l Hl @0928 Total analyzer 3.41 grab 3.42 Free grab 0.06 Mcl grab 2.91 Reservoir @1311 Total analyzer 3.79 grab 3.88 Free grab 0.10 Mcl grab 3.62 Through plant @1325 Total analyzer 2.24 grab 2.34 Free grab 0.07 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00060968 | 0 | 0
2026-02 | 2026-02-27 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | 09:51- ROC called regarding filter 3 turbidity being high after backwash. CMU 5 W11695345 issued. attended site, cleaned vial, flushed line and verified with std, and then replaced the vial for filter 3 turbidity meter. value remained high. Noticed flow to the analyzer was considerably low (0.35l/s) , increased the flow to 58l/s . Noticed Turbidity value coming down. | FLAG | stage2_low_confidence | 0.028403 | ML: above threshold (no LLM available) — 0.028 |  | 0.028403 | 0 | 0
2026-02 | 2026-02-02 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Hl @1224 Total analyzer 3.44 grab 3.46 Free grab 0.03 Mcl grab 2.85 Reservoir @1227 Total analyzer 3.77 grab 3.80 Free grab 0.06 Through plant @1236 Total analyzer 2.31 grab 2.24 Free grab 0.06 Topped up kmno tank Rotated reservoir cells | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00080521 | 0 | 0
2026-02 | 2026-02-27 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | W11620255- SWO on call 08:00 -consultation call regarding Filter 3 turbidity high. 08:30- Advised ROC to initiate backwash. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039728 | 0 | 0
2026-02 | 2026-02-02 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Eat 0.14 nitrate 0.296 nitrite 0.000 ammonium 2.36 Hl 0.17 nitrate 0.172 nitrite 0.000 ammonium 2.65 F3 0.15 F2 0.09 F1 0.11 Raw 1.80 ammonium 2.96 W4 1.99 ammonium 3.33 W2 1.48 ammonium 2.66 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005708 | 0 | 0
2026-02 | 2026-01-06 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Review UV alarm monthly summary and power failure from January 6th. System appears to have interlocked and shut down normally. Flow registered for 30 seconds during shutdown while UV dose went below 40mj/cm2. Non reportable, no compliance issues. | FLAG | stage2_low_confidence | 0.026242 | ML: above threshold (no LLM available) — 0.026 | failure [equipment_failure]; compliance [regulatory]; alarm [control_system] | 0.026242 | 0 | 0
2026-02 | 2026-02-18 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site for the scheduled PM work orders with D. Simm. Informed ROC about the work being done. W11583827 SHTP, Electric Actuated Valves Inspection, Schomberg WTP W3&4 W11583844 SHTP, Exhaust Fan Inspection, Schomberg WTP W3&4 W11583871 SHTP, Check Valves Inspection, Schomberg WTP W3&4 W11583887 SHTP, Dehumidifier Inspection, Schomberg WTP W3&4 W11591705 SHTP, Fire Pumps and Motors, Inspection, W11602054 SHTP W2, Pressure Relief Valve, Inspection Topped up KMNO4 tank 1- 16.04cm/71.72L to 81.6cm/ 365L | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; work order [maintenance_action] | fire [critical]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-19 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site for step test with water resources on well 3 Started well 3 at approximately 9 L/s Reduced plant flow from 18 to 9 l/s Reduced filters in production from 2 to 1 In order to maintain level in raw water tank For the duration of step test put post uv cl2 dosage to manual Increased flow to 18l/s manipulated plant to continue flow. Increased to 26l/s hi flow alarm came in. Stopped well and plant for hour long quiet period After that placed set points back to normal and restarted plant | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069222 | 0 | 0
2026-02 | 2026-02-13 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite for station check Checked residuals mg/l Hl @0851 Total analyzer 3.47 grab 3.48 Free grab 0.03 Mcl grab 3.10 Reservoir @0904 Total analyzer 3.78 grab 3.74 Free grab 0.02 Mcl grab 3.41 Through plant @0912 Total analyzer 2.28 grab 2.32 Free grab 0.06 Tested well 3 at various flows in prep for step test - High flow alarm came in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00048748 | 0 | 0
2026-02 | 2026-02-17 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite for station check and to collect weekly micro W11605647 Hl @0920 Total analyzer 3.55 grab 3.52 Free grab 0.04 Mcl grab 3.05 Reservoir @0926 Total analyzer 3.67 grab 3.70 Free grab 0.05 Mcl grab 3.37 Through plant @0929 Total analyzer 2.29 grab 2.30 Free 0.05 Rotated reservoir cells closed north opened south Changed reagents in reservoir cl17sc analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00085525 | 0 | 0
2026-02 | 2026-02-16 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Responding to reservoir chlorine analyzer fault. Worked with ROC to rotate sample pumps and run both pumps to see if alarm would clear. Alarm came back in repeatedly but analyzer appeared to be trending. Found sample P2 tubing leak. Replaced tubing and primed. Reservoir analyzer reagent level low. Unable to replace, no spare reagents on site. Should last until tomorrow, will request operator bring reagents and spares to site and stock as required. Residuals: mg/L 1450 Reservoir A: tcl 3.81 G: tcl 3.64 Span calibrate reservoir Cl17sc to 3.64 from 3.81mg/L based on grabs (at 1504, value after was 3.79mg/L). Cleaned Treated NTU analyzer sample vial, clears vial clarity alarm. (Was faulted on SCADA, still trending values). Chlorine dosing is in Manual setting, will request switch to auto dosing (post-UV) once reservoir Cl17 is checked again on next station check. | FLAG | stage2_low_confidence | 0.077768 | ML: above threshold (no LLM available) — 0.078 | fault [equipment_failure]; faulted [equipment_failure]; scada [control_system]; alarm [control_system]; leak [infrastructure] | 0.077768 | 0 | 0
2026-02 | 2026-02-11 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite for station check and to collect weekly micro sample W11588872 Through plant @0923 Total analyzer 2.29 grab 2.25 Free grab 0.05 Reservoir @0952 Total analyzer 3.77 grab 3.80 Free grab 0.06 Mcl grab 3.37 High lift @1031 Total analyzer 3.58 analyzer 3.50 Free grab 0.05 Rotated well duty to collect bact sample | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00083407 | 0 | 0
2026-02 | 2026-02-18 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -received call from ROC regarding step test interim -override stop set point adjusted 5.1m to 5.3m - pump 2 not adjusting to 17l/s adjustment - manual speed set from 70% to 92% for 17.1l/s - reservoir high level adjusted from 90% to 85% to warn ROC to activate high lift | FLAG | stage2_low_confidence | 0.0074875 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074875 | 0 | 0
2026-02 | 2026-02-10 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite to complete work orders Completed jhsc on well 2 Inspected actuated valves at well 2 no issues Inspected high lift pumps 1,2 &5 Checked check valves , added air to valves for p1&5 Topped up kmno tank 1 Started plant duty @1232 power blip occurred Ack reset most alarms to get plant going When arrived back on site Kmno p2 oos had to unplug and plug back in. Reservoir low level came but started to recover | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Trends checked good, reagent and equipment in good levels and conditions All readings measured in mg/l HL - time: 10:08 am free grab 0.03 Total grab 3.51 vs analyzer 3.54 Mono 3.06 Reservoir - time: 10:35 Free grab 0.05 Total grab 3.59 vs analyzer 3.64 Mono 3.37 Post filter - time : 10:42 Free grab 0.03 Total grab 2.19 vs. Analyzer 2.23 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00185 | 0 | 0
2026-02 | 2026-02-15 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Respond to KMNO P1 leakage alarm. KMNO tank 2 level at 16, pump keeps switch back to duty 2 due to tank level. Replace P1 tube element, prime and test. Place back in duty 1. Fill KNNO tank 2 from 15cm to 82cm and mix. Reset run hours on KMNO P1 to track tube element changes and hours to failure. | FLAG | stage2_low_confidence | 0.056373 | ML: above threshold (no LLM available) — 0.056 | failure [equipment_failure]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | 0.056373 | 0 | 0
2026-02 | 2026-02-05 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite to complete work orders Monthly generator run Start Fuel 83.8/83.7 cm 1614/1611 L Hrs 541.5 Ran high lifts in duty to put on load Stop Fuel 83.7/83.7 cm 1611/1589 L Hrs 543.0 Did chlorination system inspection no issues observed Changed from using chlorinator 4 in duty to chlorinator 2 Checked cl2 leaks and scrubber no issues observed Accepted cl2 cylinder delivery Received 12 12 empty taken away Noticed Kmno tank 2 filling whole tank/pump 1 in duty. Rotated duties because it was higher than the changeover level. Will continue to monitor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; leak [infrastructure] | 0.0006291 | 0 | 0
2026-02 | 2026-02-11 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Chris Iliohan Tyler Smith. In to complete PM on air compressor and close openings on raw water tank lid work is completed | FLAG | stage2_low_confidence | 0.030636 | ML: above threshold (no LLM available) — 0.031 | sso [critical] | 0.030636 | 0 | 0
2026-02 | 2026-02-03 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -on site to complete work orders -completed Scrubber System Valves, Exercise -completed UVT lens cleaning and unit flush -completed Transfer Pump and Motor Inspection -completed Transfer Pump Air Relief Valves Inspection -replaced uv#3 lamp #1 due to being close to 5000 hour runtime, reset hours | FLAG | stage2_low_confidence | 0.0074637 | ML: above threshold (no LLM available) — 0.007 | work order [maintenance_action] | 0.0074637 | 0 | 0
2026-02 | 2026-02-08 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite to clear treated ntu fault | FLAG | stage2_low_confidence | 0.02024 | ML: above threshold (no LLM available) — 0.02 | fault [equipment_failure] | 0.02024 | 0 | 0
2026-02 | 2026-02-09 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Station checks Equipment checked and ok, trends checked and ok High lift analyzer Time: 11:00 Free: grab 0.06 Total: grab 3.46 vs analyzer 3.51 Mono 2.99 Reservoir Time: 11:15 Free: grab 0.07 Total: grab 3.74 vs analyzer 3.80 Mono 3.33 Post filter Time: 11:31 Free: grab 0.03 Total: grab 2.25 vs analyzer 2.30 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011093 | 0 | 0
2026-02 | 2026-02-06 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to complete station check Checked residuals mg/l Hl @0802 Total analyzer 3.41 grab 3.50 Free grab 0.05 Mcl grab 3.03 Through plant @1019 Total analyzer 2.23 grab 2.19 Free grab 0.04 Reservoir @1034 Total analyzer 3.67 grab 3.70 Free grab 0.09 Mcl grab 3.33 Continued troubleshooting Kmno system Changed check valve in suction side of pump leading to tank Noticed level contributed to climb when not in duty Replaced prv Topped up kmno tank 2 Changed cl2 cylinder with J Bloye Cl2 weight 63 to 130 kg | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00031204 | 0 | 0
2026-02 | 2026-02-04 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite for station check and to collect weekly micro sample and iron & manganese samples W11568498 W11568659 W11152974 Plant was shutting off on arrival tried to manipulate and keep wells going but didn?t start filter duty quick enough and raw water tank hihi came in Checked residuals mg/l High lift @0938 Total analyzer 3.47 grab 3.56 Free grab 0.03 Mcl grab 3.16 Through plant @1000 Total analyzer 2.38 grab 2.36 Free grab 0.03 Reservoir @1004 Total analyzer 3.71 grab 3.82 Free grab 0.06 Mcl grab 0.07 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00081432 | 0 | 0
2026-02 | 2026-02-03 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Onsite to complete work orders Deactivated plant Completed Kmno injection point cleaning Completed inspection of Kmno pumps Ran to sight glass to check max flow / min P1 100% 405 50% 390 15% 370 P2 100% 385 50% 390 15% 370 Reduced p2 max flow to 395 ml/min from 405 Cleaned cl17sc analyzers Grabs before Reservoir 3.69 grab 3.50 Hl analyzer 3.41 grab 3.40 After Reservoir analyzer 3.64 grab 3.60 Hl analyzer 3.01 grab 3.04 Reactivated plant Completed monthly up sensor check | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.00033686 | 0 | 0
2026-02 | 2026-02-27 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: -verified pre analyzer 11:00 -analyzer free: 0.07mg/l grab: 0.06mg/l -analyzer total: 1.52mg/l grab: 1.55mg/l -reagents all ok -verified post analyzer 11:10 -analyzer free: 0.04mg/l grab: 0.06mg/l -analyzer total: 1.57mg/l grab: 1.60mg/l -reagents all ok -verified chemscan: all ok -reagents all ok -topped up ammonia tank 2 - 15-75cm -completed housekeeping | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038276 | 0 | 0
2026-02 | 2026-02-23 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Onsite for station check Duty active Checked residuals mg/l Pre @1207 TCL analyzer 1.52 grab 1.54 Fcl analyzer 0.07 grab 0.07 Mcl analyzer 1.46 grab 1.46 F nh3 analyzer 0.09 grab 0.05 T nh3 analyzer 0.37 grab 0.34 Post @1215 TCL analyzer 2.10 grab 2.11 Fcl analyzer 0.08 grab 0.06 Mcl analyzer 1.99 grab 1.95 F nh3 analyzer 0.04 grab 0.07 T nh3 analyzer 0.49 grab 0.46 Topped up ammonia tank 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00069454 | 0 | 0
2026-02 | 2026-02-25 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site for station check and weekly bacti W11620180 -checked trends trends: all ok -entered reading in PWQ: all ok -took sample and grab from north cell 10:50 -free cl: 0.06mg/l -total cl: 2.05mg/l -west cell grab 10:55 -free cl: 0.07mg/l -total cl: 2.08mg/l -south cell 11:00 -free cl: 0.10mg/l -total cl: 2.10mg/l -equipment all ok -completed station check of rechlor building -checked trends: all ok -entered reading in PWQ: all ok -verified pre analyzer 12:20 -analyzer free: 0.07mg/l grab: 0.08mg/l -analyzer total: 1.52mg/l grab: 1.48mg/l -reagents all ok -verified post analyzer 12:40 -analyzer free: 0.08mg/l grab: -analyzer total: 2.06mg/l grab: 2.14mg/l - adjusted -reagents all ok -verified chemscan: all ok -reagents all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0018342 | 0 | 0
2026-02 | 2026-02-02 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified pre- analyzer 10:45 -analyzer free: 0.05mg/l grab: 0.08mg/l -analyzer total: 1.53mg/l grab: 1.55mg/l -reagents all ok -verified post analyzer 10:55 -analyzer free: 0.03mg/l grab: 0.01mg -analyzer total: 1.60mg/l grab: 1.58mg/l -reagents all ok -verified chemscan: all ok -reagents all ok -topped up ammonia tank 1 15-75cm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041442 | 0 | 0
2026-02 | 2026-02-19 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to receive cylinder delivery - received 14/sent 15 -no issues -troubleshooting high free post ammonia -verified chemscan 12:40 - free ammonia - 0.17mg/l grab: 0.07mg/l - adjusted (0.14 - 0.04) -changed cylinder with Benson S - 46.8kg - 114.7kg | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00704 | 0 | 0
2026-02 | 2026-02-13 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Informed ROC and operations. Onsite to perform annual calibration on Chemscan analyzer. Used the calibration mode. Verified the analyzer and no adjustments made. Put everything back in service. No issues. Informed ROC, armed the building and left the site. | FLAG | stage2_low_confidence | 0.0083374 | ML: above threshold (no LLM available) — 0.008 |  | 0.0083374 | 0 | 0
2026-02 | 2026-02-19 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | completed PM work order. informed ROC beforehand W11562858 RHRSTR, JHSC Health and Safety Inspection, East Vaughan BPS | FLAG | stage2_low_confidence | 0.01477 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action] | 0.01477 | 0 | 0
2026-02 | 2026-02-17 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Onsite to wrap up annual calibrations Informed ROC and operations Used cal mode on scada during the calibrations Completed chlorine room instruments: WIT, gas detectors and chlorinators. Also completed RES FIT Cleared associated alarms No issues Informed ROC, armed building and left site | FLAG | stage2_low_confidence | 0.023947 | ML: above threshold (no LLM available) — 0.024 | sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.023947 | 0 | 0
2026-02 | 2026-02-20 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified pre analyzer 13:05 -analyzer free: 0.08mg/l grab: 0.07mg/l -analyzer total: 1.79mg/l grab: 1.80mg/l -topped up KI -verified post analyzer 13:15 -analyzer free: 0.09mg/l grab: 0.11mg/l -analyzer total: 2.64mg/l grab: 2.44mg/l - adjusted -topped up KI -verified chemscan - adjust post mono 2.12- 2.21mg/l (-0.06 - 0.03 offset) reagents all ok -electrician on site to investigate source line not available - all equipment in station and surrounding area all ok -power restored 13:35 -ammonia chemical system all ok | FLAG | stage2_low_confidence | 0.0073649 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073649 | 0 | 0
2026-02 | 2026-02-17 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site for re-chlor station check -checked trends: all ok -entered readings in PWQ: all ok -verified pre analyzer 13:20 -analyzer free: 0.13mg/l grab: 0.07mg/l - adjusted -analyzer total: 1.53mg/l grab: 1.52mg/l -reagents all ok -verified post analyzer 13:40 -analyzer free: 0.08mg/l grab: 0.08mg/l -analyzer total: 2.38/l grab: 2.34mg/l -reagents all ok -chemscan verified: adjust pre ammonia .26- .35 (0- 0.09 offset) -reagents all ok -equipment all ok -topped up ammonia tank 2 - 15- 75cm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049949 | 0 | 0
2026-02 | 2026-02-12 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Onsite for annual calibrations at chemical disinfection facility Informed ROC. ROC placed Bayview pumps manual off Completed PRE and Post free and total maintenance and calibration Took grabs: Pre injection Free 0.08mg/L Total 1.59mg/L Post injection Free 0.08mg/L Total 2.16mg/L Cleared associated alarms Informed ROC. ROC placed Bayview pumps back to auto No issues Armed building and left site | FLAG | stage2_low_confidence | 0.0095939 | ML: above threshold (no LLM available) — 0.01 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.0095939 | 0 | 0
2026-02 | 2026-02-11 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site for weekly bacti W -checked trends: all ok -entered readings in PWQ: -took north cell grab 11:30 -free cl: 0.06mg/l -total cl: 2.08mg/l -west cell grab 11:35 -free cl: 0.12mg/l -total cl: 2.06mg/l -south cell grab 11:40 -free cl: 0.11mg/l -total cl: 2.05mg/l -equipment all ok -on site for re-chlorine station check -checked trends: all ok -verified pre-analyzer 12:30 -free reading: 0.06mg/l grab: 0.07mg/l -total reading: 1.66mg/l grab: 1.64mg/l -reagents all ok -verified post - analyzer 12:50 -analyzer free:0.07mg/l grab: 0.06mg/l -analyzer total: 2.30mg/l grab: 2.48mg/l - adjusted -reagents all ok -verified chemscan: all ok -reagents all ok -re-verified pre-injection 13:30 due to high alarm -analyzer 2.03mg/l grab: 1.93mg/l - adjusted | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0017214 | 0 | 0
2026-02 | 2026-02-17 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to complete station and weekly bacti W11605685 -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab and sample north cell 10:10 -free cl: 0.03mg/l -total cl: 2.04mg/l -west cell 10:15 -free cl: 0.08mg/l -total cl: 1.92mg/l -south cell 10:20 -free cl: 0.07mg/l -total cl: 2.01mg/l -notice burning smell coming from dehumidifier/heating unit - extremely hot - turned unit off and informed team lead - turned all both block heaters | FLAG | stage2_low_confidence | 0.01181 | ML: above threshold (no LLM available) — 0.012 | burning smell [equipment_failure] | 0.01181 | 0 | 0
2026-02 | 2026-02-13 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to complete station check -checked trends: all ok -entered readings in PWQ: -verified pre analyzer 09:00 -analyzer free:0.10mg/l grab: 0.07mg/l -analyzer total: 1.56mg/l grab: 1.64mg/l - adjusted -reagents all ok -verified post analyzer 09:10 -analyzer free: 0.05mg/l grab: 0.04mg/l -analyzer total: 1.55mg/l grab: 1.65mg/l - adjusted -reagents all ok -chemscan verified: adjusted post mom 1.44 - 1.36mg/l (.02/-.06) -adjust post free ammonia 0.03 - 0.14 (0.03/0.14) -adjusted post total ammonia 0.41- 0.51 0.03/0.14 -topped up yellow reagents -topped up ammonia tank 1 -15- 75cm -replaced ammonia tubing elements on pomp 1&2 -tested and primed - all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065125 | 0 | 0
2026-02 | 2026-02-17 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -Responded hihi post-combined chlorine - due to the unstable power supply in Richmond Hill tonight, Bayview PS's pumps were on and off which caused sudden flow changes in the system - the chemical system didn't response to the flow change quick enough and caused hi post-combined chlorine at 19:01 to 19:05 (highest residual total=3.28mg/L free=0.15mg/L), 20:42 to 20:51 (highest residual total=3.73mg/L free=0.11mg/L), 22:38 to 22:42 (highest residual total=3.63mg/L free=0.14mg/L) - performed grab test total=2.38mg/L free=0.08mg/L analyzer total=2.43mg/L free=0.09mg/L - no user was affected - not reportable | FLAG | stage2_low_confidence | 0.12073 | ML: above threshold (no LLM available) — 0.121 |  | 0.12073 | 0 | 0
2026-02 | 2026-02-04 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site to replace network switch with network analyst Aaron Magsakay. All pumps were in manual. Comm failure alarm was triggered due to this. Removed Old switch from RHRSTR NAC panel Wired 24 VDC power to the new switch and plugged in the ports. Powered up new IE3300 layer 3 switch and checked the comms. Removed unused cat6 cables. Checked with ROC to make sure comms are back and trends are good. Did the same process for VNPSCD PAC panel switch | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; plugged [infrastructure] | failure [equipment_failure]; alarm [control_system]; plugged [infrastructure] |  | 1 | 0
2026-02 | 2026-02-04 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site for station check and weekly bacti W -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab and sample north cell 10:25 -free cl: 0.07mg/l -total cl: 2.05mg/l -west cell 10:30 -free cl: 0.09mg/l -total cl: 2.09mg/l -south cell 10:35 -free cl:0.08mg/l -total cl: 2.11mg/l -completed station check of re chlor building -verified pre analyzer 11:30 -analyzer free: 0.05mg/l grab: 0.08mg/l -analyzer total: 1.50mg/l grab: 1.50mg/l -reagents all ok -verified post analyzer 11:45 -analyzer free: 0.05mg/l grab: 0.03mg/l -analyzer total: 2.15mgl grab: 2.14mg/l -reagents all ok -verified chemscan -reagents all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0018879 | 0 | 0
2026-02 | 2026-02-06 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to complete rechlor station check -rechlor not active -completed cylinder change -filled ammonia tank #2 231 L to 1162 L -checked equipment -reviewed trends -recorded readings in PWQ sheet -depolox reagents ok -chemscan reagents ok -verified analyzers: 09:50 - pre-injection Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.43 mg/L TNH3 = 0.31 mg/L FNH3 = 0.07 mg/L MCL = 1.41 mg/L 09:50 - pre-injection Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.52/1.52/1.52 mg/L TNH3 = 0.34 mg/L FNH3 = 0.08 mg/L MCL = 1.35 mg/L 09:59 - adjusted pre injection total chlorine analyzer to 1.52 mg/L based on average of 3 grabs 10:00 - post-injection Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.50 mg/L TNH3 = 0.43 mg/L FNH3 = 0.07 mg/L MCL = 1.47 mg/L 10:00 - post-injection Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.54 mg/L TNH3 = 0.34/0.36/0.35 mg/L FNH3 = 0.07 mg/L MCL = 1.39/1.38/1.37 mg/L 10:34 - adjusted post injection total ammonia reading to 0.35 mg/L based on average of 3 grabs, offset 0.09 to 0.05 10:36 - adjusted post injection monochloramine reading to 1.38 mg/L based on average of 3 grabs, offset 0.07 to 0.02 -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00034665 | 0 | 0
2026-02 | 2026-02-09 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to complete station -checked trends; all ok -took reading in PWQ: all ok -verified pre analyzer and performed maintenance 09:50 -analyzer free: 0.05mg/l grab: 0.06mg/l -analyzer total: 1.58mg/l grab: 1.60mg/l -reagents/flow/pressure/motor and electrolyte all ok -verified and post analyzer and performed maintenance 10:15 -analyzer free: 0.05mg/l grab: 0.04mg/l -analyzer total: 2.16mg/l grab: 2.18mg/l -reagents/flow/pressure/motor and electrolyte all ok -verified chemscan -reagents all ok | FLAG | stage2_low_confidence | 0.0079754 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079754 | 0 | 0
2026-02 | 2026-02-05 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to complete following work order -chlorine leak test: all ok - halogen system all ok -scrubber inspection: all ok -completed cleaning and zero of chemscan -parameter 230 & 248 above 2500 and min/max values acceptable - verified unit after cleaning - pre readings 13:50 -analyzer pre- mono: 1.33mg/l grab: 1.39mg/l - adjusted (-0.03 / 0.03) -analyzer free nh: 0.07mg/l grab: 0.07mg/l -analyzer total nh: 0.33mg/l grab: 0.34mg/l -post reading 14:05 -analyzer mono: 1.94mg/l grab: 2.00mg/l - adjusted (0.01/0.06) -analyzer free nh: 0.03mg/l grab: 0.05mg/l -analyzer total nh: 0.44mg/l grab: 0.44mg/l -topped up green/grey and mutation reagents -completed chlorine inspection: all ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; leak [infrastructure] | work order [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-23 | Linear Water System | LINEAR | AUMCBS onsite to change FIT from bidirectional to unidirectional operation as per W11611748 Made changes and left site Informed ROC of the work | FLAG | stage2_low_confidence | 0.0098224 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098224 | 0 | 0
2026-02 | 2026-02-26 | Linear Water System | LINEAR | Worked with North Rock contractor to replace 2 air valves in chamber 691800532 on contract T9718-07 Grab chlorine test results after work was completed as follows Free- 0.05mg/l Total- 1.45mg/l All valves associated with the watermain isolation have been opened and the system is back to normal operation. | FLAG | stage2_low_confidence | 0.015014 | ML: above threshold (no LLM available) — 0.015 | sso [critical] | 0.015014 | 0 | 0
2026-02 | 2026-02-02 | Newmarket Pinch Valves | WW-NORTH | Adjusted EGSSSC forcemain lolo pressure alarm from 45 to 40 kPa to keep consistent with ROC forcemain lolo pressure setpoint. | FLAG | stage2_low_confidence | 0.0072419 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072419 | 0 | 0
2026-02 | 2026-02-13 | Newmarket Pinch Valves | WW-NORTH | Completed monthly PM work orders: -Flow control valve inspection -Sump pit inspection -Air valve inspection | FLAG | stage2_low_confidence | 0.017518 | ML: above threshold (no LLM available) — 0.018 | work order [maintenance_action] | 0.017518 | 0 | 0
2026-02 | 2026-02-17 | Newmarket Pinch Valves | WW-NORTH | Informed ROC. Onsite to perform annual Calibration on flowmeter. Used the calibration mode. Performed calibration. Put the flowmeter back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | FLAG | stage2_low_confidence | 0.00939 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.00939 | 0 | 0
2026-02 | 2026-02-01 | Newmarket Pinch Valves | WW-NORTH | Attended for pinch valve #1 fault Closed isolation valve and tried to open pinch valve locally on Rotork but it wouldn't move (motor stalled alarm on screen) Spoke to Brent (electrical on-call), was able to get the valve to open in local after a few tries Cleared alarm on SCADA and opened isolation valve - pinch valve #1 will stay in duty 2 for the night Notified RO?C of valve status. | FLAG | stage2_low_confidence | 0.049388 | ML: above threshold (no LLM available) — 0.049 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.049388 | 0 | 0
2026-02 | 2026-02-24 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 15m3 from clarifier 1 and 10m3 from clarifier 2 Cleaned up in the process building | FLAG | stage2_low_confidence | 0.012468 | ML: above threshold (no LLM available) — 0.012 |  | 0.012468 | 0 | 0
2026-02 | 2026-02-25 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted and then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Bled the aeration condensate line Removed rags from the aeration tanks and outlets | FLAG | stage2_low_confidence | 0.011924 | ML: above threshold (no LLM available) — 0.012 |  | 0.011924 | 0 | 0
2026-02 | 2026-02-28 | Nobleton Water Resource Recovery Facility | WW-WEST | Added two bags of soda ash each into aeration tank 1 and 2 | FLAG | stage2_low_confidence | 0.011329 | ML: above threshold (no LLM available) — 0.011 |  | 0.011329 | 0 | 0
2026-02 | 2026-02-27 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated STT and transferred to SHT -Completed lab analysis & station check , no issues found -Started batch wasting process at 9:40 , wasting from 11:00- 13:00 for 15m^3 per train -Added 2 bags of soda ash into each aeration tank -Completed online DO probe verification with handheld , cleaned out rags from both tank 1&2 probes and cleaned sensor. A difference of approximately 1.00ppm was found between online DO probes versus handheld. -Received Alum delivery at 12:20 for 16125kg. -Alum level before filling process : 0.87 m -Alum level after filling process : 3.51 m | FLAG | stage2_low_confidence | 0.028914 | ML: above threshold (no LLM available) — 0.029 |  | 0.028914 | 0 | 0
2026-02 | 2026-02-26 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 15m3 from each clarifier Received a soda ash delivery of 50 bags Inspected and greased RAS, WAS, and scum pumps | FLAG | stage2_low_confidence | 0.011922 | ML: above threshold (no LLM available) — 0.012 |  | 0.011922 | 0 | 0
2026-02 | 2026-02-25 | Nobleton Water Resource Recovery Facility | WW-WEST | Collected weekly compliance samples | FLAG | stage2_low_confidence | 0.019871 | ML: above threshold (no LLM available) — 0.02 | compliance [regulatory] | 0.019871 | 0 | 0
2026-02 | 2026-02-23 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 15m3 from clarifier 1 and 10m3 from clarifier 2 Cleaned up in the RAS/WAS room | FLAG | stage2_low_confidence | 0.012283 | ML: above threshold (no LLM available) — 0.012 |  | 0.012283 | 0 | 0
2026-02 | 2026-02-26 | Nobleton Water Resource Recovery Facility | WW-WEST | On site to look at leaking plant service water, did not find a leak informed operators to monitor area, looked at return valve 4, valve is stiff will source new valve | FLAG | stage2_low_confidence | 0.026935 | ML: above threshold (no LLM available) — 0.027 | leak [infrastructure]; leaking [infrastructure] | 0.026935 | 0 | 0
2026-02 | 2026-02-02 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated STT and transfers to SHT -Completed lab analysis, no issues found -Completed station check, no issues found -Started batch wasting process at 11:00, wasting from 12:00-14:00 for 15m^3 per train -Added 2 bags of soda ash into each aeration tank -Prepared compliance sample bottles for weekly compliance -Took out some rags from aeration tanks | FLAG | stage2_low_confidence | 0.018726 | ML: above threshold (no LLM available) — 0.019 | compliance [regulatory] | 0.018726 | 0 | 0
2026-02 | 2026-02-20 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Batch wasted 15m3 from each aeration tank Added 2 bags of soda ash to each aeration tank | FLAG | stage2_low_confidence | 0.011659 | ML: above threshold (no LLM available) — 0.012 |  | 0.011659 | 0 | 0
2026-02 | 2026-02-10 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Decanted then Emptied the sludge thickening tank Batch wasted 20m3 from clarifier 1 and 15m3 from clarifier 2 Added 2 bags of soda ash to each aeration tank Received an alum delivery of 16.5tonnes | FLAG | stage2_low_confidence | 0.012163 | ML: above threshold (no LLM available) — 0.012 |  | 0.012163 | 0 | 0
2026-02 | 2026-02-18 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the daily lab work and station check Decanted then emptied the sludge thickening tank Batch wasted 15m3 from both clarifiers Cleaned the do probes Removed floating solid?s from the aeration tanks | FLAG | stage2_low_confidence | 0.010544 | ML: above threshold (no LLM available) — 0.011 |  | 0.010544 | 0 | 0
2026-02 | 2026-02-19 | Nobleton Water Resource Recovery Facility | WW-WEST | - transferred sludge from the thickening tank to the sludge holding tank - Performed in-house labs and recorded readings on SharePoint. No issues - Enabled RAS batch wasting mode at 8:40. Wasted 20 m^3 from train 1 and 20 m^3 from train 2 - Notified ROC of the work being performed. Inspected clarifier 1 drive and oil for OJT. No issues - Inspected vortex 1 and 2. All okay. Greased fittings. Pumps are all good, oil level is good - Inspected travelling screen. Greased fittings. Checked oil level, all good - Inspected screening press. Heat trace is okay. Oil level is good - Inspected debris auger and grit dewatering screen, oil is all good. No issues - Inspected bypass sampling kit. Seal is still intact. No issues - Checked station and recorded readings on SharePoint. Created archibus for emergency light in RAS/WAS room due to low battery alarm - Exercised filter inlet valves. Greased fittings - Cleared UV fault alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; emergency [critical]; fault [equipment_failure]; archibus [maintenance_action]; alarm [control_system] | bypass [critical]; emergency [critical]; fault [equipment_failure]; archibus [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | Nobleton Water Resource Recovery Facility | WW-WEST | - Added 2 bags of soda ash each to aeration tank 1 and 2 - Removed floating solids from aeration tank 1 and 2 - Checked for condensation in the air lines for aeration tank 1 and 2. None found - Tidied up aeration tank area and blower room - Cleaned aeration tank channel - Recharged dodge ram 2118 battery | FLAG | stage2_low_confidence | 0.012133 | ML: above threshold (no LLM available) — 0.012 |  | 0.012133 | 0 | 0
2026-02 | 2026-02-13 | Nobleton Water Resource Recovery Facility | WW-WEST | Added UV Bypass alarm. Alarm will annunciate if no UV?s are active and there is plant flow for 15 min. The alarm was tested to confirm operation on the servers. No UV?s were off during test. Alarm is to be reset using reset control that appears beside the UV reactors on SCADA while the alarm is active. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; scada [control_system]; alarm [control_system] | bypass [critical]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Supernated STT and transferred to SHT -Completed lab analysis and station check , no issues found -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 15m^3 per train -Added 2 bags of soda ash into each aeration tank -Completed sand filter/air lift 1-2 air compressor inspection and cleaning , no issues found | FLAG | stage2_low_confidence | 0.024351 | ML: above threshold (no LLM available) — 0.024 | sso [critical] | 0.024351 | 0 | 0
2026-02 | 2026-02-18 | Nobleton Water Resource Recovery Facility | WW-WEST | Collected weekly samples | FLAG | stage2_low_confidence | 0.012294 | ML: above threshold (no LLM available) — 0.012 |  | 0.012294 | 0 | 0
2026-02 | 2026-02-19 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Young Jung(OIC). -Assisted Young Jung to completed work orders and recruitment video. | FLAG | stage2_low_confidence | 0.024295 | ML: above threshold (no LLM available) — 0.024 | work order [maintenance_action] | 0.024295 | 0 | 0
2026-02 | 2026-02-13 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated STT and transferred to SHT -Completed lab analysis and station check , no issues found -Started batch wasting process at 10:00, wasting from 11:00-13:00 for 15m^3 per train -Added 2 bags of soda ash into each aeration tank -Prepared weekly compliance sample bottles | FLAG | stage2_low_confidence | 0.01892 | ML: above threshold (no LLM available) — 0.019 | compliance [regulatory] | 0.01892 | 0 | 0
2026-02 | 2026-02-13 | Nobleton Water Resource Recovery Facility | WW-WEST | On site for RAS pump 2 coupling failure Found pump side of coupler deteriorated Locked out RAS pump 2 Removed two piece coupler One piece coupler in stock on site Installed new coupler and reassembled coupler. Operations put pump in service Complete | FLAG | stage2_low_confidence | 0.012873 | ML: above threshold (no LLM available) — 0.013 | failure [equipment_failure] | 0.012873 | 0 | 0
2026-02 | 2026-02-12 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted and then emptied the sludge thickening tank Batch wasted 15m3 from each clarifier Added 2 bags of soda ash to each aeration tank Removed rags from the aeration outlet Bled the condensation from the aeration lines Pulled a sand filter as it was clogged and reseated it | FLAG | stage2_low_confidence | 0.020204 | ML: above threshold (no LLM available) — 0.02 | clog [infrastructure]; clogged [infrastructure] | 0.020204 | 0 | 0
2026-02 | 2026-02-15 | Nobleton Water Resource Recovery Facility | WW-WEST | Onsite for weekend work orders. Added 2 bags of soda ash per tank. Remotely enabled batch wasting mode at 1:40pm and set auto waste for 30m3 from 3pm-5pm When wasting completed at 5pm placed WAS pumps back into manual and reset RAS | FLAG | stage2_low_confidence | 0.016856 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action] | 0.016856 | 0 | 0
2026-02 | 2026-02-16 | Nobleton Water Resource Recovery Facility | WW-WEST | Remote entry - at 6:53pm received call from ROC for alum pumps 3 and 4 uncommanded stop alarms And alum pump 5 general alarm. Alum pump 1 and 2 continue to pump to aeration tank 1 and 2. Logged in remotely and reset to clear alarms. Alarms cleared and alum pump 4 dosing alum to filter inlet as normal. Will continue to monitor. | FLAG | stage2_low_confidence | 0.011037 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011037 | 0 | 0
2026-02 | 2026-02-22 | Nobleton Water Resource Recovery Facility | WW-WEST | Added 2 bags of soda ash to each aeration tank | FLAG | stage2_low_confidence | 0.010698 | ML: above threshold (no LLM available) — 0.011 |  | 0.010698 | 0 | 0
2026-02 | 2026-02-11 | Nobleton Water Resource Recovery Facility | WW-WEST | - Added 2 bags of soda ash each to aeration tank 1 and 2 - Decanted the sludge thickening tank then transferred sludge from the thickening tank to the holding tank - Cleaned aeration tank outlet weir - Held outputs for DO probe. Cleaned probe. Once done, resumed outputs. DO readings good with manual probe - Notified ROC of the work being performed - Tested sanitary sump alarm. hihi alarm received - Filter inlet channel is good - Cleaned filter reject pit - Checked heat trace, display not working. No issues with heat | FLAG | stage2_low_confidence | 0.045035 | ML: above threshold (no LLM available) — 0.045 | not working [equipment_failure]; alarm [control_system] | 0.045035 | 0 | 0
2026-02 | 2026-02-05 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted and then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 20m3 from clarifier 1 and 15m3 from clarifier 2 | FLAG | stage2_low_confidence | 0.012969 | ML: above threshold (no LLM available) — 0.013 |  | 0.012969 | 0 | 0
2026-02 | 2026-02-11 | Nobleton Water Resource Recovery Facility | WW-WEST | Collected weekly effluent samples | FLAG | stage2_low_confidence | 0.012788 | ML: above threshold (no LLM available) — 0.013 |  | 0.012788 | 0 | 0
2026-02 | 2026-02-06 | Nobleton Water Resource Recovery Facility | WW-WEST | On site to reset process building UPS. Power cycle UPS. PAC down for short duration. Alarms cleared. | FLAG | stage2_low_confidence | 0.021025 | ML: above threshold (no LLM available) — 0.021 | alarm [control_system]; alarms [control_system] | 0.021025 | 0 | 0
2026-02 | 2026-02-09 | Nobleton Water Resource Recovery Facility | WW-WEST | On site to assist contractor Total Power with Diesel Generator 5 year PM. Completed | FLAG | stage2_low_confidence | 0.011518 | ML: above threshold (no LLM available) — 0.012 |  | 0.011518 | 0 | 0
2026-02 | 2026-02-03 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Completed lab analysis, no issues found -Completed station check, no issues found -Added 2 bags of soda ash into each aeration tank -Started batch wasting process at 9:40, wasting from 11:00-13:00 for 15m^3 per train -Competed monthly Joint Health & Safety inspection, no issues found -Inspected all aeration blowers, sludge blowers and grit blowers, no issues found | FLAG | stage2_low_confidence | 0.015596 | ML: above threshold (no LLM available) — 0.016 |  | 0.015596 | 0 | 0
2026-02 | 2026-02-04 | Nobleton Water Resource Recovery Facility | WW-WEST | Collect weekly and monthly samples of raw, sludge, final effluent and domestic wells for YDSS lab submissions. | FLAG | stage2_low_confidence | 0.018253 | ML: above threshold (no LLM available) — 0.018 |  | 0.018253 | 0 | 0
2026-02 | 2026-02-09 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted and emptied the sludge thickening tank Added 2 bags of soda ash Batch wasted 15m3 from each clarifier Removed floating rags from the aeration tank Inspected the process building sump pit | FLAG | stage2_low_confidence | 0.010512 | ML: above threshold (no LLM available) — 0.011 |  | 0.010512 | 0 | 0
2026-02 | 2026-02-04 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 15m3 from each clarifier Removed floating solids from the aeration tank and aeration tank outlet Cleaned the do probes in the aeration tanks | FLAG | stage2_low_confidence | 0.012713 | ML: above threshold (no LLM available) — 0.013 |  | 0.012713 | 0 | 0
2026-02 | 2026-02-06 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted and then emptied the sludge thickening tank Batch wasted 15m3 from each clarifier Added 2 bags of soda ash to each aeration tank Removed rags from the aeration tanks and plant inlet | FLAG | stage2_low_confidence | 0.012389 | ML: above threshold (no LLM available) — 0.012 |  | 0.012389 | 0 | 0
2026-02 | 2026-02-26 | Markham Leslie Pumping Station | WW-CEAST | -on site for Housekeeping, cleaning up garbage around site on various floors -running pump 1 in auto duty 1, if it trips on bearing high temp, or another alarm, WO will be created, ongoing issues with pump 1 -completed alarm investigation -W11692845- Leslie Pump 1 High Bearing Temp Alarm created -station okay, only 5 pumps in auto/duty rotation, pump 1 OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: trip [equipment_failure]; oos [equipment_failure]; alarm [control_system] | trip [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-23 | Markham Leslie Pumping Station | WW-CEAST | Station Check completed (See details on SharePoint). Checked drywell. cleaned dry well area Checked screen room, changed out rag bin. Cleaned/hose down screen room. Switched pumps duty to timed mode from all-stop. Pumps 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. pump 1 faulted on 'stack overtemp' alarm. cleared the alarm. pump 2 seal water line has a pinhole leak. created work request W11683392 for maintenance to fix. Pump 1 & 2 taken oos. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; alarm [control_system]; leak [infrastructure] | sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 1
2026-02 | 2026-02-24 | Markham Leslie Pumping Station | WW-CEAST | -ran pump 1 with maintenance, upper bearing on pump is overheating -pump is manual off but available if needed to run -wet well consolidated work order completed -pump 2 was put OOS for the seal water, but back online before end of day -all 6 pumps can run, but pump 1 is manual off for the night, but available if needed -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-27 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -rotated bins in screen room -pump 1 OOS, fault alarm, Fault 47 Stack Overtemp, notifying maintenance, WO already created, will add to it -5 pumps available in auto -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; scada [control_system]; alarm [control_system] | fault [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -rotated bins in screen room, and put bins out for pickup -station okay | FLAG | stage2_low_confidence | 0.011781 | ML: above threshold (no LLM available) — 0.012 | scada [control_system] | 0.011781 | 0 | 0
2026-02 | 2026-02-24 | Markham Leslie Pumping Station | WW-CEAST | Checked all seal water solenoid valves okay None leaking past All seats are good. Replaced copper seal water line on pump 2. Operator will reopen suction valve. | FLAG | stage2_low_confidence | 0.012871 | ML: above threshold (no LLM available) — 0.013 | leak [infrastructure]; leaking [infrastructure] | 0.012871 | 0 | 0
2026-02 | 2026-02-26 | Markham Leslie Pumping Station | WW-CEAST | On site for media sampling with Contractor, All Round System (John Round), under RFT 2609-25. | FLAG | stage2_low_confidence | 0.010078 | ML: above threshold (no LLM available) — 0.01 |  | 0.010078 | 0 | 0
2026-02 | 2026-02-02 | Markham Leslie Pumping Station | WW-CEAST | On site to install pump 4 discharge valve. Bonnet installed will return to install rotork. | FLAG | stage2_low_confidence | 0.011939 | ML: above threshold (no LLM available) — 0.012 |  | 0.011939 | 0 | 0
2026-02 | 2026-02-02 | Markham Leslie Pumping Station | WW-CEAST | Station check complete and the readings have been entered into the sharepoint. Changed out the rag bin. Investigated bar screen 1 fault alarm. Found large amounts of rags stuck between bottom sprocket/chain which has caused the overtorque. Removed the rags from the sprocket/chain and put the unit back in service. | FLAG | stage2_low_confidence | 0.036214 | ML: above threshold (no LLM available) — 0.036 | fault [equipment_failure]; alarm [control_system] | 0.036214 | 0 | 0
2026-02 | 2026-02-18 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bins in screen room, bins out for pickup -inspected outfall -station okay | FLAG | stage2_low_confidence | 0.010273 | ML: above threshold (no LLM available) — 0.01 | scada [control_system] | 0.010273 | 0 | 0
2026-02 | 2026-02-20 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bins in screen room -pump 1 locked out late wednesday afternoon on a high bearing temp alarm, it was left off and OOS. Reset alarm on pump today and returned pump 1 back to auto duty rotation. All 6 pumps available. If pump 1 overheats again, we will leave it OOS for the weekend and get mechanical to investigate. Cleaned the screen on the seal water system, and opened the valve all the way to get as much seal water to pump 1 as possible. Will see if this helps. -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system] | oos [equipment_failure]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | Markham Leslie Pumping Station | WW-CEAST | On site to install split seal on rebuilt pump #1 | FLAG | stage2_low_confidence | 0.0098729 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098729 | 0 | 0
2026-02 | 2026-02-17 | Markham Leslie Pumping Station | WW-CEAST | -cleaned screen room and rotated bins -cleaned up pump floor area, Housekeeping -pump 1 back to auto as per maintenance's request, all 6 pumps in auto/available -station okay | FLAG | stage2_low_confidence | 0.010919 | ML: above threshold (no LLM available) — 0.011 |  | 0.010919 | 0 | 0
2026-02 | 2026-02-15 | Markham Leslie Pumping Station | WW-CEAST | Checked station/equipments. Changed out the rag bin. Cleared comm fail alarm. All trend, equipment visible on scada Hosed down screen room floor. Pushed in empty bins back into the screen room | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system] | scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-12 | Markham Leslie Pumping Station | WW-CEAST | -on site to put pump 1 back online after repairs were completed by Christian Streef and Martin DeVries -electrical removed lockout on pump -maintenance removed their locks -LOTO on suction valve was removed, and suction valve was opened slowly, air was bled from pump -discharge valves were slowly opened and air bled from riser pipe -pump 1 was started in manual to test, seemed to run normally with no issues -mechanical was measuring the temp readings -pump 1 manual off after 45 min run test, mechanical doing further checks -pump 1 will remain manual off for the night to cool down -5 pumps in auto -station okay | FLAG | stage2_low_confidence | 0.039384 | ML: above threshold (no LLM available) — 0.039 | repair [maintenance_action] | 0.039384 | 0 | 0
2026-02 | 2026-02-10 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Completed consolidated monthly dry well pump floor inspection work order. -Sump pit inspection completed. Tested Sump Level HiHi Alarm and confirmed with ROC. -Dry well flood alarm does not exist at this site, tested sump level HiHi in its place. -High low temp alarm does not exist at this site, temperatures tracked on BAS site. -BAS check completed. -Auto dialer test completed and confirmed with ROC. -Air compressor inspection completed, checked belts, oil, filters. -Seal water strainer checks completed. -Pump 1 OOS. -Pump 6 in auto duty rotation, but discharge valve is leaking, issue already reported to maintenance team. -Bar Screen 2 fault came in at 0928 this morning, reset fault and test ran screen for multiple cycles with no issues. Left bar screen 2 running in auto. Topped up oil on both bar screens. -RS Pump and Motor Inspection completed: -Pump 1 OOS -Pump 2: 1710L/s at 100% speed. -Pump 3: 1300L/s. -Pump 4: 1290L/s. -Pump 5: 1570L/s at 100% speed. -Pump 6: 1190L/s. -Check valve inspections completed. -Air relief valve inspections completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] | sso [critical]; flood [critical]; fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 1
2026-02 | 2026-02-13 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -completed consolidated surge tank inspection -ran pump 1 for an hour, pump manual off -station okay | FLAG | stage2_low_confidence | 0.0084722 | ML: above threshold (no LLM available) — 0.008 | scada [control_system] | 0.0084722 | 0 | 0
2026-02 | 2026-02-11 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -entered data into sharepoint -inspected site -reviewed SCADA -notified ROC of work being performed -WAJAX on site for generator maintenance -YR maintenance and electrical on site for pump 1 repairs -generators started at 11:58 Generator 1: Start Hours:230.24 Stop Hours:231.42 Generator 2: Start Hours:117.40 Stop Hours:119.35 Generator 3: Start Hours:103.59 Stop Hours:105.54 Bulk Fuel Tank Start: 23,437L Fuel Stop: 22,572L -generator 1 went into shutdown due to low oil level, topped up oil, reset alarms, put generator 1 back to auto, generator started up and ran for remainder of 1 hour test run, sync/load shared with other generators Generator Run Time: 1.95 hrs -generators off at 13:52 -test successful, back on utility power, reset alarms -pump 1 remains OOS -all other pumps in auto and reset -Generator 1-3 Monthly Test Run -Hazard Waste Removal-no hazardous waste -Leslie Scrubber Inspection -bin replacement/screen room inspection -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] | oos [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] |  | 1 | 1
2026-02 | 2026-02-11 | Markham Leslie Pumping Station | WW-CEAST | On site to finish assembly of rebuilt pump #1. Will return to flood pump with operator and rack pump back in to test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-02 | 2026-02-04 | Markham Leslie Pumping Station | WW-CEAST | Station check complete and the readings have been entered into the sharepoint. Changed out the rag bin, pushed full bin out for pick up. Filled up barscreen oil reservoirs. Shelved all pump 1 and associated discharge valve alarms for now until it gets repaired. Work in progress by CMS to repair pump 4 discharge valve. | FLAG | stage2_low_confidence | 0.033687 | ML: above threshold (no LLM available) — 0.034 | sso [critical]; repair [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.033687 | 0 | 0
2026-02 | 2026-02-06 | Markham Leslie Pumping Station | WW-CEAST | On site completed work orders. Pump 4 ran twice after repair by CMS, discharge valve and running operation ok, no issues. Put back in service and includes in the auto duty rotation. Currently in duty 1, with a flow of around 1290 L/s at 420 kPa PIT1/520 kPa PIT2. Station Check (See details on SharePoint). All pumps available in timed auto duty rotation every 4 hours, except pump 1, which is out of service. All standby power generator available in auto. Drained condensates from surge tanks air compressors. Checked dry well, ok. Blew down bubblers. Checked bar screens. Switched rag bin. Put rag bins back inside the screen room after picked up by Miller Waste yesterday. Cleaned screen room of rags on the floor. Switched sump pump duty and ran sump pump to remove old/stagnant water/sewage inside the sump pit. Hoist inspection completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] | sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-09 | Markham Leslie Pumping Station | WW-CEAST | Weather today Clear and -16 Celsius -On site to complete work orders W11579343. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure]; work order [maintenance_action] | sso [critical]; out of service [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-05 | Markham Leslie Pumping Station | WW-CEAST | On site to make sure pump 4 discharge valve is moving properly. Valve opens and closes smoothly. Set open and closed limits. Pump is ready to flood and run. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-02 | 2026-02-26 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Time: 09:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.37 Time: 09:23 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.46 Total: 1.62 Verified analyzers with grabs. Adjusted the influent free from 1.37mg/l-1.46mg/l due to multiple grabs taken at 09:26. Adjusted the effluent free from 1.46mg/l-1.38mg/l due to multiple grabs taken at 09:27. Checked site and trends. Will leave silicate pump 2 off the priming valve is broken and needs to be replaced. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041532 | 0 | 0
2026-02 | 2026-02-03 | Markham Leslie Pumping Station | WW-CEAST | -On site to respond to Wet Well Screen 1 and 2 Differential LOE and HiHi Alarms. -Upon arrival to site, checked trends and bar screen inlet channel. Trends showed there were several level fluctuations and spikes within the last two hours. Inspection of the bar screen channels showed traces of white foam in channels and on bars, which likely caused the above alarms. Foam has almost entirely dissipated and issue appears to now be resolved. | FLAG | stage2_low_confidence | 0.063833 | ML: above threshold (no LLM available) — 0.064 | alarm [control_system]; alarms [control_system] | 0.063833 | 0 | 0
2026-02 | 2026-02-25 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11619936 Weekly Bac-t Samples. Also on site to top up silicate tank. Start: 19.3cm/91L Stop: 102.6cm/484L Time: 10:35 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.93 1.99 Time: 10:36 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.47 Total: 1.71 Started well 1 in local to run to waste to collect sample at 10:30. Verified analyzers with grabs. Checked site and trends. Put silicate pump 2 into manual side to starting issues. Shut down well 1 at 11:04. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0019417 | 0 | 0
2026-02 | 2026-02-24 | Mount Albert Wells 1 & 2 | EAST | On site with Travis Wyatt for on the job training and to assist in monthly maintenance: 11:45hrs: Cleaned HACH CL17 Analyzer, Verified Analyzers after cleaning @12:00hrs: Influent FCL grab residual: 1.63mg/l, Analyzer: 1.59mg/l Effluent FCL grab residual: 1.65mg/l. Analyzer: 1.67mg/l Silicate and Hypo system inspection including injection point cleaning and inspection. Inspected chemical boards. Deep well exhaust valve inspection. Low temp alarm test. | FLAG | stage2_low_confidence | 0.0097079 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0097079 | 0 | 0
2026-02 | 2026-02-23 | Mount Albert Wells 1 & 2 | EAST | On site for station check, and operational sampling (W1164413). Activated system duty. Tower level 71%. Entered data into PWQ sheets. Verified analyzers: Inffluent taken at 9:38 Free Grab: 1.78 mg/L Analyzer: 1.82 mg/L Effluent taken at 9:40 Free grab: 1.51 mg/L Analyzer: 1.52 mg/L Total grab: 1.79 mg/L Took operational sample at 9:49 Chemical systems: Hypo pump 2 running 28% speed, DP= 440 kpa Silicate pump 2 running at 37% speed, DP= 500 kpa. Reviewed SCADA trends, Outstanding alarms: gen fuel high level alarm. Station OK. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0039684 | 0 | 0
2026-02 | 2026-02-02 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Collecting PH reading Time: 13:00 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.89 1.91 Time: 3:05 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.45 Total: 1.68 Verified analyzers with grabs. At 12:30 activated duty for Mount Albert. Checked station and trends. Well 1 OOS due to WQ issues. No outstanding alarms. PH reading 8.02. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Time: 13:45 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.32 Time: 13:50 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.37 1.36 Total: 1.56 Verified analyzers with grabs Well 1 OOS due to WQ issues. Gen hi tank alarm disregard. Entered data into PWQ sheet. Cleaned NTU analyzer. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11605433 Weekly Bac-t Samples. Time: 13:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.92 1.93 Time: 13:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.40 1.48 Total: 1.64 Started well 1 at 13:14 to run well to waste for sampling. Changed out effluent free CL-17 reagents. Entered data into PWQ sheet. Checked site and trends. Gen tank hi alarm disregard. Well 1 OOS due to WQ issues. only running to waste to collect raw water sample. At 13:52 shut down well 1. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11588600 Weekly Bac-t Samples. Time: 13:18 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.95 1.93 Time: 13:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.53 Total: 1.68 At 13:24 started up well 1 to run to waste to collect sample. Verified analyzers all ok. Well 1 OOS due to WQ issues. Gen tank hi alarm disregard. Entered data into PWQ sheet. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | Mount Albert Wells 1 & 2 | EAST | Silicate Top Up Before: 33.4cm/158L After: 105.2cm/496L | FLAG | stage2_low_confidence | 0.0074588 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074588 | 0 | 0
2026-02 | 2026-02-13 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Time: 07:45 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.43 1.35 Time: 07:47 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.42 Total: 1.65 Verified analyzers with grabs. Checked station and trends. Gen hi tank alarm disregard. Well 1 OOS due to WQ issues. Entered data into PWQ Changed out reagents for the influent free CL-17 analyzer. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-03 | Mount Albert Wells 1 & 2 | EAST | On site for hypo delivery and completing work orders. Hypo tank fill. Start: 310/310L Stop: 608/602L Started generator at 11:15 also attached will be the generator readings. Started well at 11:17 to put generator under load. Shut well off at 12:17 while generator is being shut off. Completed JHSC inspection as well. No issues with work orders. | FLAG | stage2_low_confidence | 0.022268 | ML: above threshold (no LLM available) — 0.022 | work order [maintenance_action] | 0.022268 | 0 | 0
2026-02 | 2026-02-06 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Time: 12:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.40 Time: 12:35 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.47 Total: 1.68 Verified analyzers with grabs. Checked site and trends. Generator hi tank level alarm disregard. Well 1 OOS due to WQ issues. Entered data into PWQ sheets. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-09 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Time: 10:05 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.49 1.41 Time: 10:07 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.47 Total: 1.62 Verified analyzers with grabs. Checked station and trends. Well 1 OOS due to WQ issues. Generator hi fuel alarm disregard. Entered data into PWQ sheet. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-04 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11568200 Weekly Bac-t Samples. W11569414 Monthly Manganese Samples. Time: 13:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.98 2.01 Time: 13:53 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.48 Total: 1.59 Activated duty at 13:03 to sample wells 1 and 2. Checked site and trends. Verified analyzers with grabs. Well 1 OOS for WQ issues. Diesel tank level hi alarm disregard. Stopped well 1. All flow from this well went to waste and not to system. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-23 | Mount Albert Well 3 | EAST | On site to correct source of chlorine gas leak with Jack P. Cylinders already isolated, turned booster pump 2 local on to purge chlorine lines. Replaced parker fitting on outlet of the regulator on left bank cylinder. Opened chlorine cylinders and vacuum tested system for leaks. Backwashed station for a few mins, with de-chlor pucks in the catch basin. Placed chlorine system back in service and placed well back in service. Monitoring well start up. Rotated chlorinators to test both. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; oos [equipment_failure]; leak [infrastructure] | gas leak [critical]; oos [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-25 | Mount Albert Well 3 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11619936 Weekly Bac-t Samples. W11670426 Manganese Sample. Time: 11:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.73 1.73 Time: 11:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.67 1.64 Total: 1.84 Verified analyzers with grabs. Checked site and trends. No outstanding alarms. No OOS equipment. Topped up silicate tank. Start: 66.3cm/2108L Stop: 79.2cm/2518L This is silicate from Aurora wells 1-4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0036673 | 0 | 0
2026-02 | 2026-02-26 | Mount Albert Well 3 | EAST | On site to complete station check. Time: 10:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.77 Time: 10:12 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.83 1.81 Total: 2.09 Verified analyzers with grabs. Checked site and trends. Cleared any outstanding alarms on site. No OOS equipment on site. Cleaned NTU cell which locked out well at 10:30. Cleared interlock and restarted well at 10:37. NTU is currently 0.230 and dropping. Will monitor off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0068259 | 0 | 0
2026-02 | 2026-02-27 | Mount Albert Well 3 | EAST | On site for Camlok wiring for generator load tests | FLAG | stage2_low_confidence | 0.013022 | ML: above threshold (no LLM available) — 0.013 |  | 0.013022 | 0 | 0
2026-02 | 2026-02-23 | Mount Albert Well 3 | EAST | On site for station check, and operational sampling (W1164413). Duty active, Tower level 77%. Entered data into PWQ sheets. Verified analyzers: Inffluent taken at 11:53 Free Grab: 1.82 mg/L Analyzer: 1.82 mg/L Effluent taken at 11:56 Free grab: 1.76 mg/L Analyzer: 1.71 mg/L Total grab: 2.01 mg/L Took operational sample at 12:00 Chemical systems: Chlorinator 2 open at 33%, BP2 running DP=1000 kpa Silicate pump 2 running at 42% speed, DP= 500 kpa. Reviewed SCADA trends, Station OK. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0044372 | 0 | 0
2026-02 | 2026-02-26 | Mount Albert Well 3 | EAST | On site to complete station check. Time: Influent Grab (mg/l) Analyzer (mg/l) Free: Time: Effluent Grab (mg/l) Analyzer (mg/l) Free: Total: | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003136 | 0 | 0
2026-02 | 2026-02-02 | Mount Albert Well 3 | EAST | On site to complete station check. Completing raw water PH reading Time: 13:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.84 1.82 Time: 13:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.76 1.72 Total: 1.94 Verified analyzers with grabs. Checked station and trends. No OOS equipment. No outstanding alarms on site. PH reading 8.01. Replaced CL-17 reagents for the influent and effluent analyzers. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0052217 | 0 | 0
2026-02 | 2026-02-19 | Mount Albert Well 3 | EAST | On site to complete the following work orders: - Turbidity analyzer maintenance - addressed turbidity fault from earlier this morning as well - Closed chlorine leak detector test and scrubber check work orders - they were deemed to be working after chlorine leak alarm on 02/17 - Chemical system inspection Silicate: Cleaned injection points, flushed lines with hot water and verified pumps with drawdown. No issues with silicate system - Chemical system inspection chlorine: Chlorinators were tested yesterday during chlorine leak resolution. Performed visual inspection of system - Chlorine emergency kit inspection Well back to auto, station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; fault [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | emergency [critical]; fault [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-13 | Mount Albert Well 3 | EAST | On site to complete station check. Time: 08:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.61 1.54 Time: 08:30 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.53 Total: 1.87 Entered data into PWQ sheet. Verified analyzers with grabs. Checked station and trends. No outstanding alarms on site. No OOS equipment. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0051235 | 0 | 0
2026-02 | 2026-02-10 | Mount Albert Well 3 | EAST | On site to fix silicate pump 1. Replaced diaphragm and purged air from the system. Tested pump and cleared alarms at 09:06. Put pump 1 into duty 1 at 09:08, system is back to normal. | FLAG | stage2_low_confidence | 0.019019 | ML: above threshold (no LLM available) — 0.019 | alarm [control_system]; alarms [control_system] | 0.019019 | 0 | 0
2026-02 | 2026-02-12 | Mount Albert Well 3 | EAST | On site to check the silicate system especially pump 1 which has a new diaphragm. No issues noticed. | FLAG | stage2_low_confidence | 0.0125 | ML: above threshold (no LLM available) — 0.013 |  | 0.0125 | 0 | 0
2026-02 | 2026-02-18 | Mount Albert Well 3 | EAST | On site with Jackie Saunders to address chlorine leak from last night Placed chlorine scrubber back to auto Purged chlorine system using booster pump #1 - Removed leaky Parker fitting, found that the grab spacer ring was cracked. Replaced fitting and threaded on. Opened chlorine cylinders and tested for leaks, none observed @08:40 - Activated system duty - MTETNL level is 65% Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; leak [infrastructure] | oos [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-20 | Mount Albert Well 3 | EAST | On site responding to chlorine leak alarm. Tested system and have not been able to find cause of leak. Also on site to complete station check. Time: 11:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.57 Time: 11:32 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.36 Total: 1.72 Verified analyzers with grabs all ok. Checked site and trends. Entered data into PWQ sheet. No outstanding alarms on site. No OOS equipment on site. tightened up vent lines on regulators to prevent leak will monitor off site and inform OCO. | FLAG | stage2_low_confidence | 0.01361 | ML: above threshold (no LLM available) — 0.014 | oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.01361 | 0 | 0
2026-02 | 2026-02-12 | Mount Albert Well 3 | EAST | Changed chlorine cylinder on right bank. | FLAG | stage2_low_confidence | 0.01318 | ML: above threshold (no LLM available) — 0.013 |  | 0.01318 | 0 | 0
2026-02 | 2026-02-22 | Mount Albert Well 3 | EAST | On site to respond to chlorine leak alarm. Well duty is not active upon arrival. Chlorine gas sensor is reading 0.0ppm. Reset the chlorine scrubber.? Noticed a small leak from left side cl2 regulator's Parker connection. Closed both cylinders, purged the lines. Placed well 3 to local off. Will come back during the day to replace the flex tubings and connections. Informed ROC. Well 3 is OOS for the night.? | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; leak [infrastructure] | oos [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-11 | Mount Albert Well 3 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11588600 Weekly Bac-t Samples. Time: 14:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.77 1.73 Time: 14:12 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.70 1.64 Total: 1.93 Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Checked site and trends. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0051562 | 0 | 0
2026-02 | 2026-02-17 | Mount Albert Well 3 | EAST | On site responding to chlorine gas leak / scrubber running alarms W11670914 When arrived on site @20:05 reset scrubber and it stopped. Gas detector reading 0.0 ppm . Checked for leaks using ammonia, none observed. However observed a Parker fitting on the discharge side of the regulator #1 that appears cross threaded. Will inform Team lead tomorrow, to get two operators to site to fix. Isolated cylinder #1 for the time being. Leaving chlorine scrubber running in local on overnight, just in case there was an issue with that Parker fitting. Informed ROC that would be leaving scrubber running overnight and to disregard that alarm until 07:30 tomorrow Chlorine cylinder #1 OOS Station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | gas leak [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-17 | Mount Albert Well 3 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11605433 Weekly Bac-t Samples. Time: 14:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.81 1.75 Time: 14:25 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.72 1.66 Total: 2.05 Verified analyzers with grabs. Checked site and trends. No OOS equipment No outstanding alarms. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0047503 | 0 | 0
2026-02 | 2026-02-04 | Mount Albert Well 3 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. Collecting Monthly Manganese Samples. W11568200 Weekly Bac-t Samples. W11569414 Monthly Manganese Samples. Time: 14:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.76 1.72 Time: 14:28 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.64 1.63 Total: 2.02 Verified analyzers with grabs all ok. No OOS equipment. No outstanding alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0053956 | 0 | 0
2026-02 | 2026-02-09 | Mount Albert Well 3 | EAST | On site to complete station check. Time: 11:45 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.52 Time: 11:47 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.54 Total: 1.76 Verified analyzer with grabs all ok. Checked site and trends. Ruptured diaphragm on pump 1 silicate causing a fault alarm. Entered data into PWQ sheets. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure]; alarm [control_system] | 0.004818 | 0 | 0
2026-02 | 2026-02-06 | Mount Albert Well 3 | EAST | On site to complete station check. Time: 13:35 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.49 1.51 Time: 13:38 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.51 Total: 1.88 Verified analyzers with grabs. Checked site and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0050625 | 0 | 0
2026-02 | 2026-02-05 | Mount Albert Well 3 | EAST | On site to complete following work orders: W11570951 Supply Fans Check W11570957 Exhaust Fans Check W11570963 Deep Well Exhaust Valve check W11570984 Facility Outfall Inspection W11571049 Standby Generator Test W11571063 Chlorine Analyzer Maintenance W11571278 JHSC Inspection Put well 3 in manual at 09:08 and informed ROC of work to be completed at 09:09. Taking grabs to verify analyzers after maintenance. Time: 10:35 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.50 Time:10:37 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.51 Verified analyzers no issues pocket colorimetre passed calibration. Started generator at 12:46 and started well in manual at 12:47. All details of generator run will be attached to this log entry. Completed silicate work and pumped hot water through system and pump. Any changes in trends or alarms created are due to work orders being completed. Stopped well at 13:43 in preparation for generator shut down. Generator shut down at 13:53. Put well into auto at 13:54 duty is active. | FLAG | stage2_low_confidence | 0.033048 | ML: above threshold (no LLM available) — 0.033 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.033048 | 0 | 0
2026-02 | 2026-02-23 | Mount Albert North Elevated Tank | EAST | Changed the duty 1 start set point from 45% to 60% at 07:08 after a successful draw down, | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038902 | 0 | 0
2026-02 | 2026-02-25 | Mount Albert North Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11619936 Weekly Bac-t Sample. Time: 13:15 Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.52 Total: 1.72 Verified analyzers with grabs all ok. Checked site and trends. No OOS equipment. No outstanding alarms on site. | FLAG | stage2_low_confidence | 0.01139 | ML: above threshold (no LLM available) — 0.011 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.01139 | 0 | 0
2026-02 | 2026-02-17 | Mount Albert North Elevated Tank | EAST | @03:42 - ROC called for outlet free chlorine high alarm Reviewed trends, chlorine analyzer had spiked to 5 mg/L twice in the past hour. Analyzer was reading 5 mg/L from 03:34 to 03:44, and has been steadily dropping since. Coincides with when the ROC started filling the tower @04:02 - Deactivated duty to see if the alarm comes back with the tower draining. Analyzer reading spiked slightly, but then stabilized at ~1.65 mg/L around 04:40. Requested ROC to call back if the outlet FCL goes high again, and will attend site at that point. | FLAG | stage2_low_confidence | 0.016577 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system] | 0.016577 | 0 | 0
2026-02 | 2026-02-20 | Mount Albert North Elevated Tank | EAST | At 07:42 turned off duty and changed the duty start set point from 60% to 45%. This is to deep cycle the tower for WQ. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044728 | 0 | 0
2026-02 | 2026-02-17 | Mount Albert North Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11605433 Weekly Bac-t Sample. Time: 12:10 Grab (mg/l) Analyzer (mg/l) Free: 1.47 1.51 Total: 1.69 While on site took a look at the pinch plate tubing on the CL-17 analyzer. While doing this analyzer went to 0mg/l at 12:18 grabs were taken at 12:20 and are reading 1.47mg/l, same as grabs taken at 12:10. Also will be priming the CL-17 analyzer due to erratic reading that occurred over the weekend. Took another grab at 12:30 while CL-17 analyzer is priming, Time: 12:30 Grab (mg/l) Free: 1.49 Analyzer reading after prime is 1.51mg/l grab after prime is 1.48mg/l at 12:43. Activated duty at 12:44 to collect samples. | FLAG | stage2_low_confidence | 0.018519 | ML: above threshold (no LLM available) — 0.019 |  | 0.018519 | 0 | 0
2026-02 | 2026-02-19 | Mount Albert North Elevated Tank | EAST | On site for monthly maintenance: Informed ROC - JHSC health and safety inspection - Manual valves exercises - Low temperature alarm test - Sump pit inspection - Inlet / Outlet Heat trace inspections - observed a low temperature alarm as active on the inlet and outlet units - ack / reset alarms. Heaters on the heat trace are running, and current temps are okay. Informed TL to request to send an operator back to check them tomorrow - Chlorine analyzer maintenance: Started @14:14, Completed @14:33. Verified analyzer reading with grab residual @14:45 - Grab: 1.45 mg/L / Analyzer: 1.44 mg/L - Portable gasoline generator test run Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-04 | Mount Albert North Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. Collecting monthly manganese sample. W11568200 Weekly Bac-t Sample. W11569414 Monthly Manganese Sample. Time: 08:50 Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.38 Total: 1.59 Cleared historian heart beat alarm on site at 08:56. Verified analyzer on site. Checked site and trends. Verified analyzer with grabs all ok. Entered data into PWQ sheet. No OOS equipment on site. | FLAG | stage2_low_confidence | 0.0097985 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure]; alarm [control_system] | 0.0097985 | 0 | 0
2026-02 | 2026-02-11 | Mount Albert North Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11588600 Weekly Bac-t Sample. Time: 12:40 Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.39 Total: 1.54 Verified analyzers with grabs No outstanding alarms on site. No OOS equipment Activated duty at 12:48. Checked site and trends. | FLAG | stage2_low_confidence | 0.01019 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.01019 | 0 | 0
2026-02 | 2026-02-23 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check. Collected CL2 grab residual on Discharge Header: 11:20hrs: Free Cl2 grab residual: 1.36mg/l, Total Cl2 grab residual: 1.57mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-26 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check. Collected CL2 grab residual on Discharge Header: 12:20hrs: Free Cl2 grab residual: 1.34mg/l, Total Cl2 grab residual: 1.50mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check. Collected CL grab residual on Discharge Header: 12:45hrs: Free Cl2 grab residual: 1.54mg/l, Total Cl2 grab residual: 1.71mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-10 | Stouffville Zone 1 Booster Pumping Station | EAST | Placed VC_FCV1 in auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040785 | 0 | 0
2026-02 | 2026-02-13 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check. Collected CL grab residual on Discharge Header: 10:32hrs: Free Cl2 grab residual: 1.44mg/l, Total Cl2 grab residual: 1.65mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-10 | Stouffville Zone 1 Booster Pumping Station | EAST | Conducted Generator Test Run (12:42hrs): Diesel Generator Run Monthly Test: Start Runtime: 12:42hrs (Run hrs: 514.6hrs) Fuel Start: 751L Stop Runtime: 13:58hrs (Run hrs: 515.8hrs ) Fuel Stop: 735L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 64amps Volts: 594 Hertz: 61 RPM: 1800 Oil Pressure: 57psi Water temp: 176F Oil temp: 220F Pyrometer: 520F No issues during generator run test. Ran Pump 2 during run test. Valve exercise and check valve greasing Housekeeping | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013037 | 0 | 0
2026-02 | 2026-02-17 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check. Collected CL grab residual on Discharge Header: 11:10hrs: Free Cl2 grab residual: 1.81mg/l, Total Cl2 grab residual: 1.95mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-20 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check. Collected CL grab residual on Discharge Header: 12:10hrs: Free Cl2 grab residual: 1.34mg/l, Total Cl2 grab residual: 1.55mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check. Collected CL grab residual on Discharge Header: 11:20hrs: Free Cl2 grab residual: 1.54mg/l, Total Cl2 grab residual: 1.76mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Stouffville Zone 1 Booster Pumping Station | EAST | Tested FCV's auto function by placing it in auto. Activated duty and deactivated duty to for the test. It is functioning well. Left it man/off for the night and will place it in auto tomorrow. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068165 | 0 | 0
2026-02 | 2026-02-06 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check. Collected CL grab residual on Discharge Header: 11:35hrs: Free Cl2 grab residual: 1.48mg/l, Total Cl2 grab residual: 1.66mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-24 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site with Travis Wyatt for Cylinder change on Bank 1. | FLAG | stage2_low_confidence | 0.010171 | ML: above threshold (no LLM available) — 0.01 |  | 0.010171 | 0 | 0
2026-02 | 2026-02-26 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook @ 11:05 hrs. Adjusted pump speed for pump 1 to 65 % and pump 2 to 60 %, then returned speed setpoint to auto Influent Water Grab @ 11:11 hrs. TCL: 1.56 mg/L Analyzer: TCl: 1.51 mg/L Effluent Water Grab @ 11:14 hrs. FCl: 1.93 mg/L TCl: 5.00 mg/L , 1/4 dilution Analyzer: Free Chlorine FCl: 1.98 mg/L Analyzer Total Chlorine TCl: 4.95 mg/L Simulated Free Grab @ 11:24 hrs. Sim FCl: 1.76 mg/L, Analyzer: FCl: 1.70 mg/L Duty not active Equipment OOS: Pump 4 Facility OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.00026223 | 0 | 0
2026-02 | 2026-02-23 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site with Sean Peoples to investigate BP #2 outlet valve. Found actuator gearbox seal to be compromised. Oil has entered the electrical enclosure. Rotork actuator will need to be replaced. ROC notified. Replacement actuator from inventory installed. Remote control not functioning, requires further investigation. Only operable in Local Control. ROC notified. | FLAG | stage2_low_confidence | 0.0096377 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096377 | 0 | 0
2026-02 | 2026-02-23 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks - Receive chlorine cylinders (24), worked with OIC Joe Mazza Data in PWQ workbook Influent Water Grab @ 13:10 hrs. TCL: 1.54 mg/L Analyzer: TCl:: 1.51 mg/L Effluent Water Grab @ 13:14 hrs. FCl: 1.65 mg/L TCl: 2.40 mg/L Analyzer: Free Chlorine FCl: 1.56 mg/L Analyzer Total Chlorine TCl: 2.41 mg/L Simulated Free Grab @ 10:20 hrs. Sim FCl: 1.67 mg/L, Analyzer: FCl: 1.65 mg/L Duty not active Equipment OOS: Pump 4, pump 2 (power loss) Facility OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.00020218 | 0 | 0
2026-02 | 2026-02-25 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks - Test pump 2 and discharge valve Data in PWQ workbook @ 09:01 hrs. stopped pump 3 placed pump 2 in duty 1 with pump 1 Valve actuated and fully opened, pump 2 back in service. Influent Water Grab @ 13:10 hrs. TCL: 1.54 mg/L Analyzer: TCl: 1.51 mg/L Effluent Water Grab @ 09:37 hrs. FCl: 1.92 mg/L TCl: >4.40 mg/L Analyzer: Free Chlorine FCl: 1.96 mg/L Analyzer Total Chlorine TCl: 4.83 mg/L Simulated Free Grab @ 09:38 hrs. Sim FCl: 1.62 mg/L, Analyzer: FCl: 1.62 mg/L Duty not active Equipment OOS: Pump 4 Facility OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.00017966 | 0 | 0
2026-02 | 2026-02-24 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site with Sean Peoples to continue work on Pump #2 outlet valve actuator. ROC notified. Programming and installation completed. With assistance of ROC, actuator tested. Found that actuator timed out and ?Fail to open? alarm initiated. Tyler Zimmerman-Jones contacted and then coordinated with PCS to change the valve timer and test actuator. Valve now operates appropriately in remote. | FLAG | stage2_low_confidence | 0.024765 | ML: above threshold (no LLM available) — 0.025 | alarm [control_system] | 0.024765 | 0 | 0
2026-02 | 2026-02-02 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks - Chlorine cylinder change (worked with OIC Joe Mazza) Data in PWQ workbook Influent Water Grab @ 09:54 hrs. TCL: 1.54 mg/L Analyzer: TCl: 1.51 mg/L Effluent Water Grab @ 09:57 hrs. FCl: 1.95 mg/L TCl: > 4.40 mg/L Analyzer: Free Chlorine FCl: 1.99 mg/L Analyzer Total Chlorine TCl: 4.81 mg/L Simulated Free Grab @ 10:03 hrs. Sim FCl: 1.70 mg/L, Analyzer: FCl: 1.67 mg/L @10:24 hrs. Informed ROC of chlorine cylinder change, with Joe Mazza @ 10:39 placed pump 2 in manual on at 50 % to test chlorine system after cylinder change changed duty 1 from pumps 1/3 to pumps 2/3 Equipment OOS: Pump 4 Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site with Travis Wyatt to change out Cl2 Cylinder Bank 1. | FLAG | stage2_low_confidence | 0.01036 | ML: above threshold (no LLM available) — 0.01 |  | 0.01036 | 0 | 0
2026-02 | 2026-02-12 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou ON Site for PM's; - AIT Maintenance Informed ROC @ 13:01, and placed pumps 1 and 3 in manual off, pumps 2 and 4 currently in manual off Clean Start @ 13:03 Clean Stop @ 13:50 Low flow to Influent total analyzer, disregard alarm -> station off no flow to users Analyzer Verification: Influent Water Grab @ 14:05 hrs. TCL: 1.62 mg/L Analyzer: TCl: 1.65 mg/L Effluent Water Grab @ 14:01 hrs. FCl: 1.71 mg/ TCl: 2.72 mg/L Analyzer: Free Chlorine FCl: 1.67 mg/L Analyzer Total Chlorine TCl: 2.75 mg/L Simulated Free Grab @ 14:03 hrs. Sim FCl: 1.64 mg/L, Analyzer: FCl: 1.65 mg/L @ 14:10 placed pumps 1 and 3 in manual on, pumps 2 and 4 remain in manual off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00024699 | 0 | 0
2026-02 | 2026-02-18 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under direction of OIC Dan Zhou On site for PM?s - Actuated valve exercise and inspection - Chlorine leak detector and safety equipment test - Chlorine scrubber check - Chemical system inspection (chlorine) - Pump 4 inspection - Comprehensive cleaning - Chlorine cylinder change (worked with OIC Joe Mazza) - Install vent line to chlorine regulators vent (worked with OIC Joe Mazza) @ 12:35 informed ROC of chlorine leak detector test and pump 4 inspection @ 12:46 placed pumps 1 and 3 in manual off for jockey pump test, and chlorine leak detector test Chlorine leak detector test triggered @ 12:40: - All halogen valves actuated and closed cylinders, scrubber activated - Exhaust fan vfd fault light on at MCC panel, tried flipping breaker (no change), created work order (W11673974) Pump 4 inspection: @ 13:32 pump 4 (jockey pump) in manual on for inspection, using GC 1 to CBP 1 BP1 at 235 kpa Rotameter reading 33 PPD Pump pressure gauge 610 kpa Scada pump discharge pressure 629 kpa @ 13:41 put pump 4 in manual off MV 1,3,4 actuated, Pump 2 and MV2 OOS due to power loss. @ 13:59 placed pumps 1 and 3 in auto, active in Duty 1 | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; leak [infrastructure] | fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-11 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 08:48 hrs. TCL: 1.60 mg/L Analyzer: TCl:: 1.54 mg/L Effluent Water Grab @ 08:54 hrs. FCl: 1.92 mg/ TCl: > 2.20 mg/L Analyzer: Free Chlorine FCl: 1.96 mg/L Analyzer Total Chlorine TCl: 4.89 mg/L Simulated Free Grab @ 08:58 hrs. Sim FCl: 1.80 mg/L, Analyzer: FCl: 1.77 mg/L @ 8:59 hrs. Sim free sample tap disrupted flow to analyzer, disregard alarm Equipment OOS: Pump 4, pump 2 (power loss) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-13 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Joe Mazza On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 08:13 hrs. TCL: 1.61 mg/L Analyzer: TCl:: 1.60 mg/L Effluent Water Grab @ 08:20 hrs. FCl: 1.92 mg/L Using 1/4 dilution took 3 grabs TCl: 4.08 mg/L, 4.08 mg/L, 4.12 mg/L Average = 4.09 mg/L Adjusted analyzer to 4.09 mg/L @ 08:49 informed ROC of sensor warning on Effluent CL-17 @ 08:52 manually stopped pumps 1 and 3 to reset analyzer, no flow to users @ 08:54 reset effluent analyzer by turning OFF and ON -> sensor warning lifted Disregard total chlorine lolo, due to turning off and on analyzer Analyzer: Free Chlorine FCl: 1.95 mg/L Analyzer Total Chlorine TCl: 5.00 mg/L Simulated Free Grab @ 08:58 hrs. Sim FCl: 1.74 mg/L, Analyzer: FCl: 1.71 mg/L @ 09:14 returned pumps 1 and 3 back to auto (duty active) Equipment OOS: Pump 4, pump 2 (power loss) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 08:44 hrs. TCL: 1.59 mg/L Analyzer: TCl:: 1.51 mg/L Effluent Water Grab @ 08:47 hrs. FCl: 1.70 mg/L TCl: 3 grab ave. 2.50 mg/L, 2.44 mg/L, 2.48 mg/L Ave = 2.47 mg/L Effluent Analyzer adjusted to 2.47 mg/L Analyzer: Free Chlorine FCl: 1.62 mg/L Analyzer Total Chlorine TCl: 1.99 mg/L Simulated Free Grab @ 09:00 hrs. Sim FCl: 1.71 mg/L, Analyzer: FCl: 1.65 mg/L @ 09:01 sim free lolo alarm, disregard, low flow to analyzer Equipment OOS: Pump 4, pump 2 (power loss) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site to reset P1 and P3 VFD faults. P1 had no communication msg and P3 had over current msg on ABB pad. Reset the VFDs and they are back to standby. Ack+reset alarms. P1 and P3 started in auto. Station is back to normal operation. P2 remains OOS due to MV2 issue. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; no communication [control_system] | fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; no communication [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for Cl2 Cylinder change and installation of vent tubing. | FLAG | stage2_low_confidence | 0.010531 | ML: above threshold (no LLM available) — 0.011 |  | 0.010531 | 0 | 0
2026-02 | 2026-02-20 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 10:03 hrs. TCL: 1.51 mg/L Analyzer: TCl:: 1.47 mg/L Effluent Water Grab @ 10:04 hrs. FCl: 1.94 mg/L TCl: 1/4 dilution, 1.25 mg/L x 4 = 5.00 mg/L Analyzer: Free Chlorine FCl: 2.00 mg/L Analyzer Total Chlorine TCl: 4.97 mg/L Simulated Free Grab @ 10:10 hrs. Sim FCl: 1.72 mg/L, Analyzer: FCl: 1.72 mg/L Pumps 1 and 3 active in duty 1 Equipment OOS: Pump 4 (jockey pump), pump 2 (power loss) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-06 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - SL1000 Cleaning and Verification Influent Water Grab @ 12:06 hrs. TCl: 1.52 mg/L Analyzer: TCl: 1.52 mg/L Effluent Water Grab @ 12:08 hrs. FCl: 2.00 mg/L TCl: > 2.20 mg/L Analyzer FCl: 2.00 mg/L TCl: 4.71 mg/L Simulated Free Cl Grab @ 12:20 hrs. FCl: 1.80 mg/L Analyzer: FCl: 1.73 mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 6.6926e-05 | 0 | 0
2026-02 | 2026-02-03 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under direction of OIC Dan Zhou On site for; - generator test - JHSC health and safety inspection @ 09:07 informed ROC of generator test and JHSC inspections @ 09:09 hrs. Placed pump 1 in manual off, shut pump 2 off in manual @ 09:15 shut pump 3 off in manual Generator Test: Start hours: 461.9 Start time: 09:21 hrs. Stop Hours: 463.3 (includes cool down time) Stop Time: 10:50 hrs. Run Time: 1.2 hours Start Fuel: 2986/2284 L Stop Fuel: 2987/2214 L Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 09:32 hrs. Put pump 2 in Manual On @ 09:38 put pump 3 in Manual On Operating Current: 185 amps Operating Frequency: 61 Hz Operating Voltage: 600 Volts, Engine speed: 1803 RPM Water/coolant Temp: 172 F Oil Pressure: 61 psi Oil Temp: 182 F @ 10:20 hrs. Placed pump 2 in manual off @ 10:25 hrs. placed pump 3 in manual off @ 10:55 hrs. Returned all pumps to auto, pumps 2,3 active in duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure]; leak [infrastructure] | 0.00051834 | 0 | 0
2026-02 | 2026-02-03 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under direction of OIC Dan Zhou On site for PM?s; - Chlorine emergency repair kit inspection - Critical air valves flush and inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; repair [maintenance_action] | emergency [critical]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-09 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Duty rotated booster pumps: Placed P1 to D1, P2 to D2 | FLAG | stage2_low_confidence | 0.0086111 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure] | 0.0086111 | 0 | 0
2026-02 | 2026-02-09 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks - Investigate outlet MV for BP2 Data in PWQ workbook Influent Water Grab @ 10:33 hrs. TCL: 1.48 mg/L Analyzer: TCl:: 1.44 mg/L Effluent Water Grab @ 10:37 hrs. FCl: 1.87 mg/ TCl: 2.74 mg/L Analyzer: Free Chlorine FCl: 1.80 mg/L Analyzer Total Chlorine TCl: 2.65 mg/L Simulated Free Grab @ 10:41 hrs. Sim FCl: 1.95 mg/L, Analyzer: FCl: 1.86 mg/L Outlet MV at BP2 power loss. Flipped breaker, no change, flipped secondary power switch at valve, no change. MV at outlet for BP1 functions and is on the same breaker. Created WO for maintenance (W11649860). Valve left in local, BP2 in manual off. Duty inactive (pumps 1 and 3 in duty 1) Equipment OOS: Pump 4 Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 09:10 hrs. TCL: 1.53 mg/L Analyzer: TCl:: 1.51 mg/L Effluent Water Grab @ 09:13 hrs. FCl: 1.93 mg/L TCl: > 4.40 mg/L Analyzer: Free Chlorine FCl: 1.98 mg/L Analyzer Total Chlorine TCl: 4.75 mg/L Simulated Free Grab @ 09:17 hrs. Sim FCl: 1.72 mg/L, Analyzer: FCl: 1.77 mg/L Equipment OOS: Pump 4 Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-25 | Stouffville Zone 2 Elevated Tank | EAST | On site for station check and to collect weekly micro samples (W11620016) and HAA samples (W11676368). Collected Cl2 grab residuals on Header tap @10:40hrs and Sample: FCL: 1.75mg/l Analyzer FCL: 1.75mg/l TCL: 1.97mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-11 | Stouffville Zone 2 Elevated Tank | EAST | On site for station check and to collect weekly micro samples (W11588680) and HAA samples (W11642920). Collected in house iron samples. Collected Cl2 grab residuals on Header tap @12:00hrs and Sample: FCL: 1.72mg/l Analyzer FCL: 1.72mg/l TCL: 1.89mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | Stouffville Zone 2 Elevated Tank | EAST | On site for station check and to collect weekly micro samples (W11605521) and HAA samples (W11664457). Collected Cl2 grab residuals on Header tap @10:35hrs and Sample: FCL: 1.72mg/l Analyzer FCL: 1.70mg/l TCL: 1.91mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Stouffville Zone 2 Elevated Tank | EAST | On site for station check and to collect weekly micro samples (W11568302) and ANSCAN sample (W11568629). Collected Cl2 grab residuals on Header tap @10:40hrs and Sample: FCL: 1.91mg/l Analyzer FCL: 1.91mg/l TCL: 2.12mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-05 | Stouffville Zone 2 Elevated Tank | EAST | On site for monthly maintenance: 11:10hrs: Cleaned HACH CL17 Analyzer, Verified Analyzer after cleaning: FCL grab residual: 1.71mg/l, Analyzer FCL: 1.73mg/l. Sump Pit inspection, Manual valve exercise, Heat Trace System Inspection. Tested Low Temperature alarm, no issues. JHSC Inspection of STW3 and Z1 PS and this facility. | FLAG | stage2_low_confidence | 0.0075342 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075342 | 0 | 0
2026-02 | 2026-02-25 | Stouffville Zone 1 Elevated Tank | EAST | On site for station check and to collect weekly micro samples (W11620016) and HAA sample (W11676368). Collected in house iron samples and ATP. Collected Cl2 grab residuals on Header tap @11:15hrs and Sample: FCL: 1.34mg/l Analyzer FCL: 1.31mg/l TCL: 1.50mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-11 | Stouffville Zone 1 Elevated Tank | EAST | On site for station check and to collect weekly micro samples (W11588680) and HAA sample (W11642920). Collected in house iron samples. Collected Cl2 grab residuals on Header tap @12:35hrs and Sample: FCL: 1.41mg/l Analyzer FCL: 1.45mg/l TCL: 1.63mg/l Changed HACH Cl17 Reagents. Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-18 | Stouffville Zone 1 Elevated Tank | EAST | Attending site to check chlorine analyzer fault (W11670776). Analyzer had a motor error. Replaced motor and optical sensor. Verified reading at 1.39 mg/L Free. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.036628 | ML: above threshold (no LLM available) — 0.037 | fault [equipment_failure] | 0.036628 | 0 | 0
2026-02 | 2026-02-17 | Stouffville Zone 1 Elevated Tank | EAST | On site for station check and to collect weekly micro samples (W11605521) and HAA sample (W11664457). Collected Cl2 grab residuals on Header tap @11:50hrs and Sample: FCL: 1.34mg/l Analyzer FCL: 1.38mg/l TCL: 1.59mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-19 | Stouffville Zone 1 Elevated Tank | EAST | Deep cycle tower to 40% by changing the duty start setpoint from 60% to 40%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052243 | 0 | 0
2026-02 | 2026-02-17 | Stouffville Zone 1 Elevated Tank | EAST | On site responding to low low CL2 reading (0.00mg/l). Collected Free CL2 grab residual @ 12:35hrs: 1.35mg/l. Issue with the CL2 Analyzer itself, may be related to changing the reagents during station check. Initiated priming sequence to prime new reagents. Cl2 Analyzer didn't seem as though it was priming correctly, powered off Analyzer and powered back on. Received a "Motor Error" alarm on the Display. Spoke with instrumentation Eric S who will attend site. WO issued. | FLAG | stage2_low_confidence | 0.037163 | ML: above threshold (no LLM available) — 0.037 | alarm [control_system] | 0.037163 | 0 | 0
2026-02 | 2026-02-04 | Stouffville Zone 1 Elevated Tank | EAST | On site for station check and to collect weekly micro samples (W11568302) and ANSCAN sample (W11568629). Collected Cl2 grab residuals on Header tap @11:45hrs and Sample: FCL: 1.74mg/l Analyzer FCL: 1.73mg/l TCL: 1.95mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-05 | Stouffville Zone 1 Elevated Tank | EAST | On site for monthly maintenance: 12:55hrs: Cleaned HACH CL17 Analyzer, Verified Analyzer after cleaning: FCL grab residual: 1.72mg/l, Analyzer FCL: 1.65mg/l. Adjusted Cl2 Analyzer to reflect grab residual based on multiple CL2 grab residuals. Portable Generator run test, Heat Trace System Inspection. JHSC Inspection. Housekeeping. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071003 | 0 | 0
2026-02 | 2026-02-25 | Markham PD6 Reservoir | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling ( Micro, W11620058) - Operational sampling, nitrification Data in PWQ workbook Regulatory samples taken @ 10:21 from north cell South Cell Grab @ 10:07 hrs. TCl: 1.58 FCl: 0.02 Analyzer: TCl: 1.56 mg/L North Cell Grab @ 10:21 hrs. TCl: 1.51 mg/L FCl: 0.04 Analyzer: TCl: 1.56 mg/L Cells Filling Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-17 | Markham PD6 Reservoir | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling ( Micro, W11605563) - Operational sampling, nitrification and corrosion control, with ATP and flouride analysis Data in PWQ workbook Regulatory samples taken @ 10:00 from north cell South Cell Grab @ 09:54 hrs. TCl: 1.58 FCl: 0.04 Analyzer: TCl: 1.57 mg/L North Cell Grab @ 10:00 hrs. TCl: 1.48 mg/L FCl: 0.06 Analyzer: TCl: 1.57 mg/L Cells Draining Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-20 | Markham PD6 Reservoir | EAST | On site to change buffer and indicator reagents for total chlorine analyzer. | FLAG | stage2_low_confidence | 0.014523 | ML: above threshold (no LLM available) — 0.015 |  | 0.014523 | 0 | 0
2026-02 | 2026-02-04 | Markham PD6 Reservoir | EAST | On site for; - Station checks - Regulatory sampling ( Micro, W11568358) Data in PWQ workbook Regulatory samples taken @ 10:00 from north cell. South Cell Grab @ 09:57 hrs. TCl: 1.51 FCl: 0.07 Analyzer: TCl: 1.55 mg/L North Cell Grab @ 10:00 hrs. TCl: 1.45 mg/L FCl: 0.08 Cells Draining Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-11 | Markham PD6 Reservoir | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling ( Micro, W11588722) - Operational sampling, nitrification Data in PWQ workbook Regulatory samples taken @ 10:00 from north cell South Cell Grab @ 09:57 hrs. TCl: 1.51 FCl: 0.07 Analyzer: TCl: 1.58 mg/L North Cell Grab @ 10:00 hrs. TCl: 1.45 mg/L FCl: 1.53 Analyzer: TCl: 1.58 mg/L Cells Draining Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-05 | Markham PD6 Reservoir | EAST | Under direction of OIC Dan Zhou On site for PM's - Chlorine analyzer maintenance - Sump pump test - Dehumidifier cleaning and inspection - High/low water level alarms test - Flood alarm test - JHSC Health and Safety Inspection - External venting screens inspection - Air valve inspection - Comprehensive house cleaning Chlorine analyzer maintenance; Start Clean @ 12:25 hrs. Exited Clean @ 12:49 hrs. Post analyzer maintenance verification; Grab @ 13:00 hrs. TCl: 1.58 mg/L Analyzer: TCl: 1.54 mg/L Initiated Flood alarm @ 12:33 hrs. (OK) Flood Alarm test: Hi initiated @ 13:26 hrs. alarm in @ 13:26 hrs. (OK) Lo initiated @ 13:27 hrs. alarm in @ 13:29 hrs. (OK) | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | Keswick Water Treatment Plant | CENTRAL | Call from ROC about Co2 leak detector hihi alarm active. Logged in remotely to review trends on SCADA. Observed detector reading over 5000 between the hrs of 5 to 6pm. Noticed leak detector reading started to trend downward when duty deactivated. Spoke with Area TL over the phone, we agreed to leave plant off for the night for further investigation in the morning if the alarm is not triggered again. Notified ROC. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; leak [infrastructure] | scada [control_system]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-27 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Changed pre-free reagents -Performed filter performance review - 100% | FLAG | stage2_low_confidence | 0.010805 | ML: above threshold (no LLM available) — 0.011 |  | 0.010805 | 0 | 0
2026-02 | 2026-02-27 | Keswick Water Treatment Plant | CENTRAL | Filter performance both 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041743 | 0 | 0
2026-02 | 2026-02-26 | Keswick Water Treatment Plant | CENTRAL | Checked filter performance both 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043281 | 0 | 0
2026-02 | 2026-02-24 | Keswick Water Treatment Plant | CENTRAL | -Tested chlorine leak alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-23 | Keswick Water Treatment Plant | CENTRAL | As per workorder Filter performance review @ 4:55 pm via scada F1 and F2 100% all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0048551 | 0 | 0
2026-02 | 2026-02-25 | Keswick Water Treatment Plant | CENTRAL | -Changed chlorine cylinder -Responded lolo fluoride - noticed fluoride pump air locked - bleaded air -Performed station check - logged station readings into PWQ sheet -Collected weekly BacT sample YD #W11620086 -Performed filter performance review - 100% | FLAG | stage2_low_confidence | 0.013733 | ML: above threshold (no LLM available) — 0.014 |  | 0.013733 | 0 | 0
2026-02 | 2026-02-23 | Keswick Water Treatment Plant | CENTRAL | -Helped raw water sample line repair 1. LOTO low lift pump at breaker & discharge valve, travelling bar screen, raw water sample pump 2. Put LLP-FCV1, PACL pumps, SETL-TK11MV1, SETL-TK2-MV1 in manual off 3. Once the repair is done - removed the temporary sample line, put the permanent line online, restarted sample pump - no leak 4. Reversed all the changes -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.064125 | ML: above threshold (no LLM available) — 0.064 | repair [maintenance_action]; leak [infrastructure] | 0.064125 | 0 | 0
2026-02 | 2026-02-24 | Keswick Water Treatment Plant | CENTRAL | As per workorder Filter performance review via scada @ 3:25 pm F1 and F2 both 100% - all ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0043924 | 0 | 0
2026-02 | 2026-02-02 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Reviewed filter performance - 100% | FLAG | stage2_low_confidence | 0.010466 | ML: above threshold (no LLM available) — 0.01 |  | 0.010466 | 0 | 0
2026-02 | 2026-02-19 | Keswick Water Treatment Plant | CENTRAL | As directed by teamlead onsite to complete workorders Changed chlorine cylinder w/ Will M General Housekeeping Reset Raw water sample pump Fault 007 Also check filter performance via scada @ 11:00 am Filter 1 and 2 both 100% - all ok Ops normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; scada [control_system]; pump fault [infrastructure] | fault [equipment_failure]; scada [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-02 | 2026-02-11 | Keswick Water Treatment Plant | CENTRAL | Attending site to check Finished water turbidimeter (W11658745). There were no errors in the turbidimeter display. Replaced vial compartment assembly and Operations started high lift pumps. Observed turbidity to increase for a few minutes after startup and then drop to 0.121NTU, after several minutes. Turbidimeter spikes on startup have been occurring regularly. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.061397 | ML: above threshold (no LLM available) — 0.061 |  | 0.061397 | 0 | 0
2026-02 | 2026-02-18 | Keswick Water Treatment Plant | CENTRAL | -Helped replace 3" valve -Finished the following work orders *CL17 analyzer maintenance *High life pump 2 flow control valve test | FLAG | stage2_low_confidence | 0.014684 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action] | 0.014684 | 0 | 0
2026-02 | 2026-02-20 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Changed finished water free analyzer reagents -Performed filter performance review - 100% | FLAG | stage2_low_confidence | 0.011832 | ML: above threshold (no LLM available) — 0.012 |  | 0.011832 | 0 | 0
2026-02 | 2026-02-15 | Keswick Water Treatment Plant | CENTRAL | ROC called regarding settled water conduit lolo alarms, as well as CO2 adjusted pH low alarm. @15:36 - CO2 adjusted Low alarm, which stopped the low lift pumps, causing the settled water lolo alarms to follow @15:41 @15:49 when ROC called, CO2 adjusted pH had recovered. Was able to clear alarms and Low lifts restarted, filling the pretreatment / settled water conduit Monitored site remotely, everything is back to normal operations as of @16:00 | FLAG | stage2_low_confidence | 0.015727 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system]; alarms [control_system] | 0.015727 | 0 | 0
2026-02 | 2026-02-19 | Keswick Water Treatment Plant | CENTRAL | Under direction of OIC Ben Hess. Notified ROC or testing level transmitter in the diesel tank. Worked with contractors to connect and test diesel LIT and generator enclosure TT. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-12 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Reviewed filter performance - 100% -Collected GLIP sample & in-house water quality samples -Performed H&S inspection | FLAG | stage2_low_confidence | 0.011222 | ML: above threshold (no LLM available) — 0.011 |  | 0.011222 | 0 | 0
2026-02 | 2026-02-10 | Keswick Water Treatment Plant | CENTRAL | -Reviewed filter performance - 100% -Tried to isolated the plant for repair 3" gate valve - the one going east was successfully closed, but the one going west was frozen - will schedule another day and coordinate with the town of Georgina to isolate from the street -Finished the following work orders *Backwash tube maintenance *Pressure relief valve test *Hoist inspection *Washwater transfer pump maintenance *Filter Top Sample Water Pump Maintenance | FLAG | stage2_low_confidence | 0.03164 | ML: above threshold (no LLM available) — 0.032 | work order [maintenance_action]; repair [maintenance_action] | 0.03164 | 0 | 0
2026-02 | 2026-02-17 | Keswick Water Treatment Plant | CENTRAL | CO2 adjusted pH alarm came in, Co2 pH dropped to 6.5 from an increase in low lift flow. Cleared alarm, and low lift pumps restarted | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071663 | 0 | 0
2026-02 | 2026-02-13 | Keswick Water Treatment Plant | CENTRAL | -Topped up PACL day tank from 71.14cm to 82.28cm -Reviewed filter performance - 100% -Reset raw turbidimeter fault alarm - raw sample pump tripped - F007 - Restarted sample pump | FLAG | stage2_low_confidence | 0.044625 | ML: above threshold (no LLM available) — 0.045 | fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; alarm [control_system]; pump tripped [infrastructure] | 0.044625 | 0 | 0
2026-02 | 2026-02-16 | Keswick Water Treatment Plant | CENTRAL | Reviewed filter performance values and trends - both filters 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049503 | 0 | 0
2026-02 | 2026-02-13 | Keswick Water Treatment Plant | CENTRAL | Onsite to reset raw water sample pump fault. Fault 007 overload alarm Adjusted pump to 14 Hz Adjusted flow rates to pH probe, turbidimeter sample tap and lab sample tap. All in normal range. Reset low lift turbidimeter fault | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; pump fault [infrastructure] | fault [equipment_failure]; alarm [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-02 | 2026-02-20 | Keswick Water Treatment Plant | CENTRAL | Attending site to check low-lift Total Chlorine analyzer (W11679195). Cleaned colorimeter cell and calibrated but the reading went down to 0.02mg/L again. Replaced colorimeter and calibrated to 0.18mg/L, Total chlorine based on average of 3 grabs. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.035301 | ML: above threshold (no LLM available) — 0.035 |  | 0.035301 | 0 | 0
2026-02 | 2026-02-17 | Keswick Water Treatment Plant | CENTRAL | Under the direction of Ben H Onsite for station and equipment check Take weekly BacT sample W11605591 @ 11:00 am (running) Treated Total: 1.80 mg/l Treated Free: 1.50 mg/l Topped up Fluoride day tank Topped up PACL day tank Ack/reset raw sample pump fault and turbidimeter fault due to low flow - all ok Ops normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; pump fault [infrastructure] | fault [equipment_failure]; pump fault [infrastructure] |  | 1 | 0
2026-02 | 2026-02-20 | Keswick Water Treatment Plant | CENTRAL | Completed filter performance check: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049915 | 0 | 0
2026-02 | 2026-02-16 | Keswick Water Treatment Plant | CENTRAL | -Performed filter performance review - 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044728 | 0 | 0
2026-02 | 2026-02-17 | Keswick Water Treatment Plant | CENTRAL | -Reviewed filter performance - 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043114 | 0 | 0
2026-02 | 2026-02-18 | Keswick Water Treatment Plant | CENTRAL | Chris Iliohan and Tyler Smith in with contractor to freeze supply line from main Remove old valve and install new check for leaks. No leak noticed Work complete | FLAG | stage2_low_confidence | 0.029116 | ML: above threshold (no LLM available) — 0.029 | leak [infrastructure] | 0.029116 | 0 | 0
2026-02 | 2026-02-18 | Keswick Water Treatment Plant | CENTRAL | As per workorder check filter performance via scada @ 15:40 Both F1 and F2 100% - all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0049445 | 0 | 0
2026-02 | 2026-02-11 | Keswick Water Treatment Plant | CENTRAL | -Restarted the plant in auto - started with low lift pumps to fill the floc tank, settling tank, and conduit - when restarting high lift pump, the pump was interlocked by hi finish water turbidity - checked finish water turbidimeter - flow OK - performed a turbidimeter maintenance - turbidity still high - replaced sample cell - turbidity high - called in instrumentation on call Eric S. - Eric came in to replace the turbidimeter element - Turbidity came down - restarted high lift pump -Reviewed filter performance - 100% -Performed station check - logged station readings into PWQ sheet -Changed clear well free reagents -Collected weekly BacT sample YD #W11588750 Grab: free=1.28mg/L total=1.56mg/L Analzyer: free=1.23mg/L total=1.49mg/L | FLAG | stage2_low_confidence | 0.090228 | ML: above threshold (no LLM available) — 0.09 |  | 0.090228 | 0 | 0
2026-02 | 2026-02-09 | Keswick Water Treatment Plant | CENTRAL | Remove damaged piping on diesel cooling line and install isolation valve to stop water flowing through diesel | FLAG | stage2_low_confidence | 0.018184 | ML: above threshold (no LLM available) — 0.018 |  | 0.018184 | 0 | 0
2026-02 | 2026-02-05 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet Grab: treated free=1.51mg/L total=1.90mg/L@13:40 Analyzer: treated free=1.53mg/L total=1.92mg/L -Collected GIIP samples, weekly BacT sample YD #W11568386, algae sample YD#W11568587, & THM sample YD #W11568116 -Changed chlorine cylinder -Changed settling tank free analyzer reagents -Reviewed filter performance - 100% | FLAG | stage2_low_confidence | 0.015258 | ML: above threshold (no LLM available) — 0.015 |  | 0.015258 | 0 | 0
2026-02 | 2026-02-06 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.010636 | ML: above threshold (no LLM available) — 0.011 |  | 0.010636 | 0 | 0
2026-02 | 2026-02-04 | Keswick Water Treatment Plant | CENTRAL | Filter performance check completed: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049974 | 0 | 0
2026-02 | 2026-02-09 | Keswick Water Treatment Plant | CENTRAL | Onsite to complete station check. Topped up pacl day tanks. Around 10:30 found decommissioned generator water service was passing. Tightened 1? bypass valve and valve began leaking. Leaking water flowing into sanitary drain. 10:46 placed all high lifts and low lifts in manual off. Notified ROC of issues. Closed plant service isolation valve but valve continued to pass and valve housing cracked. Neither isolation valve in fluoride room are to be holding. Held off on attempting to isolate distribution plant isolation valves outside station due to extreme cold conditions and valves being very stiff. 11:30 Was able to temporarily cap leak at generator bypass. 12:00 maintenance arrived and able to install a more permanent cap. Created work order for maintenance to replace service water isolation valve. We will attempt to isolate station completely tomorrow with warmer weather. 14:02 completed filter performance review. Both filters at 100%. Verified all analyzers had reagents and correct flows. Entered data into process sheets. Outstanding settled water lolo alarm due to low lifts in manual off. Plant lab and analyzer verification unable to complete to do plant offline and service water valve issues. Will complete before placing plant online. No other issues found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] | bypass [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-02 | 2026-02-06 | Keswick Water Treatment Plant | CENTRAL | Completed filter performance check: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049915 | 0 | 0
2026-02 | 2026-02-05 | Keswick Water Treatment Plant | CENTRAL | -Finished the following work orders *Aerator maintenance *Flushed raw water sample line *Fluoride pump maintenance *Diesel generator test run -A technician from Black & McDonald came in to troubleshoot CO2 not start running - Checked heat trace to CO2 pipe - normal and working - Pressure restored to 210kPa - Low temp might cause low pressure | FLAG | stage2_low_confidence | 0.027188 | ML: above threshold (no LLM available) — 0.027 | work order [maintenance_action] | 0.027188 | 0 | 0
2026-02 | 2026-02-05 | Keswick Water Treatment Plant | CENTRAL | Completed filter performance check: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049915 | 0 | 0
2026-02 | 2026-02-09 | Keswick Water Treatment Plant | CENTRAL | Completed filter performance check: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049915 | 0 | 0
2026-02 | 2026-02-04 | Keswick Water Treatment Plant | CENTRAL | Received call from ROC stating they received a call from Linde technician that needs access to gate to look at CO2 system. Called technician to let them know I could be there in 45 minutes and technician said they would prefer to come back tomorrow at 8am. Will inform Central Crew. Placed High lifts in manual off to keep plant offline until technician can investigate CO2 not dosing issue. | FLAG | stage2_low_confidence | 0.0075834 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075834 | 0 | 0
2026-02 | 2026-02-03 | Keswick Water Treatment Plant | CENTRAL | -Reviewed filter performance - 100% -Finished the following work orders *Chemical pump inspection *Chlorine emergency kit inspection *Turbidimeter maintenance *Fluoride analyzer maintenance | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action] | emergency [critical]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-25 | Sutton Elevated Tank | EAST | On site for station check and weekly micro sampling (W11620769) Duty not active, tower level 62% Entered data in PWQ sheets. Verified analyzer: Inlet/Outlet at 10:32 Free Grab: 1.30 mg/L Analyzer: 1.26 mg/L Total Grab: 1.63 mg/l Collected micro sample from inlet/outlet at 10:38 Reviewed trends. Station OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054464 | 0 | 0
2026-02 | 2026-02-27 | Sutton Elevated Tank | EAST | On site to respond to building flood alarm. Float on sump pump was faulty. Swapped out sump pump with new pump. Tested, no issues. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; fault [equipment_failure]; alarm [control_system] | flood [critical]; fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | Sutton Elevated Tank | EAST | Attending site in response to the ROC calling for a building flood alarm. Sump pump had not triggered. Manually moved the float to trigger the pump. Tested the float a few more times to make sure it works. Notified ROC that the issue was corrected. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | Sutton Elevated Tank | EAST | On site for station check and weekly micro sampling (W11606343) Duty active, tower level 56% Entered station data into PWQ sheet. Verified chlorine analyzer: Grab sample taken at 10:50 Free Grab: 1.34 mg/L Analyzer: 1.28 mg/L Total Grab: 1.69 mg/L Micro sample taken from inlet/outlet tap at 10:54 Reviewed trends, no outstanding alarms. Station OK. | FLAG | stage2_low_confidence | 0.0081356 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0081356 | 0 | 0
2026-02 | 2026-02-12 | Sutton Elevated Tank | EAST | On site with S. Baidy to to climb tower and close rooftop hatch that was blown open. | FLAG | stage2_low_confidence | 0.015261 | ML: above threshold (no LLM available) — 0.015 |  | 0.015261 | 0 | 0
2026-02 | 2026-02-04 | Sutton Elevated Tank | EAST | On site for station check, weekly micro sampling (W11569329) and VOC sampling (W11569301) Tower level - 60% and draining. Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 10:40 Free Grab: 1.53 mg/L Analyzer: 1.47 mg/L Total Grab: 1.85 mg/L Collected micro sample @ 10:44 from inlet/outlet. Took VOC samples at 10:47. Reviewed trends, equipment ok Station ok | FLAG | stage2_low_confidence | 0.00784 | ML: above threshold (no LLM available) — 0.008 |  | 0.00784 | 0 | 0
2026-02 | 2026-02-11 | Sutton Elevated Tank | EAST | On site for station check, weekly micro sampling (W11589444) Tower level - 50% and filling. Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 10:11 Free Grab: 1.45 mg/L Analyzer: 1.42 mg/L Total Grab: 1.80 mg/L Collected micro sample @ 10:13 from inlet/outlet. Reviewed trends, equipment ok Station ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059975 | 0 | 0
2026-02 | 2026-02-03 | Sutton Elevated Tank | EAST | On site for monthly work orders, Notified ROC of work orders being done. Inlet/Outlet Heat Trace Inspection JHSC inspections, Chlorine analyzer maintenance, took grab sample to verify analyzer: Grab: 1.70 mg/L Analyzer: 1.66 mg/L Building low temp alarm test: alarm triggered at 13:38, reset and cleared. Manual valve exercise, Sump pit system inspection, Portable generator test run, And general housekeeping. | FLAG | stage2_low_confidence | 0.016488 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action]; alarm [control_system] | 0.016488 | 0 | 0
2026-02 | 2026-02-04 | Sutton Elevated Tank | EAST | Deactivated duty 1 for sampling. | FLAG | stage2_low_confidence | 0.0096669 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096669 | 0 | 0
2026-02 | 2026-02-26 | Keswick Deer Park Elevated Tank | EAST | Informed ROC. Onsite to perform calibration/maintenance on post injection and outlet chlorine analyzer. Used the calibration mode. Took a multiple grab samples and adjusted analyzers accordingly. Post injection chlorine analyzer Free readings A- 1.00 mg/l G- 1.00 mg/l Total readings A- 1.44 mg/l G- 1.45 mg/l Outlet chlorine analyzer Free readings A-1.29 mg/l G- 1.29 mg/l Total readings A- 1.73 mg/l G- 1.73 mg/l All the related alarms cleared. No issues. Informed ROC and left the site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.00025435 | 0 | 0
2026-02 | 2026-02-27 | Keswick Deer Park Elevated Tank | EAST | 14:05 chlorine grab / analyzer: (mg/l) Pre-injection free= 1.35 ?/ 1.46 Post injection free = 0.84 / 0.90 Outlet free = 0.10 / 0.01? 14:19 calibrated preinjection and outlet free according to 3 grabs' average.? Tower is isolated. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055938 | 0 | 0
2026-02 | 2026-02-27 | Keswick Deer Park Elevated Tank | EAST | On site with contractor from Syntec, Chris Scott and Dan Zhou to test operation of inlet valve. | FLAG | stage2_low_confidence | 0.016017 | ML: above threshold (no LLM available) — 0.016 |  | 0.016017 | 0 | 0
2026-02 | 2026-02-27 | Keswick Deer Park Elevated Tank | EAST | On site to assist with LCV commissioning. ET is isolated from the system. Opened the BV upstream of FCV while BV downstream remains closed. Opened the drain valve on inlet header to allow the new LCV to open. Placed dechlor pucks at outfall. Tested the LCV open/close function via SCADA. The LCV is de-energized now and will open in auto once the tower is online. ET level is 96% and remains offline. | FLAG | stage2_low_confidence | 0.012625 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.012625 | 0 | 0
2026-02 | 2026-02-27 | Keswick Deer Park Elevated Tank | EAST | On site to flush outlet line after bacteriological sample result received. Fully opened outlet riser isolation valve and opened outlet drain valve enough to hear flow through it. Placed de-chlor pucks in outfall. Flushed between 15:50 and 16:07. Verified analyzers with grab sample at 16:14 Grab free: 1.16 mg/L Analyzer: 5.00 mg/L Total grab: 1.57 mg/L Analyzer: 1.60 mg/L Adjusted free chlorine analyzer after three grab samples. Re-isolated outlet valve due to leaking drain valve. Tower still offline and isolated. | FLAG | stage2_low_confidence | 0.026319 | ML: above threshold (no LLM available) — 0.026 | leak [infrastructure]; leaking [infrastructure] | 0.026319 | 0 | 0
2026-02 | 2026-02-27 | Keswick Deer Park Elevated Tank | EAST | On site to check station Replaced chlorine injection lines with half inch tubing. Tested Lo alarm and flushed LIT: disregard alarms | FLAG | stage2_low_confidence | 0.010069 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010069 | 0 | 0
2026-02 | 2026-02-27 | Keswick Deer Park Elevated Tank | EAST | Onsite to commission the new altitude valve, had to download to the PAC to upgrade the revision. Site lost communication for about 5 minutes, Tower was offline and isolated when this occurred. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-24 | Keswick Deer Park Elevated Tank | EAST | Run tubing for analyzers Tuning installed just need instrumentation to connect | FLAG | stage2_low_confidence | 0.013128 | ML: above threshold (no LLM available) — 0.013 |  | 0.013128 | 0 | 0
2026-02 | 2026-02-25 | Keswick Deer Park Elevated Tank | EAST | 17:14 - Closed inlet valves to isolate tower at 96% 17:23 - took grab samples from inlet pipe: Free 1.61 mg/L, Total 1.96 mg/L 17:26 - took micro sample (W11673892) | FLAG | stage2_low_confidence | 0.0091228 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091228 | 0 | 0
2026-02 | 2026-02-25 | Keswick Deer Park Elevated Tank | EAST | On site to flush and to start filling KSETDP. @09:05 - Opened first inlet valve on the inlet header, and opened inlet drain valve cracked to flush lines to facility outfall Added dechlor pucks to outfall Outlet analyzer is currently plumbed to the inlet header. Took grab residuals while flushing @09:40 FCL: 1.15 mg/L / Analyzer: 2.30 mg/L - Adjusted analyzer to match grabs TCL: 1.35 mg/L / Analyzer: 1.44 mg/L - Adjusted analyzers to match grabs Grab residual from outfall @09:36 - 0.0 mg/L @09:40 - Closed drain valve on inlet line Removed LOTO from second inlet valve. From 09:40 to 09:55 - Flushed inlet riser pipe multiple times, by opening second inlet valve for a short period, and then closing the first inlet valve, and opening the drain valve to drain what was flushed into the riser pipe. Started filling tank @09:57 - Flow through inlet is 105 L/s. Inspected piping with contractors - no leaks observed on the inlet side. Took grab residuals while filling: FCL Grab: 1.36 / Analyzer: 1.41 mg/L Unshelved the following alarms - pH Lo, Tower level low alarms, Site offline alarms, Chlorine system alarms. No longer any shelved alarms for site Tower level is 15% @10:32 - will monitor and return to site later | FLAG | stage2_low_confidence | 0.078523 | ML: above threshold (no LLM available) — 0.079 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.078523 | 0 | 0
2026-02 | 2026-02-25 | Keswick Deer Park Elevated Tank | EAST | Onsite to commission new pre injection analyzer Site off line Informed ROC and ops Completed the work and verified signals to PAC with PCS Calibrated A=1.46mg/L G=1.45mg/L Cleared associated alarms Informed ROC | FLAG | stage2_low_confidence | 0.010237 | ML: above threshold (no LLM available) — 0.01 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.010237 | 0 | 0
2026-02 | 2026-02-02 | Keswick Deer Park Elevated Tank | EAST | Check drain requirements Measured up drain lines | FLAG | stage2_low_confidence | 0.011531 | ML: above threshold (no LLM available) — 0.012 |  | 0.011531 | 0 | 0
2026-02 | 2026-02-10 | Keswick Deer Park Elevated Tank | EAST | I?m site for station check and assigned work orders. Notified the ROC of work being done. Station Offline - Completed visual check of station, contractors not on site today. Chlorine gas detector test - gas leak and gas HIHI alarms triggered at 10:12, and reset. Building low temp alarm test - alarm triggered at 10:32 and reset, JHSC inspections, Ventilation system inspection, Portable generator test run, Chemical system inspection - system offline, performed visual inspection, And general housekeeping. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | gas leak [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-02 | Keswick Deer Park Elevated Tank | EAST | On site for station check - Landmark is on site for upgrades projects Visual inspection of site and equipment Station ok | FLAG | stage2_low_confidence | 0.012371 | ML: above threshold (no LLM available) — 0.012 |  | 0.012371 | 0 | 0
2026-02 | 2026-02-20 | Keswick Deer Park Elevated Tank | EAST | Connect water temporarily to analyzer Bleed air out of altitude valve and fully open | FLAG | stage2_low_confidence | 0.013529 | ML: above threshold (no LLM available) — 0.014 |  | 0.013529 | 0 | 0
2026-02 | 2026-02-20 | Keswick Deer Park Elevated Tank | EAST | 15:15 Returned to site. 15:18 Verified outfall chlorine residual by grab, FCL = 0.01 mg/l. 15:20 grab chlorine residual from inlet, FCL = 1.30 mg/l, TCL = 1.69 mg/l. Adjusted Outlet analyzer (temporarily plumbed to inlet sample line) to match with 3 grabs average. 15:30 Closed the drain valve. Estimated backflushing volume is to be calculated later. The tower remains isolated from the system. | FLAG | stage2_low_confidence | 0.012131 | ML: above threshold (no LLM available) — 0.012 |  | 0.012131 | 0 | 0
2026-02 | 2026-02-20 | Keswick Deer Park Elevated Tank | EAST | On site with Dan Boate, wiring altitude valve and chlorine analyzer. | FLAG | stage2_low_confidence | 0.014066 | ML: above threshold (no LLM available) — 0.014 |  | 0.014066 | 0 | 0
2026-02 | 2026-02-12 | Keswick Deer Park Elevated Tank | EAST | On site with Sean Peoples installing conduit for new analyzer and valve. | FLAG | stage2_low_confidence | 0.014372 | ML: above threshold (no LLM available) — 0.014 |  | 0.014372 | 0 | 0
2026-02 | 2026-02-20 | Keswick Deer Park Elevated Tank | EAST | On site with Jackie S to flush the watermain through drain valve to outfall. Verified all pipe gallery manual valves are in closed position. Lee F. and Kyle R. arrived on site as well. Plumbed the inlet header sample line to Outlet Analyzer temporarily since the new analyzer is not commissioned yet. Worked with Harsh to locate the valve box at Boyers/Queensway, opened the valve slowly. Worked with Lee F to slowly charge the new Singer valve, purged air out of the sensing lines and it is fully open. 11:55 crack opened the drain valve on the inlet header. Checked outfall for flow rate that it is controlled discharge. Placed dechlor pucks at outfall. 12:10 grab chlorine residual at outfall, FCL = 0.00 mg/l. 12:22 grab chlorine residual from inlet header: FCL = 0.01 mg/l, TCL = 0.11 mg/l. Will return to site to later in the afternoon. | FLAG | stage2_low_confidence | 0.014808 | ML: above threshold (no LLM available) — 0.015 |  | 0.014808 | 0 | 0
2026-02 | 2026-02-11 | Keswick Deer Park Elevated Tank | EAST | On site to work on altitude valve wiring. | FLAG | stage2_low_confidence | 0.012514 | ML: above threshold (no LLM available) — 0.013 |  | 0.012514 | 0 | 0
2026-02 | 2026-02-04 | Keswick Deer Park Elevated Tank | EAST | Install drain for analyzer | FLAG | stage2_low_confidence | 0.012411 | ML: above threshold (no LLM available) — 0.012 |  | 0.012411 | 0 | 0
2026-02 | 2026-02-11 | Keswick Deer Park Elevated Tank | EAST | On site for station check. Site Offline. Completed visual check. Station ok. | FLAG | stage2_low_confidence | 0.010105 | ML: above threshold (no LLM available) — 0.01 |  | 0.010105 | 0 | 0
2026-02 | 2026-02-04 | Keswick Deer Park Elevated Tank | EAST | On site for station check. Station Offline. Completed visual check of station. Station ok. | FLAG | stage2_low_confidence | 0.010787 | ML: above threshold (no LLM available) — 0.011 |  | 0.010787 | 0 | 0
2026-02 | 2026-02-09 | Keswick Deer Park Elevated Tank | EAST | On site to run conduits for new valve and analyser | FLAG | stage2_low_confidence | 0.013076 | ML: above threshold (no LLM available) — 0.013 |  | 0.013076 | 0 | 0
2026-02 | 2026-02-25 | Keswick West Park Reservoir | CENTRAL | Closed Inlet valve MV1 - Tower level is 87%. In order to allow KSETDP to fill quicker. Will be reopened later in the day. West park tank is isolated from distribution | FLAG | stage2_low_confidence | 0.0079599 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079599 | 0 | 0
2026-02 | 2026-02-25 | Keswick West Park Reservoir | CENTRAL | Adjusted duty stop from 85% to 90% in order to fill KSETDP | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048101 | 0 | 0
2026-02 | 2026-02-27 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Calibrated free analyzer based on 3 grab tests | FLAG | stage2_low_confidence | 0.011035 | ML: above threshold (no LLM available) — 0.011 |  | 0.011035 | 0 | 0
2026-02 | 2026-02-25 | Keswick West Park Reservoir | CENTRAL | Deactivated system duty. Manual open inlet valve MV1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038993 | 0 | 0
2026-02 | 2026-02-24 | Keswick West Park Reservoir | CENTRAL | -Tested chlorine leak alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.010636 | ML: above threshold (no LLM available) — 0.011 |  | 0.010636 | 0 | 0
2026-02 | 2026-02-25 | Keswick West Park Reservoir | CENTRAL | Station and equipment check Take weekly BacT sample W11620838 @ 8:25 am (draining) Total: 1.76 mg/l Free: 1.40 mg/l No adjustments required Changed CL2 cylinder w/ JZ (right side) Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058872 | 0 | 0
2026-02 | 2026-02-02 | Keswick West Park Reservoir | CENTRAL | Attending site to check issue with Chlorinator #1 failing to close (W11539246). Adjusted milliamp output on chlorinator and actuated chlorinator to check that it closes completely. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.025839 | ML: above threshold (no LLM available) — 0.026 |  | 0.025839 | 0 | 0
2026-02 | 2026-02-02 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet Grab: treated free=1.49mg/L total=1.82mg/L@9:00 Analyzer: treated free=1.54mg/L total=1.79mg/L -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.0096604 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096604 | 0 | 0
2026-02 | 2026-02-20 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Changed free reagents | FLAG | stage2_low_confidence | 0.013663 | ML: above threshold (no LLM available) — 0.014 |  | 0.013663 | 0 | 0
2026-02 | 2026-02-17 | Keswick West Park Reservoir | CENTRAL | Station and equipment check Take weekly BacT sample w11606488 and grabs. @ 12:50 pm Total: 1.77 mg/l Free: 1.30 mg/l Standardized total analyzer to match grabs Tank ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065787 | 0 | 0
2026-02 | 2026-02-13 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.010636 | ML: above threshold (no LLM available) — 0.011 |  | 0.010636 | 0 | 0
2026-02 | 2026-02-06 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Cleaned CL17 analyzers | FLAG | stage2_low_confidence | 0.009897 | ML: above threshold (no LLM available) — 0.01 |  | 0.009897 | 0 | 0
2026-02 | 2026-02-11 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Collected weekly BacT sample YD #W11589619 -Changed treated total reagents - OK -Finished the following work orders *H&S inspection *Chemical system inspection *Test ran generator | FLAG | stage2_low_confidence | 0.014567 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action] | 0.014567 | 0 | 0
2026-02 | 2026-02-04 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet Grab: free=1.53mg/L total=1.75mg/L@9:30 Analyzer: free=1.53mg/L total=1.79mg/L -Checked CL17 reagents - Ok -Collected weekly BacT sample YD #W11569728 & monthly samples YD #W11569714 | FLAG | stage2_low_confidence | 0.011246 | ML: above threshold (no LLM available) — 0.011 |  | 0.011246 | 0 | 0
2026-02 | 2026-02-09 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.010636 | ML: above threshold (no LLM available) — 0.011 |  | 0.010636 | 0 | 0
2026-02 | 2026-02-27 | Musselman's Lake Elevated Tank | EAST | Thaw outlet pipe Thawed pipe 25 ? could not see any more ice | FLAG | stage2_low_confidence | 0.0093013 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093013 | 0 | 0
2026-02 | 2026-02-25 | Musselman's Lake Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11619922 Weekly Bac-t Sample. Time: 14:08 Grab (mg/l) Analyzer (mg/l) Free: 1.34 1.39 Total: 1.39 No outstanding alarms on site. No OOS equipment. Verified analyzers. Checked station and trends. | FLAG | stage2_low_confidence | 0.010587 | ML: above threshold (no LLM available) — 0.011 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.010587 | 0 | 0
2026-02 | 2026-02-26 | Musselman's Lake Elevated Tank | EAST | On site to complete following work orders: Chlorine analyzer maintenance. Heat trace inspection. Portable gasoline generator test. JHSC inspection. Contacted ROC at 12:56 about alarms being generated. After completing analyzer maintenance took grabs to verify analyzer. Time: 13:15 Grab (mg/l) Analyzer (mg/l) Free: 1.40 1.39 Completed calibration on pocket colorimetre passed. No issues any changes in trends are due to work orders being completed. | FLAG | stage2_low_confidence | 0.016254 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.016254 | 0 | 0
2026-02 | 2026-02-17 | Musselman's Lake Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11605419 Weekly Bac-t Sample. Time: 09:15 Grab (mg/l) Analyzer (mg/l) Free: 1.35 1.36 Total: 1.49 Verified analyzer with grabs. Started well 3 at 09:20 in manual for sampling. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | FLAG | stage2_low_confidence | 0.011668 | ML: above threshold (no LLM available) — 0.012 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011668 | 0 | 0
2026-02 | 2026-02-19 | Musselman's Lake Elevated Tank | EAST | Change duty 1 start set point from 72% to 40%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045436 | 0 | 0
2026-02 | 2026-02-11 | Musselman's Lake Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11588586 Weekly Bac-t Sample. Time: 08:45 Grab (mg/l) Analyzer (mg/l) Free: 1.36 1.38 Total: 1.48 Outfall was plugged with ice and flooded the valve room. Was able to unplug by using a pick axe which allowed the water to drain. Also replaced the CL-17 chlorine analyzer reagents. No outstanding alarms on site. No OOS equipment on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; plugged [infrastructure] | flood [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; plugged [infrastructure] |  | 1 | 0
2026-02 | 2026-02-05 | Musselman's Lake Elevated Tank | EAST | Updating PAC for upcoming well pmp4 commissioning, including duty logic, total flow calculation, PTTW code etc. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061161 | 0 | 0
2026-02 | 2026-02-04 | Musselman's Lake Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11568186 Weekly Bac-t Sample. Time: 09:35 Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.38 Total: 1.46 Verified analyzer on site. No outstanding alarms on site. No OOS equipment on site. Checked station and trends. | FLAG | stage2_low_confidence | 0.011403 | ML: above threshold (no LLM available) — 0.011 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011403 | 0 | 0
2026-02 | 2026-02-25 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | Incrementally increased MV1 open set point from 5% to 17%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047969 | 0 | 0
2026-02 | 2026-02-25 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | Closed tower valve MV1 @10:01 - to allow more flow to fill KSETDP. Tower is currently isolated from distribution, level is 74% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055134 | 0 | 0
2026-02 | 2026-02-25 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | Changed MV1 open setpoint to 50%. Placed MV1 back in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040979 | 0 | 0
2026-02 | 2026-02-25 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site for station check and weekly micro sampling (W11620783) Duty active, tower level 69% Manual open recirculation valve, and manual start recirculation pump. Recorded station readings in PWQ sheets Verified analyzer readings: Header @ 9:15 Free Grab: 1.39 mg/L Analyzer: 1.31 mg/L Total Grab: 1.68 mg/L Analyzer: 1.72 mg/L Inlet @ 9:20 Free Grab: 1.62 mg/L Analyzer: 1.62 mg/L Total Grab: 2.00 mg/L Analyzer: 1.99 mg/L Outlet @ 9:06 Free Grab: 1.45 mg/L Analyzer: 1.42 mg/L Total Grab: 1.73 mg/L Analyzer: 1.66 mg/L Collected micro sample from outlet @ 9:10. 9:19 - manual stop recirculation pump, manual close recirculation valve, and place both back in auto. Chemical system: Chlorinator 1 open 13%, BP1 DP=908 kpa Noticed chlorine sysem drawing from left bank, right bank tank not empty. Found that right bank tank was closed, re-opned tank and put back in service. Reviewed trends, checked station. Station OK. | FLAG | stage2_low_confidence | 0.010754 | ML: above threshold (no LLM available) — 0.011 |  | 0.010754 | 0 | 0
2026-02 | 2026-02-25 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | Tower valve MV1 placed back to auto, open 100% @14:47 - Started closing tower isolation valve MV1 to throttle down the flow to fill KSETDP faster. Monitored system pressure on woodbine ET header, and both WTPs | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056231 | 0 | 0
2026-02 | 2026-02-17 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site for station check and weekly micro sampling (W11606357) Duty not active, tower level 64% Manual open recirculation valve, and manual start recirculation pump. Recorded station readings in PWQ sheets Verified analyzer readings: Header @ 9:23 Free Grab: 1.34 mg/L Analyzer: 1.31 mg/L Total Grab: 1.70 mg/L Analyzer: 1.69 mg/L Inlet @ 9:29 Free Grab: 1.35 mg/L Analyzer: 1.17 mg/L Total Grab: 1.68 mg/L Analyzer: 1.66 mg/L Adjusted inlet free chlorine value with the avg of three grab samples. Outlet @ 9:36 Free Grab: 1.38 mg/L Analyzer: 1.42 mg/L Total Grab: 1.69 mg/L Analyzer: 1.66 mg/L Collected micro sample from header @ 9:27. 9:42 - manual stop recirculation pump, manual close recirculation valve, and place both back in auto. Reviewed trends, checked station. Station OK. | FLAG | stage2_low_confidence | 0.0099312 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099312 | 0 | 0
2026-02 | 2026-02-11 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site for station check, weekly micro sampling (W11589458) Duty not active - Tower level 71% and draining. Manual open recirculation valve, and manual start recirculation pump. Recorded station readings in PWQ sheets Verified analyzer reading: Header @ 8:55 Free Grab: 1.51 mg/L Analyzer: 1.46 mg/L Total Grab: 1.85 mg/L Analyzer: 1.90 mg/L Inlet @ 8:59 Free Grab: 1.50 mg/L Analyzer: 1.42 mg/L Total Grab: 1.87 mg/L Analyzer: 1.83 mg/L Outlet @ 9:04 Free Grab: 1.53 mg/L Analyzer: 1.54 mg/L Total Grab: 1.87 mg/L Analyzer: 1.86 mg/L Collected micro sample from header @ 9:07. Amish stop recirculation pump, and close recirculation valve. Place both back in auto Reviewed trends, equipment ok Station ok | FLAG | stage2_low_confidence | 0.0081422 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081422 | 0 | 0
2026-02 | 2026-02-13 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | Reviewed station trends in lieu of on site station check. Duty active, tower level 75%. Trends all okay. No outstanding alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0043808 | 0 | 0
2026-02 | 2026-02-19 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site with Sean Peoples. Heater in chlorine scrubber rm replaced. | FLAG | stage2_low_confidence | 0.014022 | ML: above threshold (no LLM available) — 0.014 |  | 0.014022 | 0 | 0
2026-02 | 2026-02-06 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site for station check. Duty not active - Tower level 71% and draining Recorded station readings in PWQ sheets Manual start re-circulation pump. Verified analyzer readings, took grab samples between 9:44-9:52 No adjustments needed. Manual stop recirculation pump. Reviewed trends, equipment ok. Outstanding alarms: N/A Station ok Header @ 9:44 Free Grab: 1.54 mg/L Analyzer: 1.59 mg/L Total Grab: 1.91 mg/L Analyzer: 1.93 mg/L Adjusted free chlorine reading after three grab residuals. Inlet @ 9:52 Free Grab: 1.54 mg/L Analyzer: 1.55 mg/L Total Grab: 1.90 mg/L Analyzer: 1.81 mg/L Adjusted free chlorine reading after three grab residuals. Outlet @ 9:47 Free Grab: 1.55 mg/L Analyzer: 1.60 mg/L Total Grab: 1.90 mg/L Analyzer: 1.88 mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0053444 | 0 | 0
2026-02 | 2026-02-05 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site for station check and monthly work orders, Notified ROC of work orders being done. 9:45 - Chlorine gas detectors test: alarms triggered and were cleared. Chlorine scrubber check, Chlorine analyzer maintenance: flushed y-screens. Zero call inlet free Cl analyzer with no flow conditions. Returned all analyzers to normal operations. Verified chlorine analyzers: Header @ 10:43 Free Grab: 1.55 mg/L Analyzer: 1.58 mg/L Total Grab: 1.91 mg/L Analyzer: 1.95 mg/L Inlet @ 10:48 Free Grab: 1.90 mg/L Analyzer: 2.14 mg/L Total Grab: 2.18 mg/L Analyzer: 2.27 mg/L Outlet @ 10:52 Free Grab: 1.56 mg/L Analyzer: 1.58 mg/L Total Grab: 1.91 mg/L Analyzer: 1.88 mg/L Run recirculation pump, Inlet/outlet heat trace inspection, Manual valve exercise, Actuated valve exercise, Chlorine Scrubber media sampling, Ventilation system inspection, Dehumidifier inspection and cleaning. Entered data into PWQ sheet. Reviewed trends, equipment ok. Station ok. | FLAG | stage2_low_confidence | 0.012468 | ML: above threshold (no LLM available) — 0.012 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.012468 | 0 | 0
2026-02 | 2026-02-04 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site for station check, weekly micro sampling (W11569343), and VOC sampling (W11569315) Tower level - 77% and draining. Recorded station readings in PWQ sheets Verified analyzer reading: Header @ 9:13 Free Grab: 1.57 mg/L Analyzer: 1.56 mg/L Total Grab: 1.90 mg/L Analyzer: 1.91 mg/L Inlet @ 9:25 Free Grab: 1.78 mg/L Analyzer: 2.11 mg/L Total Grab: 2.07 mg/L Analyzer: 2.13 mg/L Adjusted inlet free Cl analyzer after three grab samples. Outlet @ 9:28 Free Grab: 1.59 mg/L Analyzer: 1.62 mg/L Total Grab: 1.89 mg/L Analyzer: 1.74 mg/L Adjusted outlet total Cl analyzer after three grab samples. Collected micro sample from header @ 9:17, took VOC samples at 9:20 Reviewed trends, equipment ok Station ok Completed JHSC inspections. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064563 | 0 | 0
2026-02 | 2026-02-27 | Markham Pumping Station | EAST | Placed pumps back into "REMOTE" after Linear work was completed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065237 | 0 | 0
2026-02 | 2026-02-23 | Markham Pumping Station | EAST | Under direction of OIC (Dan Zhou) On site for; - Station checks Analyzer verification: Grabs @ 11:35 hrs. FCl: 0.04 mg/L TCl: 1.35 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.34 mg/L Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-26 | Markham Pumping Station | EAST | Under direction of OIC (Dan Zhou) On site for; - Station checks Analyzer verification: Grabs @ 12:53 hrs. FCl: 0.03 mg/L TCl: 1.37 mg/L Analyzer: FCl: 0.00 mg/L TCl: 1.33 mg/L Duty inactive Equipment OOS: Facility, due to isolation by linear team for valve repairs. Pumps 1,2,3 in local. Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action] | oos [equipment_failure]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-02 | Markham Pumping Station | EAST | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 14:51 hrs. FCl: 0.10 mg/L TCl: 1.42 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.35 mg/L Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-19 | Markham Pumping Station | EAST | Under Direction of OIC (Dan Zhou) On Site for PM?s - JHSC Health and Safety checks - Flood alarm test - Comprehensive cleaning - Dehumidifier cleaning and inspection - Generator test run - Hoist inspection Generator Test: Start hours: 589.0 Start time: 10:18 hrs. Stop Hours: 590.6 (includes cool down time) Stop Time: 11:55 hrs. Run Time: 1 hr. 37 mins. Start Fuel: 578/579 L Stop Fuel: 550/548 L Pre run checks; Battery Cell Levels: NA Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 10:37 hrs. Put pump 2in Manual On (Active), Generator under load @ 11:19 hrs. put pump 2 in manual off Operating Current: 30 amps Operating Frequency: 60 Hz Operating Voltage: 600 Volts, Engine speed: 1801 RPM Water/coolant Temp: 183 f Oil Pressure: 58 psi kPa Oil temp: 197 f @ 11:57 manually triggered flood alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; fault [equipment_failure]; alarm [control_system]; leak [infrastructure] | flood [critical]; fault [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-17 | Markham Pumping Station | EAST | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 12:35 hrs. FCl: 0.05 mg/L TCl: 1.37 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.33 mg/L Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-13 | Markham Pumping Station | EAST | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 09:53 hrs. FCl: 0.07 mg/L TCl: 1.44 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.44 mg/L Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-20 | Markham Pumping Station | EAST | Under direction of OIC (Dan Zhou) On site for; - Station checks - Chlorine analyzer maintenance Analyzer verification: Grabs @ 11:19 hrs. FCl: 0.03 mg/L TCl: 1.31 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.29 mg/L Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Markham Pumping Station | EAST | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 11:53 hrs. FCl: 0.04 mg/L TCl: 1.09 mg/L based on 3 grab ave. Analyzer: FCl: 0.00 mg/L TCl: 0.68-1.25 mg/L ? Trial isolation by linear affecting flow/pressure to analyzer, inaccurate readings by analyzer. Analyzer OOS until isolation valve is reopened. Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-25 | Markham Milliken Elevated Tank | EAST | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling, (Micro, W11620058) - Operational sampling; nitrification - Actuated valve exercise and inspection (draining during inspection, @ 77 %) Data in PWQ workbook Regulatory sample taken @ 12:58 hrs. Grabs @ 12:58 hrs. FCl: 0.07 mg/L TCl: 1.68 mg/L Analyzer: FCl: 0.03 mg/L TCl: 1.68 mg/L Tower at 83 % (Filling, during sampling) Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-25 | Markham Milliken Elevated Tank | EAST | On site to investigate network connections. | FLAG | stage2_low_confidence | 0.012592 | ML: above threshold (no LLM available) — 0.013 |  | 0.012592 | 0 | 0
2026-02 | 2026-02-11 | Markham Milliken Elevated Tank | EAST | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling none, (Micro, W11588722) - operational sampling, nitrification Data in PWQ workbook Regulatory sample taken @ 12:44 hrs. Grabs @ 12:44 hrs. FCl: 0.07 mg/L TCl: 1.82mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.78 mg/L Tower at 80 % (Filling) Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-17 | Markham Milliken Elevated Tank | EAST | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling none, (Micro, W11605563) - Operational sampling; nitrification and corrosion control, ATP Data in PWQ workbook Regulatory sample taken @ 12:44 hrs. Grabs @ 12:44 hrs. FCl: 0.07 TCl: 1.61 Analyzer: FCl: 0.02 TCl: 1.66 Tower at 72 % (Filling) Equipment OOS: none Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-12 | Markham Milliken Elevated Tank | EAST | Under direction of OIC Dan Zhou On Site for PM?s; - Inlet/outlet Heat trace system Inspection - Low temp alarm test - Sump pit system inspection - Chlorine analyzer maintenance - Comprehensive cleaning - JHSC health and safety inspection - Dehumidifier inspection and cleaning Analyzer verification; Grabs @ 11:48 hrs. FCl: 0.05 mg/L TCl: 1.72 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.76 mg/L HI/LO Water level Alarms: HI water level alarm triggered @ 12:00 hrs. LO water level alarm triggered @ 12:03 hrs. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.00055202 | 0 | 0
2026-02 | 2026-02-27 | Markham PD5 Reservoir | EAST | Onsite to respond to building smoke alarm. Smoke alarm active after power blip on site and ROC was able to clear it first time and alarm became active again and ROC could not clear and reset this time, Arrived onsite, went into the valve room, conducted visual inspection no issues. logged into the OIT cleared building alarm. During time of visit there was a mobile generator (trailer) running with blowers and heaters supplying heat and light into the reservoir. the valve room had a burning smell or looks like hot work was done before my arrival. there was dust in the building, There was no body onsite as it was after hours, I talked to area supervisor, and will call him back if alarm comes in again for further action. Notified ROC before leaving site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: smoke [equipment_failure]; burning smell [equipment_failure]; alarm [control_system] | smoke [equipment_failure]; burning smell [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | Markham PD5 Reservoir | EAST | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11588722) - Operational sampling, nitrification Data in PWQ workbook Regulatory sample taken from west cell @ 11:01 hrs. West Cell Grabs @ 11:01 hrs. FCl: 0.07 TCl: 1.49 Analyzer: FCl: 0.03 TCl: 1.55 Equipment OOS: East Cell Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-25 | Markham PD5 Reservoir | EAST | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11620058) - Operational sampling, nitrification Data in PWQ workbook Regulatory sample taken @ 11:07 hrs. from west cell West Cell Grabs @ 11:07 hrs. FCl: 0.07 mg/L TCl: 1.46 mg/L Analyzer: FCl: 0.03 mg/L TCl: 1.50 mg/L Equipment OOS: East Cell Facility O | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-17 | Markham PD5 Reservoir | EAST | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11605563) - Operational sampling, nitrification and corrosion control, with ATP - Interconnect valve between PD5-PD6 inspection Data in PWQ workbook Regulatory sample taken @ 10:58 hrs. from west cell West Cell Grabs @ 10:58 hrs. FCl: 0.07 TCl: 1.51 Analyzer: FCl: 0.03 TCl: 1.52 Equipment OOS: East Cell (under construction) Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-04 | Markham PD5 Reservoir | EAST | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11568358) - Inspect interconnect valve between east/west cell Data in PWQ workbook Regulatory sample taken @ 10:43 hrs. West Cell Grabs @ 10:43 hrs. FCl: 0.05 TCl: 1.44 Analyzer: FCl: 0.03 TCl: 1.45 Equipment OOS: East Cell Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-02 | 2026-02-03 | Markham PD5 Reservoir | EAST | Under direction of OIC Dan Zhou On site for PM?s; - High/low water level alarm - JHSC health and safety inspection - External venting screens inspection - Chlorine analyzer maintenance - Comprehensive housekeeping Chlorine analyzer verification: Grabs @ 12:37 hrs. From west cell FCl: 0.06 mg/L TCl: 1.42 mg/L Analyzer FCl: 0.03 mg/L TCl: 1.47 mg/L Hi/Lo water level alarms functioning East Cell OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-23 | Stouffville Well 3 | EAST | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.60mg/l FCL Analyzer: 2.58mg/l 10:25hrs: Effluent Free Cl2 grab residual: 2.62mg/l FCL Analyzer: 2.58mg/l Effluent Total Cl2 grab residual: 2.85mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-25 | Stouffville Well 3 | EAST | On site for station check and to collect weekly micro samples (W11620016). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.56mg/l FCL Analyzer: 2.52mg/l 09:42hrs: Effluent Free Cl2 grab residual: 2.56mg/l FCL Analyzer: 2.52mg/l Effluent Total Cl2 grab residual: 2.80mg/l Raw collected @ 09:42hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-26 | Stouffville Well 3 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.56mg/l FCL Analyzer: 2.57mg/l 10:55hrs: Effluent Free Cl2 grab residual: 2.44mg/l FCL Analyzer: 2.50mg/l Effluent Total Cl2 grab residual: 2.84mg/l Silicate system inspection. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Stouffville Well 3 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.46mg/l FCL Analyzer: 2.42mg/l 11:25hrs: Collected Raw PH: 7.27 11:25hrs: Effluent Free Cl2 grab residual: 2.34mg/l FCL Analyzer: 2.33mg/l Effluent Total Cl2 grab residual: 2.60mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-12 | Stouffville Well 3 | EAST | On site with Travis Wyatt for Chlorine Cylinder change. Conducted monthly maintenance: 10:00hrs: Cleaned HACH CL17 Analyzer, Verified Analyzers after cleaning @10:25hrs: Influent FCL grab residual: 2.46mg/l, Analyzer: 2.44mg/l Effluent FCL grab residual: 2.40mg/l. Analyzer: 2.34mg/l Turbidimeter Calibration and maintenance Chlorine Leak Detector Test Silicate system inspection, injection point cleaning and pump dosage checks. Replaced diaphragm on Pump 2. Chlorine system inspection. Chlorinator #2 OOS for rotameter installation. Housekeeping | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; leak [infrastructure] | oos [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | Stouffville Well 3 | EAST | On site with Travis Wyatt for Cylinder change. | FLAG | stage2_low_confidence | 0.012743 | ML: above threshold (no LLM available) — 0.013 |  | 0.012743 | 0 | 0
2026-02 | 2026-02-20 | Stouffville Well 3 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.52mg/l FCL Analyzer: 2.55mg/l 12:45hrs: Effluent Free Cl2 grab residual: 2.50mg/l FCL Analyzer: 2.53mg/l Effluent Total Cl2 grab residual: 2.86mg/l Changed Influent and Effluent Analyzer reagents. Decreased Chlorine Influent dosage setpoint from 2.60mg/l to 2.50mg/l due to middle of winter. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | Stouffville Well 3 | EAST | On site for station check and to collect weekly micro samples (W11605521). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.58mg/l FCL Analyzer: 2.55mg/l 09:55hrs: Effluent Free Cl2 grab residual: 2.60mg/l FCL Analyzer: 2.54mg/l Effluent Total Cl2 grab residual: 2.92mg/l Raw collected @ 09:55hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-11 | Stouffville Well 3 | EAST | On site for station check and to collect weekly micro samples (W11588680). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.60mg/l FCL Analyzer: 2.63mg/l 09:40hrs: Effluent Free Cl2 grab residual: 2.62mg/l FCL Analyzer: 2.60mg/l Effluent Total Cl2 grab residual: 3.00mg/l Raw collected @ 09:40hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-18 | Stouffville Well 3 | EAST | On site for Silicate delivery from 33.93cm to 65.8cm. | FLAG | stage2_low_confidence | 0.0099587 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099587 | 0 | 0
2026-02 | 2026-02-13 | Stouffville Well 3 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.55mg/l FCL Analyzer: 2.45mg/l 09:50hrs: Effluent Free Cl2 grab residual: 2.55mg/l FCL Analyzer: 2.45mg/l Effluent Total Cl2 grab residual: 2.72mg/l Adjusted Influent Cl17 Analyzer from 2.45mg/l to 2.55mg/l based on multiple Cl2 grab residuals. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Stouffville Well 3 | EAST | On site for station check and to collect weekly micro samples (W11568302). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.68mg/l FCL Analyzer: 2.66mg/l 09:35hrs: Effluent Free Cl2 grab residual: 2.64mg/l FCL Analyzer: 2.57mg/l Effluent Total Cl2 grab residual: 2.80mg/l Raw collected @ 09:35hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Stouffville Well 3 | EAST | On site for station check. Operational iron samples collected. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.84mg/l FCL Analyzer: 2.91mg/l 10:40hrs: Effluent Free Cl2 grab residual: 2.86mg/l FCL Analyzer: 2.78mg/l Effluent Total Cl2 grab residual: 3.10mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-05 | Stouffville Well 3 | EAST | On site with Travis Wyatt to change CL2 Cylinder. | FLAG | stage2_low_confidence | 0.0098155 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098155 | 0 | 0
2026-02 | 2026-02-06 | Stouffville Well 3 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.60mg/l FCL Analyzer: 2.60mg/l 11:00hrs: Effluent Free Cl2 grab residual: 2.58mg/l FCL Analyzer: 2.52mg/l Effluent Total Cl2 grab residual: 2.84mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-25 | Stouffville Well 1 & 2 | EAST | On site for station check and to collect weekly micro samples (W11620016). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.42mg/l FCL Analyzer: 3.48mg/l 08:45hrs: Effluent Free Cl2 grab residual: 1.98mg/l FCL Analyzer: 1.92mg/l Effluent Total Cl2 grab residual: 2.66mg/l Well 1 Raw collected @ 08:45hrs. Well 2 Raw collected @ 09:17hrs. Switched Well duties: W1 to D2, W2 to D1. Isolated Hypo Tank #2 to drawdown Hypo Tank #1 for replacement due to leak midway up the tank. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; leak [infrastructure] | out of service [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-26 | Stouffville Well 1 & 2 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.40mg/l FCL Analyzer: 3.44mg/l 12:45hrs: Effluent Free Cl2 grab residual: 1.88mg/l FCL Analyzer: 1.93mg/l Effluent Total Cl2 grab residual: 2.54mg/l Hypo Pump Diaphragms swapped out in both pumps. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-23 | Stouffville Well 1 & 2 | EAST | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.42mg/l FCL Analyzer: 3.48mg/l 12:15hrs: Effluent Free Cl2 grab residual: 1.95mg/l FCL Analyzer: 1.91mg/l Effluent Total Cl2 grab residual: 2.44mg/l Silicate system maintenance. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Stouffville Well 1 & 2 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.50mg/l FCL Analyzer: 3.60mg/l 09:15hrs: Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.88mg/l Effluent Total Cl2 grab residual: 2.34mg/l Switched Duties on Well Pumps: W1 to D2, W2 to D1. Collected raw PH values: 09:30hrs: Well 1: 7.97 09:45hrs: Well 2: 8.00 Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-18 | Stouffville Well 1 & 2 | EAST | On site receiving Silicate delivery. Bulk Tank start: 50.33cm, Bulk tank finish: 96.35cm. | FLAG | stage2_low_confidence | 0.011866 | ML: above threshold (no LLM available) — 0.012 |  | 0.011866 | 0 | 0
2026-02 | 2026-02-18 | Stouffville Well 1 & 2 | EAST | Received 1000L hypo. 200L to BL12. | FLAG | stage2_low_confidence | 0.0098031 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098031 | 0 | 0
2026-02 | 2026-02-13 | Stouffville Well 1 & 2 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.62mg/l FCL Analyzer: 3.55mg/l 09:15hrs: Effluent Free Cl2 grab residual: 1.96mg/l FCL Analyzer: 1.94mg/l Effluent Total Cl2 grab residual: 2.46mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | Stouffville Well 1 & 2 | EAST | On site for station check and to collect weekly micro samples (W11605521). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.72mg/l FCL Analyzer: 3.75mg/l 08:32hrs: Effluent Free Cl2 grab residual: 1.74mg/l FCL Analyzer: 1.70mg/l Effluent Total Cl2 grab residual: 2.26mg/l Well 1 Raw collected @ 09:30hrs. Well2 Raw collected @ 08:35hrs. Ran Well #1 in manual to collect raw sample and to also investigate erratic flow issues noticed by ROC. Did not notice any flow fluctuations, however, as recommended by Team Lead Dan Z, we will increase the flow rates to both wells from 23L/S to 27 L/S. Placed Well #1 into Duty 1 and Well #2 to Duty #2. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-10 | Stouffville Well 1 & 2 | EAST | On site for monthly maintenance: 09:15hrs: Cleaned HACH CL17 Analyzer, Verified Analyzer after cleaning @09:55hrs: Influent FCL grab residual: 1.89mg/l, Analyzer: 1.86mg/l Effluent FCL grab residual: 1.64mg/l. Analyzer: 1.61mg/l. Received 1250L of Hypo from Glen Chemicals. Conducted Generator Test Run (10:00hrs): Diesel Generator Run Monthly Test: Start Runtime: 10:00hrs (Run hrs: 661.4) Fuel Start: 978L Stop Runtime: 11:15hrs (Run hrs: 662.7) Fuel Stop: 964L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 60amps Volts: 595 Hertz: 61 RPM: 1750 Oil Pressure: 25psi Water temp: 150F Oil temp: 180F No issues during generator run test. Ran Well 2 during run test. Turbidimeter maintenance and calibration completed. Conducted chemical system inspection including injection points. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013321 | 0 | 0
2026-02 | 2026-02-20 | Stouffville Well 1 & 2 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.42mg/l FCL Analyzer: 3.52mg/l 11:05hrs: Effluent Free Cl2 grab residual: 1.97mg/l FCL Analyzer: 2.00mg/l Effluent Total Cl2 grab residual: 2.64mg/l Changed influent and effluent CL17 Analyzers Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-11 | Stouffville Well 1 & 2 | EAST | On site for station check and to collect weekly micro samples (W11588680). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.40mg/l FCL Analyzer: 3.35mg/l 10:45hrs: Effluent Free Cl2 grab residual: 1.97mg/l FCL Analyzer: 1.92mg/l Effluent Total Cl2 grab residual: 2.42mg/l Well 1 Raw collected @ 11:13hrs. Well2 Raw collected @ 10:45hrs. Switched Pump duties: W1 to D1, W2 to D2. Silicate dose slightly low, checked Silicate Calibration columns, dosing close to what it should be. Made slight adjustment to Silicate P1, Max Flow from 88 to 95ml/min. Will monitor dosage on next station check. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Stouffville Well 1 & 2 | EAST | On site for station check. Operational iron samples collected. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.60mg/l FCL Analyzer: 3.55mg/l 09:55hrs: Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 2.18mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-11 | Stouffville Well 1 & 2 | EAST | Changed well 2 percentage decline hi alarm set point from 30% to 35%, as requested by Tanya K. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006287 | 0 | 0
2026-02 | 2026-02-06 | Stouffville Well 1 & 2 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.42mg/l FCL Analyzer: 3.49mg/l 12:45hrs: Effluent Free Cl2 grab residual: 2.03mg/l FCL Analyzer: 2.07mg/l Effluent Total Cl2 grab residual: 2.84mg/l Conducted JHSC Inspection and Housekeeping. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Stouffville Well 1 & 2 | EAST | On site for station check and to collect weekly micro samples (W11568302). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.96mg/l FCL Analyzer: 3.93mg/l 08:40hrs: Effluent Free Cl2 grab residual: 2.46mg/l FCL Analyzer: 2.46mg/l Effluent Total Cl2 grab residual: 3.26mg/l Well 1 Raw collected @ 08:40hrs. Well2 Raw collected @ 08:40hrs. Inspected Hypo Pumps and Hypo chemical board. No issues. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-27 | Ballantrae Well 1 & 2 | EAST | On site to accept diesel fuel delivery Start: 64cm/626L Stop: 100.7cm/1007L No issues with delivery on site. | FLAG | stage2_low_confidence | 0.0074323 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074323 | 0 | 0
2026-02 | 2026-02-25 | Ballantrae Well 1 & 2 | EAST | On site to check station and equipment, as well as collect samples. Well 1 is running in duty 1. 08:33 Collected well1 raw. YD W11619922. 08:38 grab chlorine residual on treated sample: FCL = 1.85 mg/l, Total = 2.09 m/g. Effluent Analyzer free = 1.88 mg/l. 08:38 Collected treated sample. 08:41 influent grab free = 1.98 mg/l, analyzer free = 1.99 mg/l. 08:43 switched duty 1 well to Well 2. Rotated hypo pump duty at the same time. 09:03 collected well 2 raw. Station readings are entered in PWQ sheet. Reviewed trends, station is under normal operation. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058712 | 0 | 0
2026-02 | 2026-02-24 | Ballantrae Well 1 & 2 | EAST | On site to receive hypo delivery | FLAG | stage2_low_confidence | 0.011991 | ML: above threshold (no LLM available) — 0.012 |  | 0.011991 | 0 | 0
2026-02 | 2026-02-26 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Time: 11:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.74 Time: 11:52 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.74 1.70 Total: 1.80 Verified analyzers with grabs all ok. Checked station and trends. No outstanding alarms on site. No OOS equipment. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0055704 | 0 | 0
2026-02 | 2026-02-23 | Ballantrae Well 1 & 2 | EAST | On site for station check, and operational sampling (W11614421). Duty active, Tower level 80%. Entered data into PWQ sheets. Verified analyzers: Inffluent taken at 14:08 Free Grab: 1.99 mg/L Analyzer: 1.97 mg/L Effluent taken at 14:10 Free grab: 1.96 mg/L Analyzer: 1.90 mg/L Total grab: 2.38 mg/L Took operational sample at 14:17 Chemical systems: Hypo pump 1 running at 22% speed, DP=780 kpa Silicate pump 1 running at 43% speed, DP= 760 kpa. Reviewed SCADA trends, Station OK. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0043489 | 0 | 0
2026-02 | 2026-02-02 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Recording raw water PH monitoring. Time: 10:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.04 2.00 Time: 10:13 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.78 1.72 Total: 2.01 Verified analyzers with grabs all ok. Raw water PH 8.04. Entered data into PWQ sheet. Checked station and trends. No OOS equipment. No outstanding alarms on site. At 10:25 put BLW3 to manual to sample raw water PH. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0050726 | 0 | 0
2026-02 | 2026-02-11 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11588586 Weekly Bac-t Samples. Time: 09:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.98 2.01 Time: 09:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.61 1.69 Total: 1.72 Entered data into PWQ sheet. Verified analyzers with grabs. Between 10:00 and 10:35 shut down well 1 ran well 2, then shut down well 2 and put well 1 in auto and everything back to normal. Checked station and trends. No OOS equipment. No outstanding alarms. | FLAG | stage2_low_confidence | 0.0074448 | ML: above threshold (no LLM available) — 0.007 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0074448 | 0 | 0
2026-02 | 2026-02-18 | Ballantrae Well 1 & 2 | EAST | 7:42am Man/Start well 1 for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043393 | 0 | 0
2026-02 | 2026-02-10 | Ballantrae Well 1 & 2 | EAST | Check hose bib for leaks Install new hose bib old one leaking badly Needs a new garden hose will notify operator | FLAG | stage2_low_confidence | 0.019926 | ML: above threshold (no LLM available) — 0.02 | leak [infrastructure]; leaking [infrastructure] | 0.019926 | 0 | 0
2026-02 | 2026-02-17 | Ballantrae Well 1 & 2 | EAST | Placed well 1&2 man/off for planned shut down. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045221 | 0 | 0
2026-02 | 2026-02-17 | Ballantrae Well 1 & 2 | EAST | -on site to assist with power down of station transferred pac panel to the portable unit and turned generator off called roc (0830) to warn them of the alarms that would be generated. Once electrical contractor and hydro reconnected we confirmed rotation and voltage at the breaker. Closed station back to utility and cleared alarms (1715). Retuned pac panel to normal power. Called roc to activate duty and confirmed that pump was running. Under direction of oic. | FLAG | stage2_low_confidence | 0.068141 | ML: above threshold (no LLM available) — 0.068 | alarm [control_system]; alarms [control_system] | 0.068141 | 0 | 0
2026-02 | 2026-02-20 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Time: 09:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.55 Time: 09:27 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.49 Total: 1.76 Verified analyzers with grabs all ok. Checked station and trends. No outstanding alarms on site. No OOS equipment. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0055704 | 0 | 0
2026-02 | 2026-02-18 | Ballantrae Well 1 & 2 | EAST | On site to complete following work orders: W11590524 Hypo System Maintenance W11590555 CL-17 Analyzer Maintenance W11590585 Diesel Generator Test Run W11590632 CL-17 Analyzer Maintenance W11590719 NTU Maintenance W11592847 Silicate System Inspection W11592871 Dechlorination Puck Dispenser Inspection On site to help with hypo delivery. Start: 275L Stop: 425L Well 1 and 2 put in manual at 10:02. Started generator at 12:46. Attached to this entry will be the generator stats. Any changes in trends or alarms created re due to work orders being completed. After analyzer cleaning verifying analyzers with grabs. Time: 14:00 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.04 2.00 Time: 14:02 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.03 1.98 After verifying analyzers no issues calibration on pocket colorimetre passed with standard viles. I issues with work orders. | FLAG | stage2_low_confidence | 0.0093008 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.0093008 | 0 | 0
2026-02 | 2026-02-10 | Ballantrae Well 1 & 2 | EAST | On site to complete hypo top up from Glen Chemicals certificate of analysis is attached to log entry. Start: 56.44 Stop: 80.76 No issues with top up. | FLAG | stage2_low_confidence | 0.009092 | ML: above threshold (no LLM available) — 0.009 |  | 0.009092 | 0 | 0
2026-02 | 2026-02-13 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Time: 10:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.91 1.95 Time: 10:12 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.83 1.69-1.83 Total: 2.01 Verified analyzers with grabs. Adjusted the effluent free after multiple grabs were taken from a 1.69mg/l to a 1.83mg/l at 10:15. Replaced reagents in both the influent and effluent free CL-17 analyzers. Checked site and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ. | FLAG | stage2_low_confidence | 0.0092646 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0092646 | 0 | 0
2026-02 | 2026-02-18 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11638986 Weekly Bac-t Samples. Time: 08:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.17 2.26 Time: 08:13 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.80 Total: 1.80 Verified analyzers with grabs all ok. Stopped well 1 at 08:16. Started well 2 at 08:17. No outstanding alarms on site. No OOS equipment. At 08:52 shut down well 2 and put it to auto. At 08:53 put well 1 back to auto duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0054894 | 0 | 0
2026-02 | 2026-02-17 | Ballantrae Well 1 & 2 | EAST | -on site to address Vfd fault. Found unit in overcurrent alarm. Reset the Vfd on the keypad and cleared alarms on scada. Motor started and currently monitoring to confirm operation. Well has been running for 15 minutes no issues current output of drive all within spec. Called Patrick F to let him know what happened. Under direction of oic. | FLAG | stage2_low_confidence | 0.04556 | ML: above threshold (no LLM available) — 0.046 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.04556 | 0 | 0
2026-02 | 2026-02-04 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11568186 Weekly Bac-t Samples. Time: 11:38 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.00 2.04 Time: 11:41 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.72 1.64 Total: 1.93 Verified analyzers with grabs. Checked station and trends. Stopped well 1 at 11:45 and started well 2 in manual at 11:46. Stopped well 2 at 12:10 and put all wells back to auto and restarted well 1 at 12:11. No outstanding alarms on site. No OOS equipment. | FLAG | stage2_low_confidence | 0.0089477 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0089477 | 0 | 0
2026-02 | 2026-02-03 | Ballantrae Well 1 & 2 | EAST | On site to place both wells local off for electrical shutdown today. Contractors conducting electrical upgrades to facility and will require electricity to be shutdown until 3pm. Generator will be offline and unavailable during this time. ROC notified of shutdown. Hypo delivery received 200L. | FLAG | stage2_low_confidence | 0.014338 | ML: above threshold (no LLM available) — 0.014 |  | 0.014338 | 0 | 0
2026-02 | 2026-02-09 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Time: 13:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.87 1.87 Time: 13:17 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.85 1.77 Total: 2.09 Verified analyzers with grabs. Checked station and trends. Entered data into PWQ sheets. No outstanding alarms on site. No OOS equipment. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0051488 | 0 | 0
2026-02 | 2026-02-06 | Ballantrae Well 1 & 2 | EAST | On site to complete station check. Time: 09:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.80 1.84 Time: 09:23 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.66 Total: 1.87 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0054651 | 0 | 0
2026-02 | 2026-02-03 | Ballantrae Well 1 & 2 | EAST | -on site to assist with site shut down 0930 got pac ups on the temp gen contractor brought. We confirmed power was disconnected and contractor completed work. We returned power at 1320 and confirmed no issues. PAC returned to normal power and placed pumps back to auto. Under direction of oic. | FLAG | stage2_low_confidence | 0.025553 | ML: above threshold (no LLM available) — 0.026 |  | 0.025553 | 0 | 0
2026-02 | 2026-02-26 | Ballantrae Well 3 | EAST | On site to verify silicate pump 1 operation. Placed it in duty 1 and enabled silicate pump duty rotation. Enable chlorine system duty rotation. Activated well duty. System is running normally. Equipment OOS: silicate bulk tank. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-23 | Ballantrae Well 3 | EAST | WRONG BOOK MTW3 On site to correct source of chlorine gas leak with Jack P. Cylinders already isolated, turned booster pump 2 local on to purge chlorine lines. Replaced parker fitting on outlet of the regulator on left bank cylinder. Opened chlorine cylinders and vacuum tested system for leaks. Backwashed station for a few mins, with de-chlor pucks in the catch basin. Placed chlorine system back in service and placed well back in service. Monitoring well start up. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; oos [equipment_failure]; leak [infrastructure] | gas leak [critical]; oos [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-26 | Ballantrae Well 3 | EAST | On site to complete station check. Time: 11:03 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.69 1.63 Time: 11:05 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.74 Total: 1.83 Verified analyzers with grabs. No outstanding alarms on site. Silicate level is 140cm. No OOS equipment. Checked site and trends. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.004957 | 0 | 0
2026-02 | 2026-02-23 | Ballantrae Well 3 | EAST | On site for station check, and operational sampling (W11614421). Activated system duty, Tower level 73%. Entered data into PWQ sheets. Verified analyzers: Inffluent taken at 13:10 Free Grab: 2.46 mg/L Analyzer: 2.38 mg/L Effluent taken at 13:12 Free grab: 1.56 mg/L Analyzer: 1.65 mg/L Total grab: 1.89 mg/L Took operational sample at 13:19 Chemical systems: Chlorinator 2 open at 56%, BP2 running DP=1450 kpa Silicate pump 2 running at 22% speed, DP= 680 kpa. Noticed silicate pump 1 was air locked, rotated to pump 2 and deactivated duty rotation and SCADA. Was unable to correct pump 1 while on site. Reviewed SCADA trends, Station OK. | FLAG | stage2_low_confidence | 0.0075832 | ML: above threshold (no LLM available) — 0.008 | scada [control_system] | 0.0075832 | 0 | 0
2026-02 | 2026-02-26 | Ballantrae Well 3 | EAST | Check leaking backflow preventer Replaced 1st check disc debris on disc cleaned and retested Passed | FLAG | stage2_low_confidence | 0.014473 | ML: above threshold (no LLM available) — 0.014 | leak [infrastructure]; leaking [infrastructure] | 0.014473 | 0 | 0
2026-02 | 2026-02-25 | Ballantrae Well 3 | EAST | On site to check station and equipment, as well as collect samples. Well 3 is running in duty 1. 09:25 Collected well 3 raw. YD W11619922. 09:30 grab chlorine residual on treated sample: FCL = 1.69 mg/l, Total = 2.01 m/g. Effluent Analyzer free = 1.71 mg/l. 09:30 Collected treated sample. 09:33 influent grab free = 2.07 mg/l, analyzer free = 2.18 mg/l. 09:36 standardized influent analyzer reading according to 3 grabs? average. 09:43 Switched chlorine duty to run #1 Chlorinator #1 is dosing at 28 ppd, which is the same of #2. #1 vacuum is at -100mbar. Chlorine booster pump 1 discharge pressure is 205 psi, which is similar to #2?s discharge pressure of 210 psi. No noticeable issue with chlorine #1. Leaving chlorine #1 running in lead duty. Trouble shoot silicate pump 1 issue. Foot valve needs cleaning. Will return to site to perform more testing on silicate pump 1 system. It is OOS for now. Station readings are entered in PWQ sheet. Reviewed trends, station is under normal operation. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Ballantrae Well 3 | EAST | On site to complete station check. Collecting raw water PH samples. Time: 11:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.05 2.11 Time: 11:18 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.40 Total: 1.61 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. Chlorinator 1 OOS due to issues with dosing will troubleshoot tomorrow. Raw water PH is 8.13. At 11:26 put well 3 into auto which shut down the well. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | Ballantrae Well 3 | EAST | Disabled well 3 percent decline master alarm. It is not setup by Water Resources yet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0050214 | 0 | 0
2026-02 | 2026-02-10 | Ballantrae Well 3 | EAST | Silicate top up: Before: 120L After: 200L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070212 | 0 | 0
2026-02 | 2026-02-10 | Ballantrae Well 3 | EAST | Update software/PAC/SCADA with new updates for contract. Dan onsite for the duration of the update. Well was OFF for the complete update time period. Started Well, commissioned new software, confirmed data capture as required. All work for preparation of contract development occurring. | FLAG | stage2_low_confidence | 0.043791 | ML: above threshold (no LLM available) — 0.044 | scada [control_system] | 0.043791 | 0 | 0
2026-02 | 2026-02-12 | Ballantrae Well 3 | EAST | Switched chlorinator 2 to chlorinator 1 to see if the chlorinator causes any issues. Will monitor remotely. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060287 | 0 | 0
2026-02 | 2026-02-11 | Ballantrae Well 3 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11588586 Weekly Bac-t Samples. Time: 11:00 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.12 2.21 Time: 11:03 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.55 Total: 1.69 Verified analyzers with grabs. Entered data into PWQ sheet. No OOS equipment on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.0043648 | 0 | 0
2026-02 | 2026-02-12 | Ballantrae Well 3 | EAST | On site to complete following work orders: W11600561 Cl2 Emergency Repair Kit Inspection. W11600571 Low Temperature Alarm Test W11600582 Exhaust Fan Check W11600588 Supply Fan 1 Check W11600594 Chlorine Leak Detector Test W11600612 Chlorine Scrubber Check W11600622 Diesel Generator Test W11592057 Housekeeping Attached to this entry is the information for the generator test. At 09:46 informed ROC of work orders to be completed. At 09:46 put well 3 in manual and shut it down. No issues with generator run while generator was running on load. Any changes in trends are due to work orders being completed, any alarms created are also due to work orders being done. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | emergency [critical]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-10 | Ballantrae Well 3 | EAST | On site to complete the following work orders: W11600663 Well Pump Oil Drip System Inspection. W11600668 Chlorine Analzyer Maintenance W11602115 JHSC Inspection W11602138 NTU Calibration and Maintenance W11602493 Dechlorination Puck Dsicpenser Inspection W11602606 Chemical System Inspection Silicate W11602630 Chemical System Inspection Chlorine. Informed ROC of work to be completed at 10:24. Leaving site to top up BLW1/2 with hypo delivery. Back on site to continue completing work orders. Testing chlorintor 1 and troubleshooting to see if we get any lolo influent. Going to start generator shutting well 3 off at 13:15. Will not be running generator today will finish this work order later this week. Time: 14:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.5. 1.55 Time: 14:26 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.07 2.09 Verified analyzers with grabs no issues. No issues with work orders. Any changes in trends or alarms created are due to work orders being completed. | FLAG | stage2_low_confidence | 0.030997 | ML: above threshold (no LLM available) — 0.031 | work order [maintenance_action]; alarm [control_system]; alarms [control_system]; drip [infrastructure] | 0.030997 | 0 | 0
2026-02 | 2026-02-13 | Ballantrae Well 3 | EAST | On site to complete station check. Time: 09:33 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.20 2.28 Time: 09:35 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.63 Total: 1.86 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.005248 | 0 | 0
2026-02 | 2026-02-20 | Ballantrae Well 3 | EAST | On site to complete station check. Time: 09:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.49 Time: 09:42 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.32 Total: 1.49 Verified analyzers with grabs all ok. Chlorinator 1 is still off for the weekend due to issues on start up and shut down. No outstanding alarms on site. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0032961 | 0 | 0
2026-02 | 2026-02-17 | Ballantrae Well 3 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11605419 Weekly Bac-t Samples. Time: 10:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.10 2.18 Time: 10:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.58 1.56 Total: 1.70 Verified analyzers with grabs all ok. Checked site and trends. Percent decline alarm acknowledged not Abel to reset. Lowered flow from 30l/s to 25l/s and switched to chlorinator 1 to test and see if there is any issue with influent free. Entered data into PWQ sheet. Put flow back to 30l/s to see if there is a change will monitor off site. Shut well 3 off due to sample being collected and more troubleshooting needing to be done. Put chlorinator 1 in manual off. | FLAG | stage2_low_confidence | 0.009056 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.009056 | 0 | 0
2026-02 | 2026-02-11 | Ballantrae Well 3 | EAST | Silicate bulk tank (SILC_TK1_LIT1) is reading 55cm. Confirmed with on site consultant (Adil M.), it is coming from contractors' activity. There is no chemical/liquid in side the tank. Ask consultant to submit request to power off the LIT until the bulk tank is in placed in service. Disregards the LIT reading until then. | FLAG | stage2_low_confidence | 0.0073926 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073926 | 0 | 0
2026-02 | 2026-02-10 | Ballantrae Well 3 | EAST | On site with Kyle C to test new software. Tested AIT1, AIT2, PIT1 interlocks and alarms. Tested silicate pump operation in manual. 11:37 ? 11:54 Man/start well 3. 12:04 ? 12:24 Run Well 3 in auto. 12:30 ? 13:36 Run well 3 in auto. 14:00 ? 15:03 Man/Start well 3 a few times to test and start/stop sequence. New software commissioning is complete. Disabled Master Alarms on silicate day tank LIT, silicate bulk tank LIT as they are not commissioned. Well 4 is visible on SCADA, however, it is not commissioned. Well 3 is back to auto duty standby. Silicate system is drawing from the temporary day tank. | FLAG | stage2_low_confidence | 0.0090808 | ML: above threshold (no LLM available) — 0.009 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0090808 | 0 | 0
2026-02 | 2026-02-15 | Ballantrae Well 3 | EAST | On site responding to Influent Chlorine Lolo lockout that occurred overnight @03:42 CMU5 #W11664802 Arrived on site @11:35 and analyzer is reading 0.05 mg/L. Verified analyzer reading with grab residual 0.07 mg/L Connected 2 lengths of discharge hosing to the waste man hole at back of building. Started backflushing @11:50. Added dechlorination pucks to chamber. Stopped backflushing @12:18. Disconnected backflushing hose. Influent residual is 1.25 mg/L Tested chlorinator #1 while backflushing. Did not observe any issues while running it. Will leave OOS for remainder on weekend, but is available if needed. Started well #3 in manual @12:30, with chlorinator #2 in D1. Well is running okay, no issues with chlorine dosing. Also investigated the well #3 percent decline Lolo alarms tat have been coming in. Observed that after an hour of well #3 running the value for well performance spikes above 100%. Will inform Team lead/supervisor next week. Station ok, no further issues on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-04 | Ballantrae Well 3 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11568200 Weekly Bac-t Samples. W11569414 Monthly Manganese Samples. Time: 13:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.98 2.01 Time: 13:53 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.48 Total: 1.59 Activated duty at 13:03 to sample wells 1 and 2. Checked site and trends. Verified analyzers with grabs. Well 1 OOS for WQ issues. Diesel tank level hi alarm disregard. Stopped well 1. All flow from this well went to waste and not to system. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-09 | Ballantrae Well 3 | EAST | Activate duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051483 | 0 | 0
2026-02 | 2026-02-06 | Ballantrae Well 3 | EAST | On site to complete station check. Time: 10:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.52 Time: 10:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.53 Total: 1.70 Entered data into PWQ sheet. Verified analyzers on site. Checked site and trends. No outstanding alarms on site. Chlorinator 1 still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-09 | Ballantrae Well 3 | EAST | On site with Kyle C to test new software. Man/Stop well 3 and placed W3 to local off. Informed ROC. Well 3 is to remain OOS and Local OFF for the night. Informed ROC and team. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Ballantrae Well 3 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11568186 Weekly Bac-t Samples. Time: 12:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.07 2.12 Time: 12:33 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.49 1.48 Total: 1.70 Verified analyzers with grabs all ok. Checked site and trends. Chlorinator 1 still OOS. No outstanding alarms on site. Entered info into PWQ sheet. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-04 | Ballantrae Well 3 | EAST | Scratch last entry it was meant for MTW1/2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045078 | 0 | 0
2026-02 | 2026-02-25 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and to collect weekly micro samples (W11620016). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.97mg/l FCL Analyzer: 1.98mg/l 12:35hrs: High Lift Effluent Free Cl2 grab residual: 1.79mg/l FCL Analyzer: 1.83mg/l Effluent Total Cl2 grab residual: 1.97mg/l Well 5 collected @ 12:20hrs. Well 6 collected @ 12:17hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-23 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.87mg/l FCL Analyzer: 1.90mg/l 09:05hrs: High Lift Effluent Free Cl2 grab residual: 1.77mg/l FCL Analyzer: 1.76mg/l Effluent Total Cl2 grab residual: 1.96mg/l Changed Influent Discharge from West Cell to East Cell and Sample pumps. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-26 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.93mg/l FCL Analyzer: 1.94mg/l 09:05hrs: High Lift Effluent Free Cl2 grab residual: 1.87mg/l FCL Analyzer: 1.79mg/l Effluent Total Cl2 grab residual: 1.97mg/l Tested Cl2 leak alarm. No issues. Switched High Lift Pump duties: P1 to D1, P2 to D2. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; alarm [control_system]; leak [infrastructure] | out of service [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-17 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and to collect weekly micro samples (W11605521). Well 5 collected @ 12:20hrs. Well 6 collected @ 12:15hrs. Had to leave site to respond to low CL2 at Bethesda Tower. | FLAG | stage2_low_confidence | 0.0080355 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080355 | 0 | 0
2026-02 | 2026-02-18 | Stouffville Reservoir and Wells 5 & 6 | EAST | Conducted monthly maintenance: 12:20hrs: Cleaned Influent HACH CL17 Analyzer, Verified Analyzers after cleaning @12:45hrs: Influent FCL grab residual: 1.76mg/l, Analyzer: 1.65mg/l Adjusted CL2 Analyzer from 1.65mg/l to 1.76mg/l based on multiple Cl2 grab residuals. Chlorine Cylinder repair kit inspection. Chlorine Scrubber inspection | FLAG | stage2_low_confidence | 0.016181 | ML: above threshold (no LLM available) — 0.016 | repair [maintenance_action] | 0.016181 | 0 | 0
2026-02 | 2026-02-17 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and to collect weekly micro samples (W11605521). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.97mg/l FCL Analyzer: 1.98mg/l 13:30hrs: High Lift Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 1.91mg/l Well 5 collected @ 12:20hrs. Well 6 collected @ 12:15hrs. Switched reservoir influent cell from EAST to WEST and sample pump suction line. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-10 | Stouffville Reservoir and Wells 5 & 6 | EAST | Repair leak high lift pump 2 Back in auto | FLAG | stage2_low_confidence | 0.024906 | ML: above threshold (no LLM available) — 0.025 | repair [maintenance_action]; leak [infrastructure] | 0.024906 | 0 | 0
2026-02 | 2026-02-13 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.90mg/l FCL Analyzer: 1.94mg/l 08:15hrs: High Lift Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 1.95mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-20 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check. Travis Wyatt on site for Chlorine Cylinder change. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.78mg/l FCL Analyzer: 1.80mg/l 09:45hrs: High Lift Effluent Free Cl2 grab residual: 1.77mg/l FCL Analyzer: 1.75mg/l Effluent Total Cl2 grab residual: 1.87mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-11 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and to collect weekly micro samples (W11588680). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.00mg/l FCL Analyzer: 2.04mg/l 08:45hrs: High Lift Effluent Free Cl2 grab residual: 1.85mg/l FCL Analyzer: 1.84mg/l Effluent Total Cl2 grab residual: 1.99mg/l Well 5 collected @ 08:30hrs. Well 6 collected @ 08:25hrs. Switched duties on High lift Pumps: P1 to D2, P2 to D1. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-06 | Stouffville Reservoir and Wells 5 & 6 | EAST | Acknowledged and reset a High Lift P1 failed to stop alarm on Duty Stop. On Scada, pump had actually stopped but may have took longer than normal to stop when the command was given. Will need to investigate further as to why pump is stopping slightly longer than it should. | FLAG | stage2_low_confidence | 0.027357 | ML: above threshold (no LLM available) — 0.027 | failed [equipment_failure]; scada [control_system]; alarm [control_system] | 0.027357 | 0 | 0
2026-02 | 2026-02-19 | Stouffville Reservoir and Wells 5 & 6 | EAST | Conducted monthly maintenance: 09:35hrs: Cleaned HACH CL17 High Lift Effluent Analyzer, Verified Analyzers after cleaning @09:50hrs: Effluent FCL grab residual: 1.77mg/l. Analyzer: 1.75mg/l. Changed Effluent HACH Cl17 Analyzer reagents. Changed Influent HACH Cl17 Analyzer reagents. Conducted Generator Test Run (09:24hrs): Diesel Generator Run Monthly Test: Start Runtime: 09:24hrs (Run hrs: 14.25hrs) Fuel Start: 3107L Stop Runtime: 10:30hrs (Run hrs: 15.35hrs ) Fuel Stop: 3091L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 50amps Volts: 596 Hertz: 61 RPM: 1800 Oil Pressure: 37psi Water temp: 170F No issues during generator run test. Ran HLP2 during run test. Turbidimeter maintenance and calibration completed. Conducted chemical system inspection. Housekeeping. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013986 | 0 | 0
2026-02 | 2026-02-09 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.88mg/l FCL Analyzer: 1.89mg/l 12:30hrs: High Lift Effluent Free Cl2 grab residual: 1.83mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 1.95mg/l Changed Reservoir inlet from West to East and Sampling pumps. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: High Lift P1 offline for flow control valve repair. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; repair [maintenance_action] | out of service [equipment_failure]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-06 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.79mg/l FCL Analyzer: 1.78mg/l 09:40hrs: High Lift Effluent Free Cl2 grab residual: 1.81mg/l FCL Analyzer: 1.81mg/l Effluent Total Cl2 grab residual: 1.95mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and to collect weekly micro samples (W11568302). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.03mg/l FCL Analyzer: 2.10mg/l 12:50hrs: High Lift Effluent Free Cl2 grab residual: 1.91mg/l FCL Analyzer: 1.92mg/l Effluent Total Cl2 grab residual: 2.04mg/l Well 5 collected @ 12:26hrs. Well 6 collected @ 12:18hrs. Adjusted Target influent from 2.10mg/l to 2.00mg/l. Changed Influent feed from East to West and Sampling Pump feed. Collected RAW Water PH @12:57hrs: Well 5: 7.45 Well 6: 7.43 Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-05 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for Cl2 Cylinder change with Travis Wyatt. | FLAG | stage2_low_confidence | 0.0098659 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098659 | 0 | 0
2026-02 | 2026-02-23 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check. 09:35hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.80mg/l Analyzer: 1.81mg/l TCL grab residual: 1.95mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: No | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-26 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check. 10:10hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.70mg/l Analyzer: 1.69mg/l TCL grab residual: 1.85mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-19 | Stouffville Highway 48 Booster Pumping Station | EAST | Conducted monthly maintenance: 13:40hrs: Cleaned HACH CL17 Analyzer, Verified Analyzers after cleaning @13:50hrs: FCL grab residual: 1.70mg/l. Analyzer: 1.73mg/l. JHSC conducted on site. | FLAG | stage2_low_confidence | 0.0089256 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089256 | 0 | 0
2026-02 | 2026-02-20 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check. 10:30hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.70mg/l Analyzer: 1.69mg/l TCL grab residual: 1.87mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-13 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check. 08:35hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.74mg/l Analyzer: 1.71mg/l TCL grab residual: 1.88mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check. 14:00hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.53mg/l Analyzer: 1.57mg/l TCL grab residual: 1.65mg/l Changed HACH CL17 Analyzer reagents. Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check. 13:30hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.59mg/l Analyzer: 1.62mg/l TCL grab residual: 1.72mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-06 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check. 10:20hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.79mg/l Analyzer: 1.77mg/l TCL grab residual: 1.91mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check. 13:05hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.82mg/l Analyzer: 1.82mg/l TCL grab residual: 1.90mg/l Ran air compressor to regulate pressure tank levels. Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure] | sso [critical]; out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-13 | King City Wells 3 & 4 | WEST | On site for station check. Site offline. Doors locked. | FLAG | stage2_low_confidence | 0.0091396 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091396 | 0 | 0
2026-02 | 2026-02-20 | King City Wells 3 & 4 | WEST | On site for station check. Site offline. Doors locked. | FLAG | stage2_low_confidence | 0.0091396 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091396 | 0 | 0
2026-02 | 2026-02-06 | King City Wells 3 & 4 | WEST | On site for station check. Site offline. Doors locked. W11574343- JHSC inspection complete. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.007219 | 0 | 0
2026-02 | 2026-02-25 | Kleinburg Wells 3 and 4 | WEST | On site for station check and micro sampling W11620283 Check Trends- All okay Ran Well 3 and 4 in local 11:20-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.01 mg/L, Analyzer - 0.01 mg/L Total Cl2 Grab- 1.85 mg/L, Analyzer - 1.89 mg/L 11:16-Verified Effluent Free Analyzer Free cl2 Grab- 0.04 mg/L, Analyzer - 0.04 mg/L 11:16-Verified Influent Free Analyzer Free cl2 Grab- 0.02 mg/L, Analyzer - 0.07 mg/L Topped up KI reagent. Entered Values in PWQ sheet Samples taken stopped wells Equipment oaky. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055579 | 0 | 0
2026-02 | 2026-02-17 | Kleinburg Wells 3 and 4 | WEST | On site for station check and micro sampling W11605699 Check Trends- All okay Ran Well 3 and 4 in local 13:44-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.01 mg/L Total Cl2 Grab- 1.96 mg/L, Analyzer - 1.98 mg/L 13:48-Verified Effluent Free Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.04 mg/L 13:48-Verified Influent Free Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.06 mg/L Topped up Acetate. Entered Values in PWQ sheet Samples taken stopped wells Equipment oaky. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054768 | 0 | 0
2026-02 | 2026-02-11 | Kleinburg Wells 3 and 4 | WEST | On site for station check and to collect bacti sample W11605699 ran wells to waste - distribution valve locked out. Checked residuals Total Analyzer 1.99mg/L Grab 1.95mg/L Free Analyzer 0.01mg/L Grab 0.03mg/L Reagents all okay Wells back offline after sampling No known issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047097 | 0 | 0
2026-02 | 2026-02-13 | Kleinburg Wells 3 and 4 | WEST | Ran well 3 and 4 locally to collect raw water resampling 11:30- collected samples | FLAG | stage2_low_confidence | 0.0084959 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084959 | 0 | 0
2026-02 | 2026-02-04 | Kleinburg Wells 3 and 4 | WEST | On site for station check and micro sampling W11568550 Check Trends- All okay Ran Well 3 and 4 in local 11:15-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.01 mg/L Total Cl2 Grab- 2.01 mg/L, Analyzer - 2.00 mg/L 13:58-Verified Effluent Free Analyzer Free cl2 Grab- 0.05 mg/L, Analyzer - 0.04 mg/L 10:55-Verified Inffluent Free Analyzer Free cl2 Grab- 0.04 mg/L, Analyzer - 0.06 mg/L Reagents All good Entered Values in PWQ sheet Samples taken stopped wells Equipment oaky. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054799 | 0 | 0
2026-02 | 2026-02-03 | Kleinburg Wells 3 and 4 | WEST | Onsite for the following PM Work orders. Informed ROC about the works being done. W11562248 KLW34, Diesel Generator Test Run Pre check Battery okay- 26.5V Coolant- Okay Oil - Okay Before Start Start time- 10:00 Run time- 416.1 hr Fuel level-1987L/38.5cm KLPSWL pump 4 running Local. After Stop Stop time- 11:14 Run time- 417.3 hr Fuel level-1953L/37.8 cm W11562437-Chlorine Analyzer, Maintenance 13:50-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.02 mg/L, Analyzer - 0.04 mg/L Total Cl2 Grab- 2.07 mg/L, Analyzer - 2.07 mg/L 13:53-Verified Effluent Free Analyzer Free cl2 Grab- 0.05 mg/L, Analyzer - 0.04 mg/L 13:55-Verified Inffluent Free Analyzer Free cl2 Grab- 0.02 mg/L, Analyzer - 0.06 mg/L W11562403-Turbidimeter Maintenance- Display not showing any options after vail cleaning and verification. Value still in hold output mode. CMU created-W11634370 W11562289-Pressure Relief Valve, Inspection W11563441- Ammonia System, Inspection W11563465-Deep Well Exhaust Valve, Maintenance W11563510- Chlorine Leak Detector, Test W11562826-JHSC Health and Safety Inspection W11564230-Chemical System Inspection - Chlorine W11564270- Chemical System Inspection - Silicate W11563405- Ventilation System - Exhaust Fans W11563325- Chlorine Scrubber, Check W11563395-Chlorine Cylinder Emergency Repair Kit Inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action]; repair [maintenance_action]; leak [infrastructure] | emergency [critical]; work order [maintenance_action]; repair [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-06 | Kleinburg Wells 3 and 4 | WEST | Attending site to check Turbidimeter screen issue (W11634370). Cycled power on transmitter and device rebooted normally. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.019621 | ML: above threshold (no LLM available) — 0.02 |  | 0.019621 | 0 | 0
2026-02 | 2026-02-23 | Schomberg Elevated Tank | WEST | Trends checked and ok, equipment checked and ok All measurement are in mg/l Tower draining Common inlet/outlet - time : 11:35 Free 0.05 Total grab 3.49 vs analyzer 3.52 Mono 2.90 Post injection - time : 11:42 Free 0.04 Total grab 4.08 vs analyzer 4.14 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0021085 | 0 | 0
2026-02 | 2026-02-27 | Schomberg Elevated Tank | WEST | Onsite for station check Tower filling Post inj @1106 Total analyzer 3.67 grab 3.72 Free grab 0.00 Deactivated duty Pre inj @1128 Total analyzer 3.54 grab 3.56 Free grab 0.04 Mcl grab 3.00 Topped up hypo tank | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00084614 | 0 | 0
2026-02 | 2026-02-02 | Schomberg Elevated Tank | WEST | Onsite for station check Tower draining Checked residuals mg/l Common @1047 Total grab 3.44 grab 3.36 Free grab 0.03 Post inj @1051 Total analyzer 3.25 grab 3.10 Free grab 0.06 Reagents ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00076256 | 0 | 0
2026-02 | 2026-02-10 | Schomberg Elevated Tank | WEST | Attending site to replace failed hypo pump#2 (W11497370). Replaced pump and corroded connection cables. Primed pump and adjusted valves so it is ready to run from SCADA, if needed. Operations were notified so that they can test the pump next time they are on site. A spare pump will be available from the inventory at 145 HWP. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.10908 | ML: above threshold (no LLM available) — 0.109 | failed [equipment_failure]; scada [control_system] | 0.10908 | 0 | 0
2026-02 | 2026-02-25 | Schomberg Elevated Tank | WEST | Equipment checked and ok, trends checked and ok Tower draining Common inlet time: 11:45 Free grab 0.04 Total grab 3.60 vs analyzer 3.62 Mono 2.94 Bact Sample grabbed time 12:16 Post injection time 12:10 Free grab 0.06 Total grab 4.28 vs analyzer 4.22 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0024908 | 0 | 0
2026-02 | 2026-02-20 | Schomberg Elevated Tank | WEST | Tower filling Trends checked and ok, equipment checked and ok All readings are in mg/l Common inlet/outlet -time 11:35 Free grab 0.08 Total grab 3.10 vs analyzer 3.16 Mono 2.74 Post injection- time: 11:50 Free grab 0.10 Total grab 3.81 vs analyzer 3.78 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0020982 | 0 | 0
2026-02 | 2026-02-17 | Schomberg Elevated Tank | WEST | Onsite for station check and to collect weekly micro W11605647 Tower filling Post inj @1136 Total analyzer 3.69 grab 3.60 Free grab 0.02 Deactivated duty Pre inj @1153 Total analyzer 3.54 grab 3.52 Free grab 0.03 Mcl grab 2.98 Changed reagents in post injection analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013902 | 0 | 0
2026-02 | 2026-02-13 | Schomberg Elevated Tank | WEST | Onsite for station check Tower draining Checked residuals mg/l Common / pre @0953 Total analyzer 3.54 grab 3.46 Free grab 0.09 Mcl grab 2.90 Post inj @1006 Total analyzer 4.33 grab 4.26 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010807 | 0 | 0
2026-02 | 2026-02-12 | Schomberg Elevated Tank | WEST | Onsite to complete work orders Cleaned cl17sc analyzers grabs before @1200 Post inj Total analyzer 3.38 grab 3.10 Free grab 0.04 @1206 Common Total analyzer 3.29 grab 3.02 Free grab 0.06 Completed monthly generator run Completed jhsc Change reagents in common cl17sc Closed common inlet to work in hypo injection point feed system through bypass, resulting in loss of flow to analyzer Compliance alarm came in @1407 Common Grab Total grab 3.26 Free grab 0.03 Opened valve back to normal operation @ 1418 Cleaned common inlet analyzer again @1423 High spike came in due to adjusting flow and maintenance Checked residuals mg/l @1454 Common Total analyzer 3.32 grab 3.28 Free grab 0.01 Started high lift to get flow to post inj Grabs @1516 Total analyzer 3.44 grab 3.30 Hypo pump 2 drawdown 150 ml/min Hypo pump 1 drawdown 140 ml/min Topped up hypo tank | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; work order [maintenance_action]; compliance [regulatory]; alarm [control_system] | bypass [critical]; work order [maintenance_action]; compliance [regulatory]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | Schomberg Elevated Tank | WEST | Onsite for station check and to collect weekly micro sample W11588872 Tower filling Checked residuals mg/l @1112 Post inj Total analyzer 3.60 grab 3.70 Free grab 0.06 Deactivated hl duty Common/ Pre inj @1128 Total analyzer 3.36 grab 3.28 Free grab 0.05 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012847 | 0 | 0
2026-02 | 2026-02-03 | Schomberg Elevated Tank | WEST | Attending site to check display on Hypo Tank Level (W11621184). Cycled power to display and it booted up normally. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.018977 | ML: above threshold (no LLM available) — 0.019 |  | 0.018977 | 0 | 0
2026-02 | 2026-02-09 | Schomberg Elevated Tank | WEST | Tower draining Equipment checked and ok, trends checked and ok Common inlet/ outlet Time 1:21 pm Free: grab 0.08 Total: grab 3.42 vs analyzer 3.44 Mono 2.93 Post injection Time 1:27 pm Free: grab 0.09 Total: grab 4.40 vs 4.50 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.001869 | 0 | 0
2026-02 | 2026-02-04 | Schomberg Elevated Tank | WEST | Onsite for station check and to collect weekly micro sample W11568498 Tower draining Checked residuals mg/l Common @1143 Total analyzer 3.51 grab 3.54 Free grab 0.06 Mcl grab 2.97 Post inj @ 1151 Total analyzer 4.31 grab 4.00 Free grab 0.13 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0014583 | 0 | 0
2026-02 | 2026-02-06 | Schomberg Elevated Tank | WEST | Tower draining Equipment inspected ok, trends ok Post injection free 0.09, total 3.03 vs analyzer 3.05 - 11:15 am Pre injection free 0.08, total 3.51 vs analyzer 3.46 Monochloramine 3.03 - 11:25 am | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057912 | 0 | 0
2026-02 | 2026-02-24 | Georgina Water Treatment Plant | EAST | ROC informed of train 3, 6 shut down. Backpulse flow lolo and pumps OOS. Reviewed SCADA, noticed the backpulse fill valves are man/off. Placed them to auto and Tank 2 valve is in duty 1. Ack+Reset alarms, initiated train 3 and train 6 backwash. Initiated rest of trains' backwashes to stagger recovery percentage. Changed the backwash tank fill rate from 65 l/s to 75 l/s. Enabled backup power selection for all types of cleans. Changed Train 1 and 2 permeate pumps' VFD speed from 65% to 60%. All trains are available and plant is under normal operation. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; backup [infrastructure] | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; backup [infrastructure] |  | 1 | 0
2026-02 | 2026-02-27 | Georgina Water Treatment Plant | EAST | On site to respond to High Lift CL2 free analyzer HIHI alarm. Was reading in excess of 3.20mg/l. Collected CL2 grab residual @ 14:25hrs: 1.57mg/l. Zero calibrated the CL2 Analyzer and Cal spanned the analyzer to reflect Cl grab residual values. | FLAG | stage2_low_confidence | 0.018533 | ML: above threshold (no LLM available) — 0.019 | alarm [control_system] | 0.018533 | 0 | 0
2026-02 | 2026-02-26 | Georgina Water Treatment Plant | EAST | ROC called about hi lift header FCL hi alarm logged in remotely, duty active and tower level at 55% and filling. @ 1710 hrs: Hi lift header 2.66 mg/l with hi hi alarm active. keswick header -FCL= 1.59 mg/l Sutton header - FCL= 1.57 mg/l Contact tanks and clear-wells residuals are trending normal No chlorine issues based on trends 1910 hrs: Hi lift header analyzer still trending upward (2.87 mg/l) but analyzer downstream and upstream all reading normal, changes. Directed ROC to ignore Hi lift header reading for the night and will be attended to tomorrow morning, if ROC notice any changes in chlorine analyzers at the clearwells or contact tanks to notify me right away. Also, train 5 experiencing TMP issues, reduced HL flow from 200 down to 190 l/s | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | Georgina Water Treatment Plant | EAST | Onsite for station check and lab analysis, entered data into PWQ sheets. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. 11:00 - Adjusted high lift pump duty to duty 1 - P3, duty 2 - P1, duty 3 - P2. | FLAG | stage2_low_confidence | 0.017759 | ML: above threshold (no LLM available) — 0.018 |  | 0.017759 | 0 | 0
2026-02 | 2026-02-24 | Georgina Water Treatment Plant | EAST | Change out 24 inch butterflyUV south line Filled and ready to be put back in service | FLAG | stage2_low_confidence | 0.010379 | ML: above threshold (no LLM available) — 0.01 |  | 0.010379 | 0 | 0
2026-02 | 2026-02-24 | Georgina Water Treatment Plant | EAST | On site for UV maintenance support for CMS UV1 and UV2 manual off, BKPL_TK_PV3, BKPL_TK1_PV1, BKPL_TK2_PV1 manual closed, Train 7 and Train 8 OFF, 9:50 Initiated backpulse on Train 1, 9:53 UV1 and UV2 influent and effluent valves manual closed, 10:01 Initiated backpulse on Train 2, requested Central Water run KSTP to support UV maintenance on site at GWTP. KSTP high lift pump 3 placed manual on by Jerry Zhang, 10:02 BKPL_TK2_PV1 backpulse tank fill valve manual open, closed handwheel valve to UV2, 10:06, to drain the permeate header Permeate header drained. Electrician Dan Boate cut power to UV2 influent and effluent valves. Operator - UV2 effluent valve local closed, locked and tagged out. Operator - UV2 local off, locked and tagged out. Remote Operator Carter Dunn informed of work and directed to disregard alarms, 10:35 Primed permeate header and UV2 line after UV2 MV1 valve was replaced. Electrician, Dan Boate, powered the influent and effluent UV valves and Operators removed the locked on the UV2 effluent valve and UV2 breaker. Reset train turbidity faults after priming permeate header. Placed all equipment back to auto, placed Trains 1-8 ON. High common permeate turbidity, 15:00 and 15:22, shut down trains, flushed line and reset. High common permeate turbidity and Trains 5-8 in shutdown on high turbidity, 15:52. Initiated backpulse on Train 8. Remained on site for supervised start up. | FLAG | stage2_low_confidence | 0.1791 | ML: above threshold (no LLM available) — 0.179 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.1791 | 0 | 0
2026-02 | 2026-02-27 | Georgina Water Treatment Plant | EAST | Informed ROC. Onsite to perform annual calibration at low lift GWTP building. Calibration mode was used during the work. All the PITs and LITs completed. Put everything back in service. All the related alarms were cleared. No issues . Informed ROC, armed the building and left the site. | FLAG | stage2_low_confidence | 0.0085637 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0085637 | 0 | 0
2026-02 | 2026-02-23 | Georgina Water Treatment Plant | EAST | Attended site and completed MIT and membrane performance review - all good. Recorded observations in the shared PWQ sheet | FLAG | stage2_low_confidence | 0.019165 | ML: above threshold (no LLM available) — 0.019 |  | 0.019165 | 0 | 0
2026-02 | 2026-02-25 | Georgina Water Treatment Plant | EAST | Verified CT & CW, Keswick Header, and Sutton Header analyzers. Entered data into PWQ sheets. Adjusted Keswick header free analyzer with the average of three grab samples. Adjusted Post Clear well free chlorine analyzer with the average of three grab samples. | FLAG | stage2_low_confidence | 0.025039 | ML: above threshold (no LLM available) — 0.025 |  | 0.025039 | 0 | 0
2026-02 | 2026-02-26 | Georgina Water Treatment Plant | EAST | On site for preventative maintenance work orders Completed MIT review and membrane performance review - all okay Chlorine analyzer maintenance sed tanks to lake Low lift pump and motor inspection PSW line injection point maintenance Treated header chlorine analyzer maintenance Chlorine scrubber check Low lift housekeeping Membrane and permeate room housekeeping Chlorine system overhaul - inspected Station and equipment okay | FLAG | stage2_low_confidence | 0.012243 | ML: above threshold (no LLM available) — 0.012 | work order [maintenance_action] | 0.012243 | 0 | 0
2026-02 | 2026-02-23 | Georgina Water Treatment Plant | EAST | Inspected low lift pump 3 flow control valve. Replaced O-rings on indicator shaft. No other issues to report, unit can return to service. | FLAG | stage2_low_confidence | 0.01579 | ML: above threshold (no LLM available) — 0.016 |  | 0.01579 | 0 | 0
2026-02 | 2026-02-25 | Georgina Water Treatment Plant | EAST | On site for station check and sampling work orders W11620072, 9:00 Sutton header turbidity fault - found analyzer in low flow state, increased sample flow from 0.25L/min to 0.5L/min and cleared alarm, 9:30 UV1 reactor minor fault, UV reactor 1 lamp #1-1 lo UV irradiance - UV dosage 32.75 mJ/cm2 and UV intensity 17% okay. Will investigate lamp 1-1 when the plant is off, 9:58 Completed MIT and filter performance review and log, 10:31 Completed lab and station rounds and recorded observations in the shared lab sheet and PWQ sheet, 12:15 Collected raw and treated micro samples, W11620072 Raw water sample collected at 11:20 Treated water sample collected at 12:10 Treated FCl 2.13 mg/L; Treated TCl 2.26 mg/L Completed low lift inspection, 13:30 UV Reactor 3-1 lo UV irradiance - PERM_SV2 and SV3 valves were left manual open from last night. Must leave these valves manual open until the plant shuts off to ensure the plant doesn't lock out from a false turbidity spike while KSETDP fills, 14:30. Station and equipment okay, Jackie Saunders and Patrick Fobert on site | FLAG | stage2_low_confidence | 0.16632 | ML: above threshold (no LLM available) — 0.166 | fault [equipment_failure]; work order [maintenance_action]; sample collected [regulatory]; alarm [control_system] | 0.16632 | 0 | 0
2026-02 | 2026-02-27 | Georgina Water Treatment Plant | EAST | Completed MIT review and membrane performance check - all okay | FLAG | stage2_low_confidence | 0.014665 | ML: above threshold (no LLM available) — 0.015 |  | 0.014665 | 0 | 0
2026-02 | 2026-02-01 | Georgina Water Treatment Plant | EAST | ZW6 permeate turbidity fault, turbidity out of range - directed RO Carter to place OFF and reduced plant setpoint to 180 L/s | FLAG | stage2_low_confidence | 0.010326 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.010326 | 0 | 0
2026-02 | 2026-02-02 | Georgina Water Treatment Plant | EAST | On site for station check, lab analysis and equipment verifications Reviewed MIT and daily filter performance on all membrane trains - Train #2 MIT had failed overnight, will troubleshoot. All other trains passed MIT and filter performance is within range - Recorded data in PWQ sheets Jack P addressed train #6 turbidity fault from over the weekend. Cleaned vial and cleared alarms. Train back in service Initiated MIT on train #2 @09:48 - MIT passed: High: 6.12 kpa / Low: 4.49 kpa Placed train #2 back in service @10:27 Train #4 Air inlet valve failed to close @13:22. Second time this has occurred today. Adjusted the speed setpoint on the aeration valve, will monitor. Placed train back in service. Completed in-house lab analysis on Raw and treated waters Verified analyzer readings - Contact tanks, clearwells, treated, residual management. Made the following adjustments: - Post clearwell adjusted from 1.70 to 1.87 mg/L based on multiple grabs Completed lab reagents, inventory and replace WO Reviewed trends, equipment OOS: Sludge P3, Bisulfite P2 Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; valve failed [infrastructure] | fault [equipment_failure]; failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; valve failed [infrastructure] |  | 1 | 0
2026-02 | 2026-02-02 | Georgina Water Treatment Plant | EAST | Initiated MIT on train #6 @07:49 - it was left off for the weekend due to NTU fault. | FLAG | stage2_low_confidence | 0.0073085 | ML: above threshold (no LLM available) — 0.007 | fault [equipment_failure] | 0.0073085 | 0 | 0
2026-02 | 2026-02-02 | Georgina Water Treatment Plant | EAST | On site for station check and lab Cleaned train 6 turbidimeter and cleared bubbles in cuvette, cleared turbidity fault alarm, and returned to service 9:00 Rotated air compressor duty - Kaiser in lead, 11:20 Rotated raw water sample pump duty, P2 to duty 3, P1 to duty 1, 11:21 Rotated post-chlorination and clearwell ejector solenoid valves - valve 2 OFF, valve 1 to duty 1, 11:23 Rotated backpulse fill valve from tank 2 to tank 1, 11:26 Chris Iliohan completed work strapping down the clearwell backpulse line and BKPL_TK_PV3 was cycled for testing, 11:38. BKPL_TK_PV3 placed back to auto after backpulse tank level of 1.76 M achieved. AER_FMB4_PV1B failed to close (11:57) reset and initiated M-clean, will monitor AER_FMB_P1VB failed to close (14:10) - adjusted speed to open and speed to close, attempted to seat. Monitoring. Completed station rounds and lab, 14:11 Station and equipment okay | FLAG | stage2_low_confidence | 0.036484 | ML: above threshold (no LLM available) — 0.036 | sso [critical]; fault [equipment_failure]; failed [equipment_failure]; alarm [control_system] | 0.036484 | 0 | 0
2026-02 | 2026-02-02 | Georgina Water Treatment Plant | EAST | Reviewed monthly and daily filter performance criteria. All values within range. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069992 | 0 | 0
2026-02 | 2026-02-02 | Georgina Water Treatment Plant | EAST | Chris Iliohan Tyler Smith in to add pipe support To back pulse piping also adjusted opening speed on supply valve . Check operation couple time no further pipe movement | FLAG | stage2_low_confidence | 0.019933 | ML: above threshold (no LLM available) — 0.02 |  | 0.019933 | 0 | 0
2026-02 | 2026-02-17 | Georgina Water Treatment Plant | EAST | On site for station check and sampling work orders, W11588736 Collected GLIP and Bac-T micro samples, 11:46 Treated chlorine residuals, in mg/L FCl 1.95 TCl 2.23 Completed lab Completed JHSC inspection Completed SBS pump inspection Completed low lift housekeeping Verified fluoride, clearwell, contact tank and Keswick treated and Sutton treated chlorine analyzers. Recorded observations in the shared PWQ sheet. Treated chlorine analyzers, grab/analyzer, mg/L Keswick: FCl: 1.81/1.78, TCl: 2.07/2.13 Sutton: FCl: 1.85/1.87, TCl: 2.07/2.18 Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.0063337 | 0 | 0
2026-02 | 2026-02-12 | Georgina Water Treatment Plant | EAST | On site for preventative maintenance work orders Placed GLIP samples out for pickup Completed 2 ton and 5 ton crane inspections, high lift crane, membrane crane and chlorine tonner crane Completed wash water and sludge transfer pump inspection and rotation. Rotated sludge transfer pump duty to: P1 in duty for tank 2, Pump 3 in duty for tank 1, Pump 2 OFF Wash water transfer pump 3 still OOS for maintenance - currently isolated. Wash water transfer pump 1 in duty for tank 1, P2 in duty for tank 2, P3 OFF Completed SO2 emergency repair kit inspection Station and equipment okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] | emergency [critical]; oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-17 | Georgina Water Treatment Plant | EAST | On site for station check, equipment verifications, and weekly micro sampling (W11588736) Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded values in PWQ sheets, no issues observed. Manual backwash on GAC #1: - Placed filter OOS and began draining to clearwell through filter effluent valve @08:15 - Filter drained to 3.01 m @08:35, and started backwash sequence in manual - @09:06 - Stopped backwash pump, allowing filter to rest for 10 minutes - @09:17 - Started filter to waste, by opening inlet valve and FTW valve UV 2 has started with one train to fill the GAC inlet channel. Placed trains 3, 4 and 8 to demand override to fill channel, backwash clearwell and allow for filter to waste. Disabled the demand overrides @10:17 - UV dosage high and UV intensity low alarms - Alarms are due to lower than normal flow through the UVs, okay to disregard - Closed BKWS_MV1 backwash clearwell fill valve @09:55, level is 4.93 m, will finish filling later Activated Duty 1 @09:58 - KSTKWP Level - 58% - Stopped GAC 1 filter to waste @10:25 - Placed GAC 1 back in service - NTU is 0.239 - Completed PWQ sheets plant rounds and data collection, chemical dosage verifications Operations and Adjustments - Duty rotated air compressors - placed KAESER compressor in lead duty - Deactivated Zebra mussel control chlorination @14:03 - Increased Clearwell dosage factors by 2% each: Chlorinator #5 50 to 52%, Chlorinator #6 51 to 53% - Made minor adjustment to clearwell chlorination diffusers, in order to better balance the clearwell chlorine residuals Reviewed trends, Equipment OOS: Sludge Pump #3, Low lift pump #3 Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | sso [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | Georgina Water Treatment Plant | EAST | Initiated Hypo Recovery clean on train #8 @09:22 Collected grab sample from train #8 hypo R-clean @12:50 - 440 mg/L cl2, pH = 10.01 Troubleshooted with train #2 MIT fail overnight and with the TMP alarms that have came in this afternoon. - Manually added pressure to the low side of train #2 to test for leaks @13:28 - Observed leaking camlock fittings on cassette F - Replaced gaskets and re-installed. - Manually added pressure to low side again to test membranes after gasket replacement. - Placed train #2 back in service @14:14 Collected grab sample from train #8 hypo R-clean @15:05 - 430 mg/L cl2, pH = 9.96 | FLAG | stage2_low_confidence | 0.048156 | ML: above threshold (no LLM available) — 0.048 | alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | 0.048156 | 0 | 0
2026-02 | 2026-02-20 | Georgina Water Treatment Plant | EAST | On site for station check. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Reviewed trends in lieu of performing full station check, recorded data in PWQ sheets. Trends for filters, and treated headers OK. Station OK. | FLAG | stage2_low_confidence | 0.019434 | ML: above threshold (no LLM available) — 0.019 |  | 0.019434 | 0 | 0
2026-02 | 2026-02-12 | Georgina Water Treatment Plant | EAST | On site for monthly maintenance - informed ROC of work to be completed - Reviewed MIT and daily filter performance on all membrane trains - All passed and within range - recorded readings in PWQ sheets - Completed UV system cleaning on UVs 1 and 2 - UV sensor calibration - Completed UV 1 from 11:00 to 11:35. Completed UV 2 from 14:00 to 14:30. Placed both UVs back to auto - UVT analyzer dehumidifier element change out - Activated Keswick system duty @14:43, and activated Sutton duty @15:07 | FLAG | stage2_low_confidence | 0.026171 | ML: above threshold (no LLM available) — 0.026 |  | 0.026171 | 0 | 0
2026-02 | 2026-02-11 | Georgina Water Treatment Plant | EAST | On site for station check and sampling work orders GLIP sampling, raw water, W11588975 Operational sampling, raw water algae monitoring, W11568744 Micro sampling, raw and treated water, W11605577 Train 2 low pressure MIT failure - placed Train 2 OFF and initiated MIT, 8:32 Train 7 Recirc inlet V failed to close alarm - reset recirculation valve alarm, 8:37 Train 7 neutralization exceeded dur alarm - verified neutralization with a grab sample, pH 7.35. Returned to service, ON, 8:44 Train 7 recirculation valve not closing when commanded in manual. Train 7 OFF, 8:50 Train 7 recirculation valve - adjusted the limit and cycled the valve in manual, returned to auto, cleared alarm and placed back into service. Train 7 ON, 9:10 Train 7 MIT initiated, 9:10 Initiated Train 8 hypo R clean and activated Keswick duty 1, 9:23 Train 2 ON, 9:30 Collected raw and treated water samples, 10:05 Treated water chlorine residuals: FCl 1.98, TCl 2.08 mg/L Completed MIT and daily filter performance review - all passed, 10:22 Verified Treated water chlorine analyzers, grab/analyzer, in mg/L Keswick FCl, 10:44, 1.65/1.52 - adjusted to match average of grabs Keswick TCl, 10:44, 1.95/1.93 Sutton FCl, 10:50, 1.69/1.80 - adjusted to match average of grabs Sutton TCl, 10:50, 1.97/2.06 - adjusted to match average of grabs Verified treated water fluoride analyzers, grab/analyzer, in mg/L Keswick, 10:49, 0.768/0.65 - increased offset from 0.00 to 0.10 Sutton, 10:49, 0.81/0.59 - increased offset from 0.01 to 0.14 Recorded observations in the station shared PWQ sheet and lab sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.034491 | ML: above threshold (no LLM available) — 0.034 | failed [equipment_failure]; failure [equipment_failure]; work order [maintenance_action]; alarm [control_system] | 0.034491 | 0 | 0
2026-02 | 2026-02-16 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets @09:40 - activated system duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052533 | 0 | 0
2026-02 | 2026-02-12 | Georgina Water Treatment Plant | EAST | Train #8 shutdown on Hihi turbidity @08:07 - first run cycle after recovery clean. Reviewed trends, turbidity back to normal levels. Placed train to backwash and back in service | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069731 | 0 | 0
2026-02 | 2026-02-11 | Georgina Water Treatment Plant | EAST | ROC called regarding MIT fail on Train 2. Directed ROC to leave Train 2 in off position for the night. Directed ROC to deactivate duty since tower was almost full. | FLAG | stage2_low_confidence | 0.0078323 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078323 | 0 | 0
2026-02 | 2026-02-18 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets Deactivated system duty @10:00 - Informed ROC that we would be performing maintenance on turbidity analyzers for Trains, GACs, Treated - Train / Permeate header turbidity analyzer maintenance from 10:00 to 11:15 - GAC 1-4 analyzer maintenance from 11:15 to 12:00 - Treated turbidity analyzer maintenance from 13:00 to 13:30 Manual backwash on GAC #3: Placed GAC 3 OOS on the setpoints page - @12:25 Closed Inlet valve, and opened effluent valve to drain GAC to clearwell - @13:07 Started backwash pump 2 - @13:34 Backwash is complete, allowing filter to rest - Started Filter to waste @13:48, by opening inlet valve, and filter to waste valve. UV had started to fill the GAC inlet channel @13:28 - Causing UV dosage high alarms - Completed housekeeping of common areas - Wash water transfer pump maintenance and duty rotation Activated system duty @14:24 - KSTKWP Level - 50% GAC #3 continuing filter to waste - NTU is still elevated. Will inform on call OIC to place GAC back in service around 16:00 Alarms cleared, station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | Georgina Water Treatment Plant | EAST | Enabled following SCADA alarms on both UV1 and UV2: UV Transmittance lo, lolo UV Intensity hihi, hi, lo, lolo, OOR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.005527 | 0 | 0
2026-02 | 2026-02-10 | Georgina Water Treatment Plant | EAST | ROC called regarding Train 7 neutralization exceeded alarm followed by Train 7 Recirc inlet valve failed to close alarm. Logged into Scada, Neutralization did end up completing without any issues. Still an outstanding inlet valve failed to close alarm. Unable to exercise or reset. Train 7 will be offline for the night. No scheduled M-Cleans tomorrow so can leave this Recirc inlet valve in open status for the night. | FLAG | stage2_low_confidence | 0.058886 | ML: above threshold (no LLM available) — 0.059 | failed [equipment_failure]; scada [control_system]; alarm [control_system]; valve failed [infrastructure] | 0.058886 | 0 | 0
2026-02 | 2026-02-19 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Common Permeate turbidity fault alarm (triggered 06:50) active upon arrival, wiped down vial exterior and cleared alarm. Manual backwash on GAC4: 9:58 - Called ROC to notify of backwash on GAC 4 to be performed. 9:59 - Manual opened backwash clearwell fill valve 10:06 - Placed GAC4 OOS on the setpoints page 10:36 - Common Perm turbidity HIHI alarm, and ZW3 shutdown alarm. Discovered the permeate turbidity vial exterior was wet, wiped down to dry, returned to service, and cleared alarms. 10:38 - Manual closed backwash clearwell fill valve. 10:42 - UV reactor 1 shutdown alarms due to low flow. 10:44 - Changed train three status to off and back on (M-Clean pending) 10:47 - Cleared UV alarms, UV reactor 1 start/stop sequnce fault alarm. UV 1 interlocked. Rotated UV duty to UV reactor 2, to let UV 1 cool down. Monitoring Permeate turbidity while UV 2 runs. 11:33 - Placed GAC4 back in service. Will resume backwash when backwash clearwell can be filled at a later time. Placed UV reactor 1 back in auto. 11:48 - Examined Permeate turbidimeter again - dampness on the interior of the analyzer created turbidity spikes. Wiped down and returned to service. 12:00 - 13:20 Received SBS chemical delivery. 14:00 - 15:00 Completed chlorine analyzer maintenance for Permeate, CIP, Clearwell, CT Tanks, and Post CW analyzers. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | Georgina Water Treatment Plant | EAST | Placed train #8 to Standby @18:45. Recovery clean has been completed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042304 | 0 | 0
2026-02 | 2026-02-13 | Georgina Water Treatment Plant | EAST | On site for station checks, lab analysis and data collection Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets @08:42 - Activated system duty - KSTKWP level - 67% Completed PWQ sheets plant rounds and data collection Completed in-house lab for raw and treated waters Verified chlorine analyzer readings with grab residuals - Made the following adjustments to average of 3 grabs Clearwell #2 - Grab: 1.55 / Analyzer: 1.47 mg/L Post clearwell - Grab: 1.44 / Analyzer: 1.61 mg/L Train #7 CIP Cleaning inlet valve failed to open @10:38. Exercised valve and it was very sticky trying to open. Increased open speed setpoint, and it opened. Also adjusted the close limit on the valve. Exercised valve a few times after, and it seems to actuate better. Will monitor @11:10 - Observed that raw water chlorinator #8 was not dosing. Booster pump is running, but the rotameter is at 0 kg/day. Duty rotated to chlorinator #7, and it is dosing normally at 8 kg/day. Reviewed trends Equipment OOS: Low lift pump #3, Sludge pump #3, Chlorinator #8 Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; oos [equipment_failure]; valve failed [infrastructure] | failed [equipment_failure]; oos [equipment_failure]; valve failed [infrastructure] |  | 1 | 0
2026-02 | 2026-02-18 | Georgina Water Treatment Plant | EAST | 15:37 Closed GAC3 filter to waste valve. Placed GAC3 in service. GAC3 turbidity = 0.146 and trending down. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034966 | 0 | 0
2026-02 | 2026-02-15 | Georgina Water Treatment Plant | EAST | Activated Duty 1 - KSTKWP level - 57% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004347 | 0 | 0
2026-02 | 2026-02-10 | Georgina Water Treatment Plant | EAST | On site for preventative maintenance Completed fluoride probe calibration with a 1.0 mg/L standard, UVs manual off Keswick - 9:41 - reduced offset from 0.12 to 0.01 Sutton - 9:53 - manual closed Sutton PRV for fluoride probe calibration - 9:59 reduced fluoride offset from 0.13 to 0.00 10:28 Sutton PRV returned to auto Completed aeration blower maintenance Completed emergency chlorine repair kit inspection Completed clearwell drain pump inspection Completed clearwell drain valve exercise Completed fluoride pump maintenance - inspection Completed MIT and daily filter performance review and log Station and equipment okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; repair [maintenance_action] | emergency [critical]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-10 | Georgina Water Treatment Plant | EAST | On site for monthly PM's - Informed ROC of work to be completed Initiated MIT on train #7 @08:45 - It was left off overnight after recovery clean Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets Initiated acid Recovery clean on train #7 @09:30 Manual closed Sutton PRV @09:53 for fluoride probe calibration. No alarms caused - Triggered containment leak alarms @10:28 - Hypo, Fluoride and SBS Took grab on train #7 Recovery clean acid - pH = 3.19 @10:30 - Triggered chlorine leak alarms @11:15 - Tonner room and Chemical room Took second grab on train #7 acid clean - pH = 2.96 - Sodium hypo pumps inspection - Caustic soda pumps inspection - Sodium bisulfite pumps inspection - High lift FCV Inspections - High lift pump and motor inspections Train #7 remains in R-clean Equipment OOS: Sludge P3, Low lift P3 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; containment [safety] | oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-07 | Georgina Water Treatment Plant | EAST | Increased Fluoride P1 dosage factor from 105 to 110 due to low Sutton header alarm while feeding Sutton (0.45mg/l). Keswick header in the 0.50 range. | FLAG | stage2_low_confidence | 0.0081183 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081183 | 0 | 0
2026-02 | 2026-02-04 | Georgina Water Treatment Plant | EAST | ROC called regarding Backpulse Valve failed to close alarm. Directed ROC to ack and reset. Aldso had backpulse tank HIHI alarm, most likely related to this valve not closing fully. Will inform GWTP operator tomorrow. | FLAG | stage2_low_confidence | 0.044115 | ML: above threshold (no LLM available) — 0.044 | failed [equipment_failure]; alarm [control_system]; valve failed [infrastructure] | 0.044115 | 0 | 0
2026-02 | 2026-02-03 | Georgina Water Treatment Plant | EAST | Completed MIT and membrane review - all okay | FLAG | stage2_low_confidence | 0.01354 | ML: above threshold (no LLM available) — 0.014 |  | 0.01354 | 0 | 0
2026-02 | 2026-02-06 | Georgina Water Treatment Plant | EAST | Completed low lift station check: - Observed leak on Low lift pump 3 Flow control valve - on the rising stem to the limit switch / indicator. Attempted to tighten the top nut on the stem, could not resolve leak. Placed low lift pump 3 to local off OOS, and isolated pump from the discharge header by closing the pump 3 discharge valve. Created WO for maintenance to address. - Pre chlorination system - chlorine system remains active, with the new chlorine analyzers online and linked to SCADA. Isolated old chlorine analyzers from the sample lines, so that flow is now only going through the new analyzers. Will monitor. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; leak [infrastructure] | oos [equipment_failure]; scada [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-07 | Georgina Water Treatment Plant | EAST | ROC called regarding low fluoride on Sutton Header (0.40mg/l). Keswick header reading 0.52mg/l. Directed ROC to increase dose on P1 (D1) from 1.00 to 1.05. Will monitor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055442 | 0 | 0
2026-02 | 2026-02-03 | Georgina Water Treatment Plant | EAST | On site for monthly maintenance: Informed ROC - Low lift JHSC inspection - Low lift FCV inspections - Low lift turbidity analyzer maintenance - Low lift chlorine analyzer maintenance - Lift chlorine gas detector test: Triggered @10:04. After triggering the alarm, the sensor is stuck at 5.12 ppm, with a fault, OOR and high alarms active. Suspect that the sensor is not working and may need replacement. Will create WO for instrumentation - Received hypo delivery: 1000 L - Troubleshooted train #4 aeration valve B. Train shutdown during backwash @14:14. Observed that the air pressure to the valve was lower than usual. Increased air pressure to the valve from 40 to 60 psi - which is standard to the aeration valves - Troubleshooted train #7 CIP inlet valve - which had failed to open during train #7 M-clean. Had instructed ROC to ack and reset and it reopened it. Made adjustments to close limit on the valve. Will monitor Reviewed trends Equipment OOS: Sludge P3, Bisulfite P2 Disregarding low lift CL2 gas alarms for the night. Work order to be created for instrumentation Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failed [equipment_failure]; oos [equipment_failure]; not working [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; gas alarm [safety] | fault [equipment_failure]; failed [equipment_failure]; oos [equipment_failure]; not working [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; gas alarm [safety] |  | 1 | 0
2026-02 | 2026-02-09 | Georgina Water Treatment Plant | EAST | On site for station check and lab Activated Keswick (KSTKWP) and Georgina (SUETDR) duty 1, 9:05 Fluoride pump 1 running at, 11:25, 60% speed Verified fluoride probes, 11:25, (grab/analyzer), mg/L Keswick: 0.78/0.63 Sutton: 0.71/0.45 - Increased analyzer offset from -0.12 to 0.00 Continuing to monitor to match the analyzers with the average of grabs Rotated from fluoride pump 1 to fluoride pump 2, 11:45 Completed air compressor inspection, 12:30 14:05 - Keswick fluoride in mg/L: grab: 0.85, analyzer: 0.65 - increased offset to 0.12 to match average of grabs 14:05 - Sutton fluoride in mg/L: grab: 0.85, analyzer: 0.61 - increased offset to 0.13 to match average of grabs Completed lab and station rounds, 14:10 Station and equipment okay | FLAG | stage2_low_confidence | 0.010076 | ML: above threshold (no LLM available) — 0.01 | sso [critical] | 0.010076 | 0 | 0
2026-02 | 2026-02-04 | Georgina Water Treatment Plant | EAST | On site for sampling and station check Sampling work orders Algae (raw) W11568573 VOC (raw and treated) W11568102 MBTEB and MBHP (Raw and treated micro sample) W11568372 GEOMIB (raw and treated) W11568573 Mixed citric acid tank and ensured priming tanks were filled and initiated Acid R clean on Train 6, 8:50 Completed MIT and daily filter performance review and log - all okay, 8:51 Low lift chlorine gas detector hi, gas detector hi hi, gas detector OOR alarms outstanding - work order created for Instrumentation Sodium hypo tank level hi hi alarm outstanding from hypo tank top up yesterday, okay to disregard Increased high lift plant flow from 180 to 200 L/s, 11:47 Completed station rounds, sampling, lab, 13:15 Recorded observations in the shared PWQ and station spreadsheets Collected raw and treated samples. Raw sample collected at 9:30. Treated sample collected at 11:40. Treated chlorine grabs as follows: FCl - 2.05 mg/L TCl - 2.36 mg/L Station and equipment okay | FLAG | stage2_low_confidence | 0.014772 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action]; work order created [maintenance_action]; sample collected [regulatory]; alarm [control_system]; alarms [control_system] | 0.014772 | 0 | 0
2026-02 | 2026-02-05 | Georgina Water Treatment Plant | EAST | On site for preventative maintenance Received fluoride delivery Tank level start: 0.46 M, stop: 1.25 M Performed two point calibration on Keswick and Sutton fluoride probes. Plant was off, UVs manual off, ROC informed. Verified fluoride probes with the average of grabs and adjusted offset to match. Keswick: 0.38 mg/L, Sutton: 0.38 mg/L, 11:50 Total Power contractor, Jeremy, inspected diesel generator and reproduced the re-occurring overcrank issue. He and Sean Peoples (CMS Electrician) replaced the speed pot and test ran the generator with no issues. Initiated generator test on load. Generator test run Hours Start 514.55 Stop 515.93 Fuel Start 0.73 M Stop 0.68 M Run statistics 60 Hz 600 V 440 kW 325 A Increased fluoride dosage factor, 13:03 Pump 1 from 0.95 to 1.00 Pump 2 from 0.50 to 0.55 Compressed air receiver B Pressure switch low - disregard. Exercising standby compressor Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | sso [critical] | 0.0025293 | 0 | 0
2026-02 | 2026-02-05 | Georgina Water Treatment Plant | EAST | Train #6 was left off overnight after acid clean. Initiated MIT on train #6 @10:12 - MIT passed - High: 3.16 / Low: 1.82 kpa Reviewed MIT and daily filter performance on all membrane trains - All passed and within range - recorded values in PWQ sheets Completed the following WO's: - Air compressor maintenance and inspection - ran emergency compressor #3 - no issues - Air dryer inspection - Compressed air system inspection, no leaks observed | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; emergency [critical]; leak [infrastructure] | sso [critical]; emergency [critical]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-09 | Georgina Water Treatment Plant | EAST | On site for station check and equipment verifications Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets Initiated Recovery clean Hypo on Train #7 @10:15 Operations and adjustments: - Duty rotated air compressors - Placed BOGE to Lead D1, and Kaeser to Standby D2 - Created WO for maintenance to service Kaeser air compressor, there is a maintenance prompt on the screen. Kaeser compressor remains available in Standby if needed - Primed and tested Sodium bisulfite pump #2 during a neutralization sequence. No leaks observed, pump is now in auto back in service - @11:00 duty rotated clearwell chlorinators - placed chlorinator #6 to D1 - @11:05 duty rotated clearwell solenoid valves, placed valve #2 to D1. Performed visual inspection of chlorination system and lines. Chlorinator #6 is dosing 45 kg/day, with adequate vacuum - @11:22 duty rotated low lift chlorinators (Mussel control) Placed chlorinator #8 in D1 Collected grab sample on train #7 R-clean @13:45 - 400 mg/L cl2, pH = 9.96 Completed PWQ sheets plant rounds, verified dosages all okay. Reviewed trends, equipment OOS: Low lift P3, Sludge P3 Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure]; leak [infrastructure] | sso [critical]; oos [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-06 | Georgina Water Treatment Plant | EAST | On site for station check, 08:00 Activated SUETDR duty 1, 08:18 Completed MIT and daily filter performance review and log - all okay, 08:24 Activated Keswick duty 1, 9:40 Increased fluoride pump 2 dosage factor 0.55 to 0.60, at 10:31 Fluoride analyzer readings: Keswick 0.41 and Sutton 0.38 prior to change with fluoride pump 2 running Increased fluoride pump 2 dosage factor 0.60 to 0.65, 11:11 Verified chlorine analyzers (grab/analyzer) in mg/L Contact tank 1 FCl, 13:06, 1.88/1.91 Contact tank 2 FCl, 13:09, 2.17/2.21 Clearwell 1 FCl, 13:05, 1.91/1.85 Clearwell 2 FCl, 13:10, 1.93/1.84 Post clearwell FCl, 13:12, 1.93/2.15 Adjusted to match average of grabs Keswick header FCl, 13:23, 1.89/1.76 Adjusted to match average of grabs Keswick header TCl, 13:23, 2.12/2.26 Sutton header FCl, 13:04, 1.84/1.97 Sutton header TCl, 13:04, 2.09/2.29 Adjusted Keswick fluoride analyzer, 13:30 Grab: 0.76, Analyzer: 0.51 -- adjusted to 0.61. Continuing to monitor Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047296 | 0 | 0
2026-02 | 2026-02-08 | Georgina Water Treatment Plant | EAST | ROC called regarding Make Up Air Unit low temp alarm. Will disregard till Monday. | FLAG | stage2_low_confidence | 0.0077955 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077955 | 0 | 0
2026-02 | 2026-02-05 | Georgina Water Treatment Plant | EAST | On site with total power for generator issue | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005541 | 0 | 0
2026-02 | 2026-02-23 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Satnam and Chris Iliohan in to get pump 3 up running. Discharge valve faulty. Removed actuator from pump 4 since it out of service Install on pump 3 discharge valve had to reprogram actuator due to left have operation being moved to right hand valve configuration Tested local and remote. No issues noticed at this time | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; out of service [equipment_failure] | fault [equipment_failure]; out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-26 | Aurora Henderson Sewage Pumping Station | WW-CEAST | On site to assist for wet well scum removal. Put station on pac mode around 9.30am. Wessuc was able to clean scum off cell 1 in the wet well. They will be back again to clean the remainder of the wet well. Station put back to auto mode from pac mode at 3.00pm. station back to normal operations. | FLAG | stage2_low_confidence | 0.031026 | ML: above threshold (no LLM available) — 0.031 |  | 0.031026 | 0 | 0
2026-02 | 2026-02-23 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. All pumps available in all-stop auto duty rotation. Station running normal. Standby power generator available in auto. | FLAG | stage2_low_confidence | 0.016603 | ML: above threshold (no LLM available) — 0.017 | scada [control_system] | 0.016603 | 0 | 0
2026-02 | 2026-02-26 | Aurora Henderson Sewage Pumping Station | WW-CEAST | On site for media sampling with Contractor, All Round System (John Round), under RFT 2609-25. | FLAG | stage2_low_confidence | 0.010078 | ML: above threshold (no LLM available) — 0.01 |  | 0.010078 | 0 | 0
2026-02 | 2026-02-02 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. All pumps available in all-stop auto duty rotation. Station running normal. JHSC Health and Safety Inspection completed. Dry Well Flood Alarm Test, High/Low Temperature Alarm Test completed Hazardous Waste Collection and Removal Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped running without problem. Gen Start time: 80.3, Stop time: 81.6, Run time: 1:3hrs. Cleared/reset all alarms. Generator back in auto and available. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] | flood [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] |  | 1 | 0
2026-02 | 2026-02-13 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station check complete and the readings have been entered into the sharepoint | FLAG | stage2_low_confidence | 0.015844 | ML: above threshold (no LLM available) — 0.016 |  | 0.015844 | 0 | 0
2026-02 | 2026-02-27 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. All pumps available in all-stop auto duty rotation. Station running normal. Odour control scrubber system inspection completed. Standby power generator available in auto. | FLAG | stage2_low_confidence | 0.017675 | ML: above threshold (no LLM available) — 0.018 | scada [control_system] | 0.017675 | 0 | 0
2026-02 | 2026-02-20 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. All pumps available in all-stop auto duty rotation. Station running normal. RS Pump inspection. Pump 1 - @ 50% speed, 54 L/s, 329 kPa, 57 A, 551 V, 58 Hz, 1710 Rpm; @100% speed, 65 L/s, 352 kPa, 66 A, 572 V, 60 Hz, 1783 Rpm Pump 2 - @ 50% speed, 50 L/s, 325 kPa, 56 A, 551 V, 58 Hz, 1711 Rpm; @100% speed, 62 L/s, 347 kPa, 65 A, 575 V, 60 Hz, 1783 Rpm Pump 3 - @ 50% speed, 54 L/s, 323 kPa, 57 A, 551 V, 58 Hz, 1711 Rpm; @100% speed, 63 L/s, 349 kPa, 67 A, 545 V, 60 Hz, 1782 Rpm Pump 4 - @ 50% speed, 53 L/s, 330 kPa, 57 A, 551 V, 58 Hz, 1711 Rpm; @100% speed, 64 L/s, 352 kPa, 65 A, 575 V, 60 Hz, 1784 Rpm RS Pump Discharge Valves Actuator Inspection and Exercise Manual Valves Exercise Check valve inspection. Air Relief Valve inspection. | FLAG | stage2_low_confidence | 0.052597 | ML: above threshold (no LLM available) — 0.053 | scada [control_system] | 0.052597 | 0 | 0
2026-02 | 2026-02-09 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station check complete and the readings have been entered into the sharepoint. | FLAG | stage2_low_confidence | 0.015915 | ML: above threshold (no LLM available) — 0.016 |  | 0.015915 | 0 | 0
2026-02 | 2026-02-06 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station check complete and the readings have been entered into the sharepoint | FLAG | stage2_low_confidence | 0.015844 | ML: above threshold (no LLM available) — 0.016 |  | 0.015844 | 0 | 0
2026-02 | 2026-02-24 | Oak Ridges Air Management Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -armed site, and locked gate -station okay | FLAG | stage2_low_confidence | 0.010211 | ML: above threshold (no LLM available) — 0.01 | scada [control_system] | 0.010211 | 0 | 0
2026-02 | 2026-02-02 | Oak Ridges Air Management Facility | WW-CEAST | On site for station check. Entered station readings to sharepoint. Fans 1 and 2 running in auto. Nutrient tank batch mixing completed. Unit 1 recirculation pump #2 OOS. Unit 2 recirculation pump #1 OOS. Standby power generator available in auto | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-19 | Oak Ridges Air Management Facility | WW-CEAST | On site to investigate recirc pump flow issues. Got an approval from Dave(NAC) prior to coming on site for investigation. Found system 1 recirc 1 and system 2 recirc 2 pumps have been isolated with both suction/discharge closed. Talked to Dave(NAC) and he confirmed all valves should have been open and all pumps should have been in service. Opened all valves for above pumps, bled the air out from the pump, and then put it back in service. Noticed 2 different types of pump motors mounted/installed on recirc pumps. Inquired to NAC/Aecom as to why we have 2 different motors. | FLAG | stage2_low_confidence | 0.038155 | ML: above threshold (no LLM available) — 0.038 |  | 0.038155 | 0 | 0
2026-02 | 2026-02-17 | Oak Ridges Air Management Facility | WW-CEAST | On site for station check & Support for EATON VFD Programming. EATON VFD Programming completed successfully. Tested out new recirculation pump for train 1. Entered station readings to sharepoint. Fans 1 and 2 running in auto. Nutrient tank batch mixing completed. Unit 1 recirculation pump #1 OOS. Standby power generator available in auto | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | Oak Ridges Air Management Facility | WW-CEAST | Shelved Estop/communication loss alarms for all recirc pumps as requested by Graham.B/ROC | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-03 | Oak Ridges Air Management Facility | WW-CEAST | -Received call from ROC regarding power failure on site. Utility power has now been restored, but multiple alarms on site. Cleared alarms related to power failure, but Fan 1 VFD Fault will not clear. Contacted team lead, who is following up with NAC regarding Fan 1 fault. | FLAG | stage2_low_confidence | 0.025457 | ML: above threshold (no LLM available) — 0.025 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.025457 | 0 | 0
2026-02 | 2026-02-09 | Oak Ridges Air Management Facility | WW-CEAST | Station check complete and the readings have been entered into the sharepoint. System 2 recirc pump 2 overload alarm outstanding. Informed NAC and Jim(NAC) on his way to troubleshoot. Filled nutrient tank. Increased blowdown for both trains in response to low recirc pH | FLAG | stage2_low_confidence | 0.015595 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system] | 0.015595 | 0 | 0
2026-03 | 2026-03-30 | Keswick Water Resource Recovery Facility | WW-NORTH | decant and transfer sludge tank 1 complete lab and enter data into SharePoint pump scum down batch waste into tank 1 plant checks completed Rake bar screen Level grit bin Clean train three turbidity meter | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061526 | 0 | 0
2026-03 | 2026-03-31 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Delivered spent UV bulbs to Newmarket Completed scheduled work orders Inspected OCU and recorded readings in binder Received citric acid delivery Satnam (electrical) was here to investigate train 2 permeate pump issue - now running in auto. | FLAG | stage2_low_confidence | 0.041944 | ML: above threshold (no LLM available) — 0.042 | work order [maintenance_action]; regulatory [regulatory] | 0.041944 | 0 | 0
2026-03 | 2026-03-15 | Keswick Water Resource Recovery Facility | WW-NORTH | Decanted Sludge holding tanks: 2 & 3 Transferred Sludge holding tanks: 2 & 3 Directed WAS to tank 2 Pumped down scum chambers Rotated UV duties: Duty 1 = Channel 2 Duty 2 = Channel 1 Rotated Headworks screening channel: Duty 1 = Channel 2 Duty 2 = Channel 1 Channel 1 bin is full Overhead door to channel 2 bin room is not working; cycled breaker in an attempt to resolve issue- no success. Will create a followup work order | FLAG | stage2_low_confidence | 0.016957 | ML: above threshold (no LLM available) — 0.017 | not working [equipment_failure]; work order [maintenance_action] | 0.016957 | 0 | 0
2026-03 | 2026-03-11 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Made process adjustment as a result of high flows - lowered aeration tank alum dosages (50 to 20 mg/L), switched bar screen to continuous mode, disabled M-cleans for trains 3-5, and lowered plant recovery from 93 to 90% Completed scheduled work orders Inspected and greased online clarifiers Performed housekeeping around aeration blowers Cleaned TSS probe. | FLAG | stage2_low_confidence | 0.0636 | ML: above threshold (no LLM available) — 0.064 | work order [maintenance_action]; regulatory [regulatory] | 0.0636 | 0 | 0
2026-03 | 2026-03-11 | Keswick Water Resource Recovery Facility | WW-NORTH | Train 4 shut down on hihi turbidity which came in on start up; cleared alarm and placed train back in service and observed start up- turbidity did not immediately drop but gradually reduced below 1 NTU. Will schedule a turbidimeter cleaning tomorrow. | FLAG | stage2_low_confidence | 0.012487 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.012487 | 0 | 0
2026-03 | 2026-03-13 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Lowered RAS return rate from 50 to 40% Scheduled hypo R-cleans for trains 2, 3, and 5 to start at 18:00 Worked on UV 1A - replaced intensity probe sleeve and rack 9, bulb 5 sleeve Found membrane air compressor 2 auto drain passing air continuously - isolated the drain and created a WO for maintenance Cleaned train 2 turbidimeter and returned to service Completed scheduled work orders Exercised outfall gates Inspected microscreen actuators and valves Honeywell was here to fix various arming/disarming issues around plant and Ferguson Electric was here working in generator building. | FLAG | stage2_low_confidence | 0.068167 | ML: above threshold (no LLM available) — 0.068 | sso [critical]; work order [maintenance_action] | 0.068167 | 0 | 0
2026-03 | 2026-03-01 | Keswick Water Resource Recovery Facility | WW-NORTH | Started decanting S.T.T's 2 and 3 | FLAG | stage2_low_confidence | 0.0097781 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097781 | 0 | 0
2026-03 | 2026-03-10 | Keswick Water Resource Recovery Facility | WW-NORTH | Replaced batteries on generator | FLAG | stage2_low_confidence | 0.012678 | ML: above threshold (no LLM available) — 0.013 |  | 0.012678 | 0 | 0
2026-03 | 2026-03-02 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, fed tank 3 until full, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Reset sludge blower/channel blower/membrane MUA alarms Scheduled a heated hypo/acid R-clean on train 2 for 19:00 Worked on membrane turbidimeters Completed scheduled work orders Topped up caustic tank (no delivery today) Inspected OCU and recorded readings in binder Performed portable Honda generator test runs Performed H&S inspection Checked for hazardous waste. | FLAG | stage2_low_confidence | 0.03588 | ML: above threshold (no LLM available) — 0.036 | work order [maintenance_action]; alarm [control_system]; alarms [control_system]; hazard [safety] | 0.03588 | 0 | 0
2026-03 | 2026-03-04 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Checked membrane air compressors and dryers Checked membrane turbidimeters Scheduled a heated hypo/acid R-clean on train 3 for 19:00. | FLAG | stage2_low_confidence | 0.029417 | ML: above threshold (no LLM available) — 0.029 | sso [critical]; regulatory [regulatory] | 0.029417 | 0 | 0
2026-03 | 2026-03-10 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Adjusted aeration tank alum dosages from 60 to 50 mg/L Topped up hypo and caustic tanks Completed scheduled work orders and notified ROC of work being completed Flushed alum lines to aeration tanks Checked aeration tank DO probes Investigate diesel containment flood alarm - contractors working on containment. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; containment [safety] | flood [critical]; work order [maintenance_action]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-05 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Topped up hypo tank Completed scheduled work orders Inspected OCU and recorded readings in binder Inspected sludge holding pumps Anchor Experts was here to inspect fall arrest equipment. | FLAG | stage2_low_confidence | 0.018677 | ML: above threshold (no LLM available) — 0.019 | work order [maintenance_action] | 0.018677 | 0 | 0
2026-03 | 2026-03-23 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Investigated train 2 permeate pump showing in local on SCADA - hour meter on MCC doesn't have power and train 2 won't run in remote Completed scheduled work orders Cleaned TSS probe Inspected and cleaned membrane turbidimeters Exercised alum chemical panel valves Cleaned DO probes Pumped down scum chambers Inspected OCU and recorded readings in binder Performed housekeeping around plant. | FLAG | stage2_low_confidence | 0.03033 | ML: above threshold (no LLM available) — 0.03 | work order [maintenance_action]; scada [control_system] | 0.03033 | 0 | 0
2026-03 | 2026-03-18 | Keswick Water Resource Recovery Facility | WW-NORTH | Test backflow preventers All 6 tested passed | FLAG | stage2_low_confidence | 0.0085344 | ML: above threshold (no LLM available) — 0.009 |  | 0.0085344 | 0 | 0
2026-03 | 2026-03-26 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 2, then directed WAS to tank 3 Replaced tank 2 and 3 decant pumps Completed lab and entered readings into ACE sheet Replaced train 1 turbidimeter vial Completed scheduled work orders Inspected OCU and recorded readings in binder Pumped down scum chambers. | FLAG | stage2_low_confidence | 0.015666 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action] | 0.015666 | 0 | 0
2026-03 | 2026-03-21 | Keswick Water Resource Recovery Facility | WW-NORTH | 1150hrs switched WAS feed from STT2 to STT1 checked scada | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0035573 | 0 | 0
2026-03 | 2026-03-17 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Completed scheduled work orders and notified ROC of work being completed Inspected scum pumps Cleaned DO probes Hosed membrane trains 2-5 and collected sample of initial hypo solution during train 1 R clean (470 mg/L) Placed generator in local for the day while contractors worked on silencers. | FLAG | stage2_low_confidence | 0.029908 | ML: above threshold (no LLM available) — 0.03 | work order [maintenance_action] | 0.029908 | 0 | 0
2026-03 | 2026-03-17 | Keswick Water Resource Recovery Facility | WW-NORTH | Test backflow preventers All passed | FLAG | stage2_low_confidence | 0.010767 | ML: above threshold (no LLM available) — 0.011 |  | 0.010767 | 0 | 0
2026-03 | 2026-03-12 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Made process adjustments - increased aeration tank alum dosages (20 to 40 mg/L), switched bar screen to intermittent mode, enabled M-cleans for trains 3-5 Completed scheduled work orders Pumped down scum chambers Cleaned membrane turbidimeters Tested headworks gas detectors Inspected grit vortexes Inspected headworks sump pump Inspected dewatering pump. | FLAG | stage2_low_confidence | 0.021433 | ML: above threshold (no LLM available) — 0.021 | work order [maintenance_action] | 0.021433 | 0 | 0
2026-03 | 2026-03-03 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Fed tank 2 until full, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Hosed scum buildup in grit classifier 1 Worked on train 5 turbidimeter flowmeter Completed scheduled work orders and notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 369.1 h Stop: 370.2 h Run time: 1.1 h Started effluent pumps after diesel transfer (both in duty 1 but not running) Cleaned DO probes Checked chlorine analyzer Inspected hoists in membrane building Received caustic delivery Inspected air compressors Hosed membrane trains 4&5. | FLAG | stage2_low_confidence | 0.043375 | ML: above threshold (no LLM available) — 0.043 | sso [critical]; not running [equipment_failure]; work order [maintenance_action] | 0.043375 | 0 | 0
2026-03 | 2026-03-06 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Scheduled heated hypo/acid R-cleans on train 4/5 for 18:00 Completed scheduled work orders Checked membrane sump pit and tested high level alarm Tested chemical containment flood alarms Replaced aeration blower 1, 3, and 4 filters Received captor delivery Chris (PCS) was here to replace SCADA UPS in admin building. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; containment [safety] | flood [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-14 | Keswick Water Resource Recovery Facility | WW-NORTH | Directed WAS to sludge thickening tank 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044507 | 0 | 0
2026-03 | 2026-03-09 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Replaced decant pump 2 handle and hose connection, and hosed sludge pad Completed lab and entered readings into ACE sheet Scheduled a hypo/acid R-clean on train 1 for 18:00 Rotated effluent pump duties Completed scheduled work orders Inspected membrane and generator air compressors Inspected OCU, RAS/WAS, and admin sump pumps and tested high level alarm Inspected sludge transfer pumps Inspected supernatant pumps Pumped down scum tanks. | FLAG | stage2_low_confidence | 0.035801 | ML: above threshold (no LLM available) — 0.036 | sso [critical]; work order [maintenance_action]; alarm [control_system] | 0.035801 | 0 | 0
2026-03 | 2026-03-18 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Worked on UV bank 1A - replaced intensity probe but still reading low Scheduled a heater hypo/acid R-clean for train 2 @ 18:00 Lowered alum dosage to aeration tanks from 40 to 35 mg/L Rotated headworks channel 1 into service after bin was emptied Completed scheduled work orders Hosed membrane train 1 Received alum delivery Pumped north flowmeter chamber Placed generator in local for the day while contractors worked on silencers. | FLAG | stage2_low_confidence | 0.041383 | ML: above threshold (no LLM available) — 0.041 | work order [maintenance_action]; regulatory [regulatory] | 0.041383 | 0 | 0
2026-03 | 2026-03-23 | Keswick Water Resource Recovery Facility | WW-NORTH | Test backflow preventers B1 water meter failed 2nd check installed repair kit retested Passed The others both passed | FLAG | stage2_low_confidence | 0.027771 | ML: above threshold (no LLM available) — 0.028 | failed [equipment_failure]; repair [maintenance_action] | 0.027771 | 0 | 0
2026-03 | 2026-03-18 | Keswick Water Resource Recovery Facility | WW-NORTH | Remove broken auto drain from compressor. | FLAG | stage2_low_confidence | 0.021222 | ML: above threshold (no LLM available) — 0.021 | sso [critical] | 0.021222 | 0 | 0
2026-03 | 2026-03-23 | Keswick Water Resource Recovery Facility | WW-NORTH | On site to replace the auto drain on compressor 1 Also took the Ginie lift battery to get a replacement | FLAG | stage2_low_confidence | 0.020399 | ML: above threshold (no LLM available) — 0.02 | sso [critical] | 0.020399 | 0 | 0
2026-03 | 2026-03-22 | Keswick Water Resource Recovery Facility | WW-NORTH | on site 0712hrs sludge handling. out 0720hrs to KeswickPS back 0900hrs. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0023239 | 0 | 0
2026-03 | 2026-03-16 | Keswick Water Resource Recovery Facility | WW-NORTH | Plant checks completed Sludge handling Batch waste into tank 1 Alum delivery received Check OCU Top up hypo day tank Check and grease micro screens Check RAS/WAS pumps and sumps Check crane in RAS/WAS building Competed lab and enter data into SharePoint Program R clean on train 1&4 Clean train 3 turbidity meter Check air compressors | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | sso [critical] | 0.0071062 | 0 | 0
2026-03 | 2026-03-27 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Increased alum dosages to aeration tanks from 35 to 50 mg/L Topped up hypo tank. | FLAG | stage2_low_confidence | 0.010531 | ML: above threshold (no LLM available) — 0.011 |  | 0.010531 | 0 | 0
2026-03 | 2026-03-08 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed weekend sludge work. Decanted and transferred STT 2 and 3 - Investigated where sodium bisulfite containment spill alarm was coming from but could not find source. All other containments are dry. - While in membrane building noticed that the braided water line feeding micro screen 1 was leaking. Removed damaged hose and replaced with new line. Micro screen 1 back online running in auto. | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure]; containment [safety] | spill [critical]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-20 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Scheduled heated hypo+acid R-cleans on trains 3 & 5 for 18:00 and topped up chemical tanks Adjusted citric acid tank level alarms (lo from 0.3 to 0.2 m, lolo from 0.2 to 0.15 m). | FLAG | stage2_low_confidence | 0.017755 | ML: above threshold (no LLM available) — 0.018 | alarm [control_system]; alarms [control_system] | 0.017755 | 0 | 0
2026-03 | 2026-03-26 | Keswick Water Resource Recovery Facility | WW-NORTH | Fuel tank 1 vacuum is 14 inches Hg Fuel tank 2 vacuum is 18.5 inches Hg Day tank is new and contractors are plumbing fittings into it Containment is recently epoxied for bulk and day tanks. | FLAG | stage2_low_confidence | 0.017968 | ML: above threshold (no LLM available) — 0.018 | containment [safety] | 0.017968 | 0 | 0
2026-03 | 2026-03-24 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Topped up caustic tank Cleaned up oil puddle under compressor 1 Performed housekeeping in RAS/WAS basement. | FLAG | stage2_low_confidence | 0.017762 | ML: above threshold (no LLM available) — 0.018 | sso [critical] | 0.017762 | 0 | 0
2026-03 | 2026-03-25 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Recorded monthly meter readings in rounds sheet Collected weekly regulatory samples and delivered to Newmarket Returned caustic lo and lolo setpoints to 0.3 and 0.2 m Initiated M-clean on train 2 during scheduled time (cleans not running remotely while train is interlocked) Performed housekeeping around plant. | FLAG | stage2_low_confidence | 0.056484 | ML: above threshold (no LLM available) — 0.056 | not running [equipment_failure]; regulatory [regulatory] | 0.056484 | 0 | 0
2026-03 | 2026-03-19 | Keswick Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Replaced cable to UV intensity probe - intensity still reading low Completed scheduled work orders Inspected OCU and recorded readings in binder Pumped down scum tanks Received hypo delivery Inspected bar screens Total Lift was here to inspect AWP. | FLAG | stage2_low_confidence | 0.015313 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action] | 0.015313 | 0 | 0
2026-03 | 2026-03-02 | Holland Landing Lagoons | WW-NORTH | station checks health and safety | FLAG | stage2_low_confidence | 0.010632 | ML: above threshold (no LLM available) — 0.011 |  | 0.010632 | 0 | 0
2026-03 | 2026-03-26 | Holland Landing Lagoons | WW-NORTH | site checks | FLAG | stage2_low_confidence | 0.011536 | ML: above threshold (no LLM available) — 0.012 |  | 0.011536 | 0 | 0
2026-03 | 2026-03-09 | Holland Landing Lagoons | WW-NORTH | checked site. | FLAG | stage2_low_confidence | 0.011582 | ML: above threshold (no LLM available) — 0.012 |  | 0.011582 | 0 | 0
2026-03 | 2026-03-20 | Holland Landing Lagoons | WW-NORTH | time in 1100hrs station checks lagoon berm inspection. out 1200 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0023769 | 0 | 0
2026-03 | 2026-03-09 | Holland Landing Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry Diesel containment inspected. | FLAG | stage2_low_confidence | 0.015718 | ML: above threshold (no LLM available) — 0.016 | containment [safety] | 0.015718 | 0 | 0
2026-03 | 2026-03-30 | Holland Landing Sewage Pumping Station | WW-NORTH | Under direction of OIC Chris Colangelo Worked with CMS, David Dougherty, Martin DeVries, Christian Streef. Impeller on RSP_PMP3 was changed. VFD #3 Max Frequency adjusted to 57Hz. Scada speed SP remained the same 85% which reduced the operating speed to 53Hz from 56Hz. Ran flow and speed testing on PMP3 with Maint and Supplier contractors. Everything was put back in Auto after the testing. No outstanding Issues remaining. | FLAG | stage2_low_confidence | 0.039514 | ML: above threshold (no LLM available) — 0.04 | impeller [equipment_failure]; scada [control_system] | 0.039514 | 0 | 0
2026-03 | 2026-03-11 | Holland Landing Sewage Pumping Station | WW-NORTH | on site for OCU media sampling. Drywell condensed inspection | FLAG | stage2_low_confidence | 0.011351 | ML: above threshold (no LLM available) — 0.011 |  | 0.011351 | 0 | 0
2026-03 | 2026-03-05 | Holland Landing Sewage Pumping Station | WW-NORTH | station checks diesel generator test run health and safety OCU inspection drywell flood alarm test , appx1045hrs. Received by cpo | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-10 | Holland Landing Sewage Pumping Station | WW-NORTH | Attended for investigation into abnormal wetwell overflow flowmeter readings Observed water from river has backed up to facility outfall pipe Opened hatch in wetwell to check overflow trough and found some water pooled below the overflow transmitter - no active flow is occurring. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure] | overflow [critical]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-19 | Holland Landing Sewage Pumping Station | WW-NORTH | on site 1030hrs station checks sharepoint data entry diesel containment inspection house cleaning | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | containment [safety] | 0.0032917 | 0 | 0
2026-03 | 2026-03-24 | Holland Landing Sewage Pumping Station | WW-NORTH | Onsite to verify WWEL_FIT1 configuration as requested Informed ROC Placed device into cal mode on scada then connected via HART Found that the flow totalizer had not been configured correctly. Corrected the issue and saved the parameters Removed device from cal mode and cleared associated alarms Informed ROC, armed building and left site | FLAG | stage2_low_confidence | 0.033207 | ML: above threshold (no LLM available) — 0.033 | sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.033207 | 0 | 0
2026-03 | 2026-03-26 | Holland Landing Sewage Pumping Station | WW-NORTH | station checks security car on site , with gate open on arrival. Honeywell working on door. sharepoint data entry diesel containment inspection | FLAG | stage2_low_confidence | 0.017552 | ML: above threshold (no LLM available) — 0.018 | containment [safety] | 0.017552 | 0 | 0
2026-03 | 2026-03-16 | Holland Landing Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry Diesel containment inspection overflow kit inspection. dropped off davit and winch | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure]; containment [safety] | overflow [critical]; overflow [infrastructure]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-02 | Holland Landing Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry | FLAG | stage2_low_confidence | 0.010855 | ML: above threshold (no LLM available) — 0.011 |  | 0.010855 | 0 | 0
2026-03 | 2026-03-10 | Holland Landing Sewage Pumping Station | WW-NORTH | While checking SCADA I noticed that WWEL_FIT1 was showing a flow of approx 25L/s. This reading on SCADA is for the overflow to the river. Based on the SCADA trends this flow started to creep up from 0 L/s on March 7. The trends did not indicate the wetwell level getting to an elevation that would cause an overflow event. At 1113HRS I contacted Kevin Kerek to notify him of the findings. He confirmed that he will dispatch an operator to check out the station and confirm the overflow weir is dry and follow-up as needed with instrumentation. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; follow-up [maintenance_action]; scada [control_system]; overflow [infrastructure] | overflow [critical]; follow-up [maintenance_action]; scada [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | Holland Landing Sewage Pumping Station | WW-NORTH | Responding to inlet channel hihi, caused by channel grinder fault from earlier this morning. Ran grinder locally in reverse and then forward. Placed back to auto and observed start up and brief run period- no issues | FLAG | stage2_low_confidence | 0.04668 | ML: above threshold (no LLM available) — 0.047 | fault [equipment_failure] | 0.04668 | 0 | 0
2026-03 | 2026-03-12 | Holland Landing Sewage Pumping Station | WW-NORTH | On site for PM on odour control system. Checked out motor and fan. Direct coupled no issues with noise or vibration. | FLAG | stage2_low_confidence | 0.021658 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure]; noise [equipment_failure] | 0.021658 | 0 | 0
2026-03 | 2026-03-25 | Holland Landing Sewage Pumping Station | WW-NORTH | Changed Overflow Hi from 250 to 10l/s and HiHi from 280 to 25l/s. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure] | overflow [critical]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | Holland Landing Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint No alarms Check river level - water from river has backed up to facility outfall pipe Opened hatch in wetwell to check overflow trough and found water still pooled below the overflow transmitter - verified there is no active flow occurring. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-23 | Holland Landing Sewage Pumping Station | WW-NORTH | on site 0845hrs station check reset RSP2 at MCC, tripped out on power failure. Ran in duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure] | 0.0056687 | 0 | 0
2026-03 | 2026-03-04 | Holland Landing Sewage Pumping Station | WW-NORTH | On site to add grease wip to channel grinder to make easier access for greasing | FLAG | stage2_low_confidence | 0.014978 | ML: above threshold (no LLM available) — 0.015 |  | 0.014978 | 0 | 0
2026-03 | 2026-03-12 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint Cpd onsite with ghd contractor | FLAG | stage2_low_confidence | 0.01282 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.01282 | 0 | 0
2026-03 | 2026-03-09 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry Diesel containment dry. | FLAG | stage2_low_confidence | 0.015325 | ML: above threshold (no LLM available) — 0.015 | containment [safety] | 0.015325 | 0 | 0
2026-03 | 2026-03-11 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | on site for OCU media sampling. | FLAG | stage2_low_confidence | 0.011917 | ML: above threshold (no LLM available) — 0.012 |  | 0.011917 | 0 | 0
2026-03 | 2026-03-23 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | on site 1000hrs station checks sharepoint data entry diesel containment inspection ( dry ) out 1050hrs | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | containment [safety] | 0.0033867 | 0 | 0
2026-03 | 2026-03-11 | Queensville West Sewage Pumping Station | WW-NORTH | on site for OCU media sampling | FLAG | stage2_low_confidence | 0.011867 | ML: above threshold (no LLM available) — 0.012 |  | 0.011867 | 0 | 0
2026-03 | 2026-03-02 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | station checks van 3081-24 on site ( electrical ), GHD car246-72 on site, 0n arrival. Diesel containment flood alarm from feb 28 @02:37 will not clear, checked containment and is dry. sharepoint data entry 09:05 hrs driller with Thurburn on site to drill one hole in conjunction with GHD. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; containment [safety] | flood [critical]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-03 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | WO's Generator test run OCU inspection drywell flood alarm test, CPO received appx 0924hrs drywell and hoist inspections Recirc valves and actuators exercise health and safety inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry diesel containment inspection ( dry) | FLAG | stage2_low_confidence | 0.016272 | ML: above threshold (no LLM available) — 0.016 | containment [safety] | 0.016272 | 0 | 0
2026-03 | 2026-03-16 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry overflow kit inspection Diesel containment inspection (dry) dropped off davit base and winch | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure]; containment [safety] | overflow [critical]; overflow [infrastructure]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-06 | Queensville West Sewage Pumping Station | WW-NORTH | Onsite to enter wetwell - consolidated work order Alert roc Wetwell overflow came in on scada at 0941hrs Clear and reset alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; alert [control_system]; overflow [infrastructure] | overflow [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; alert [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | Queensville West Sewage Pumping Station | WW-NORTH | Complete pump PM?s No unusual noise, heat , or vibration. Pumps ran well. No slamming of check valves. Pump 3 discharge pressure gauge is broken. Pump 2 discharge 72 L/sec Pump 3 discharge 64 L/sec | FLAG | stage2_low_confidence | 0.014895 | ML: above threshold (no LLM available) — 0.015 | vibration [equipment_failure]; noise [equipment_failure] | 0.014895 | 0 | 0
2026-03 | 2026-03-08 | Queensville West Sewage Pumping Station | WW-NORTH | Responding to sewage pump 2 VFD fault - reset VFD on MCC and cleared alarm on SCADA | FLAG | stage2_low_confidence | 0.021686 | ML: above threshold (no LLM available) — 0.022 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.021686 | 0 | 0
2026-03 | 2026-03-11 | Queensville West Sewage Pumping Station | WW-NORTH | Responding to pump 1 vfd fault (32 fan cooling T1->T16); reset fault and ran pump in manual- no issues. Left pump in duty 1 | FLAG | stage2_low_confidence | 0.023744 | ML: above threshold (no LLM available) — 0.024 | fault [equipment_failure] | 0.023744 | 0 | 0
2026-03 | 2026-03-12 | Queensville West Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint Clear info alarms Diesel containment check | FLAG | stage2_low_confidence | 0.017611 | ML: above threshold (no LLM available) — 0.018 | scada [control_system]; alarm [control_system]; alarms [control_system]; containment [safety] | 0.017611 | 0 | 0
2026-03 | 2026-03-02 | Queensville West Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry | FLAG | stage2_low_confidence | 0.010855 | ML: above threshold (no LLM available) — 0.011 |  | 0.010855 | 0 | 0
2026-03 | 2026-03-05 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry Diesel containment is dry. alarm will not clear. | FLAG | stage2_low_confidence | 0.019631 | ML: above threshold (no LLM available) — 0.02 | alarm [control_system]; containment [safety] | 0.019631 | 0 | 0
2026-03 | 2026-03-04 | Queensville West Sewage Pumping Station | WW-NORTH | WO's generator test run ocu inspection actuators exercise consolidated drywell/hoist inspections. drywell flood alarm test on scada @1037hrs. health and safety | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system] | flood [critical]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | on site 0945hrs station checks sharepoint data entry diesel conatinment inspection out 1030hrs | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0021475 | 0 | 0
2026-03 | 2026-03-05 | Queensville West Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry Diesel conatainment alarm. Found water in containment as snow had been plowed over and melted. Vacuumed out containment. Cleared alarm on scada | FLAG | stage2_low_confidence | 0.030111 | ML: above threshold (no LLM available) — 0.03 | scada [control_system]; alarm [control_system]; containment [safety] | 0.030111 | 0 | 0
2026-03 | 2026-03-09 | Queensville West Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry | FLAG | stage2_low_confidence | 0.010855 | ML: above threshold (no LLM available) — 0.011 |  | 0.010855 | 0 | 0
2026-03 | 2026-03-16 | Queensville West Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry dropped off davit and winch | FLAG | stage2_low_confidence | 0.010297 | ML: above threshold (no LLM available) — 0.01 |  | 0.010297 | 0 | 0
2026-03 | 2026-03-12 | Morton Avenue Air Management Facility | WW-NORTH | WO's station checks blower inspection fanbody inspection recirculation system inspection | FLAG | stage2_low_confidence | 0.0079685 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079685 | 0 | 0
2026-03 | 2026-03-19 | Queensville West Sewage Pumping Station | WW-NORTH | 1117hrs on site station checks sharepoint data entry diesel containment inspection | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | containment [safety] | 0.0036898 | 0 | 0
2026-03 | 2026-03-23 | Queensville West Sewage Pumping Station | WW-NORTH | on site 1056hrs station checks out 1209hrs | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0024138 | 0 | 0
2026-03 | 2026-03-26 | Queensville West Sewage Pumping Station | WW-NORTH | station check sharepoint data entry diesel containment inspection. | FLAG | stage2_low_confidence | 0.015713 | ML: above threshold (no LLM available) — 0.016 | containment [safety] | 0.015713 | 0 | 0
2026-03 | 2026-03-02 | Morton Avenue Air Management Facility | WW-NORTH | Onsite to check station Review scada Enter data in sharepoint Flush blowdown Swap blower duties. Blower 1 in duty 1 Drain flex hose JHSC inspection | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0071127 | 0 | 0
2026-03 | 2026-03-09 | Morton Avenue Air Management Facility | WW-NORTH | Onsite to check station Review scada Enter data in sharepoint Flush blowdown Swap blower duties. Blower 2 in duty 1 | FLAG | stage2_low_confidence | 0.0088291 | ML: above threshold (no LLM available) — 0.009 | scada [control_system] | 0.0088291 | 0 | 0
2026-03 | 2026-03-23 | Morton Avenue Air Management Facility | WW-NORTH | Onsite to check station Review scada - no alarms Enter data in sharepoint Flush blowdown Swap blower duty - blower 2 in d1 | FLAG | stage2_low_confidence | 0.0091562 | ML: above threshold (no LLM available) — 0.009 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0091562 | 0 | 0
2026-03 | 2026-03-16 | Morton Avenue Air Management Facility | WW-NORTH | Rotate blowers Enter data into SharePoint Drain condensation in media unit | FLAG | stage2_low_confidence | 0.010839 | ML: above threshold (no LLM available) — 0.011 |  | 0.010839 | 0 | 0
2026-03 | 2026-03-26 | Morton Avenue Air Management Facility | WW-NORTH | Onsite to check station Review scada Enter data in sharepoint Flush blowdown | FLAG | stage2_low_confidence | 0.011565 | ML: above threshold (no LLM available) — 0.012 | scada [control_system] | 0.011565 | 0 | 0
2026-03 | 2026-03-05 | Morton Avenue Air Management Facility | WW-NORTH | Onsite to check station Review scada Enter data in sharepoint Flush blowdown | FLAG | stage2_low_confidence | 0.011565 | ML: above threshold (no LLM available) — 0.012 | scada [control_system] | 0.011565 | 0 | 0
2026-03 | 2026-03-11 | Morton Avenue Air Management Facility | WW-NORTH | Test backflow preventer | FLAG | stage2_low_confidence | 0.012233 | ML: above threshold (no LLM available) — 0.012 |  | 0.012233 | 0 | 0
2026-03 | 2026-03-19 | Morton Avenue Air Management Facility | WW-NORTH | Onsite to check station Review scada Enter data in sharepoint Flush blowdown | FLAG | stage2_low_confidence | 0.011565 | ML: above threshold (no LLM available) — 0.012 | scada [control_system] | 0.011565 | 0 | 0
2026-03 | 2026-03-30 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: replaced grit bins and raked manual bar screen Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-31 | Sutton Water Resource Recovery Facility | WW-NORTH | Diverted Woodriver Bend to lagoon @ 08:56 hrs Adjusted Flow bias max: 10 L/s --> 15 L/s Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11705266) Raw @ 09:30 / Effluent @ 09:35 Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 38 m3 Diverted Woodriver Bend to lagoon at 08:56 hrs Adjusted Flow bias max: 10 L/s --> 15 L/s Filter B-F3 airlift not throwing sand- pulled and is now functioning Filter A-F1 airlift not throwing sand and unable to pull up airlift. Lanced with air but still unable to budge. Will continue troubleshooting tomorrow Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-05 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tank Transferred Sludge thickening tank Inspected headworks: leveled grit bin and raked bar screen Total Power LTD on site to perform semi annual generator maintenance Completed monthly PM work orders: -Generator test run Date: March 05, 2026 Start time: 11:26 Start hours: 601 Stop Hours: 602.2 Run Time hours: 1.02 Start Fuel: 674 L (23.0 cm) Stop Fuel: 642 L (21.9 cm) Pre run checks: Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok Operating Current: 122 Amps Operating Frequency: 60.0 Hz Operating Voltage: 600 Volts Engine speed: 1803 RPM Water/coolant Temp: 184 F Pyrometer: 864 F Oil Pressure: 42 psi Oil Temp: 212 F | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure]; work order [maintenance_action]; leak [infrastructure] | 0.0011658 | 0 | 0
2026-03 | 2026-03-03 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted and transferred STT Cleaned bar screen area Completed lab analysis and entered readings into SharePoint Pushed out rag and grit bins Checked sand filters | FLAG | stage2_low_confidence | 0.010646 | ML: above threshold (no LLM available) — 0.011 |  | 0.010646 | 0 | 0
2026-03 | 2026-03-13 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted and transferred STT GFL took sludge load 51m3 Completed lab analysis and entered readings into SharePoint Worked on sand filters AF3 and BF3 to get them operating Changed 3 bulbs on UV bank 2A (1-2, 1-4, 2-2) Inspected blower air relief Inspected and cleared inlet channel Test ran South River temp diesel for 15min | FLAG | stage2_low_confidence | 0.0098886 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098886 | 0 | 0
2026-03 | 2026-03-11 | Sutton Water Resource Recovery Facility | WW-NORTH | Onsite for ocu media sampling with omar and contractor | FLAG | stage2_low_confidence | 0.014106 | ML: above threshold (no LLM available) — 0.014 |  | 0.014106 | 0 | 0
2026-03 | 2026-03-10 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted and transferred STT GFL took sludge load 51m3 Completed lab analysis and entered into SharePoint Checked sand filters | FLAG | stage2_low_confidence | 0.0081641 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081641 | 0 | 0
2026-03 | 2026-03-11 | Sutton Water Resource Recovery Facility | WW-NORTH | 07:34 Diverted High St SPS to lagoon and returned Woodriver SPS to plant and placed lagoon pumps to manual off\ 11:36 Placed lagoon pumps back to auto Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11656781) Raw @ 09:25 / Effluent @ 0920 Decanted Sludge holding tank Transferred Sludge thickening tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 51m3 Adjusted Lagoon hydrostatic level Lo alarm: 0.70 m ==> 0.30 m Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | Sutton Water Resource Recovery Facility | WW-NORTH | On site for the broken screen auger and meet green frog. A quote was requested for a new auger | FLAG | stage2_low_confidence | 0.016152 | ML: above threshold (no LLM available) — 0.016 |  | 0.016152 | 0 | 0
2026-03 | 2026-03-15 | Sutton Water Resource Recovery Facility | WW-NORTH | Decanted sludge thickening tank Transferred sludge holding tank Raked manual bar screen | FLAG | stage2_low_confidence | 0.0096993 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096993 | 0 | 0
2026-03 | 2026-03-01 | Sutton Water Resource Recovery Facility | WW-NORTH | Started decanting S.T.T Checked and leveled grit and rag bins Cleaned bar screen equipment Finished decanting and raised gate back to top position Started transfer from S.H.T | FLAG | stage2_low_confidence | 0.011968 | ML: above threshold (no LLM available) — 0.012 |  | 0.011968 | 0 | 0
2026-03 | 2026-03-04 | Sutton Water Resource Recovery Facility | WW-NORTH | Attending site to commission and verify the Lagoon Flowmeter - SUSP_SUSPLG_LGN_FIT1 (W11479921). Configured device, added asset number and verified function. ROC was notified before and after maintenance activities. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-08 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed weekend sludge work - Decanted and transferred STT | FLAG | stage2_low_confidence | 0.012189 | ML: above threshold (no LLM available) — 0.012 |  | 0.012189 | 0 | 0
2026-03 | 2026-03-06 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted and transferred STT Skimmed SBRs GFL took sludge load 50m3 Cleaned bar screen Completed lab analysis and entered readings into SharePoint | FLAG | stage2_low_confidence | 0.0075022 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075022 | 0 | 0
2026-03 | 2026-03-09 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted and transferred STT Completed lab analysis and entered readings into SharePoint GFL took sludge load 51m3 Upon arrival noticed dewatering screw press hopper, which is fed from the bar screen, was full. - Inspected screw press and found it to be sheered in half. - Switched bar screen and screw press to local off. - Pulled gate to manual bar screen and placed it into channel feeding offline bar screen. Maintenance on site to begin repairs on screw press. | FLAG | stage2_low_confidence | 0.031855 | ML: above threshold (no LLM available) — 0.032 | repair [maintenance_action] | 0.031855 | 0 | 0
2026-03 | 2026-03-02 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed station check Decanted and transferred STT Completed lab analysis and entered readings into SharePoint Cleaned bar screen | FLAG | stage2_low_confidence | 0.011872 | ML: above threshold (no LLM available) — 0.012 |  | 0.011872 | 0 | 0
2026-03 | 2026-03-24 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 50 m3 Cleaned DO probe SBR2 Adjusted SBR Common Setpoints: Post DO Low Setpoint = 3.00 PPM --> 3.20 PPM Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-26 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Adjusted WAS Total Cycle time SBR#1: 450 sec --> 430 sec SBR#2: 420 sec --> 380 sec Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-19 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Adjusted filter feed pump duty start: 1.10 m ==> 1.30 m Adjusted UV priorities: LEAD = Channel 2: BANKS- LEAD = A / LAG = B LAG = Channel 1: BANKS- LEAD = A / LAG = B Replaced ballast on UV Bank 1B: lamps 1/2- replaced with an allegedly rebuilt ballast. Ballast failed on start up. Will replace with a brand new ballast tomorrow. Adjusted UV priorities: LEAD = Channel 1: BANKS- LEAD = B / LAG = A LAG = Channel 2: BANKS- LEAD = A / LAG = B Filter B-F3: airlift has started throwing sand. Will continue to monitor. GFL hauled sludge = 51 m3 Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; oos [equipment_failure] | failed [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-20 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Replaced ballast on UV Bank 1B: lamps 1/2- replaced with new ballast. Cleaned effluent sample jug and lines Equipment OOS: Mechanical bar screen and building effluent pump 2 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-20 | Sutton Water Resource Recovery Facility | WW-NORTH | On site to install new effluent pumps. Pump installed but leaking at flange, leaving 1 pump off until Monday when flange can be corrected. | FLAG | stage2_low_confidence | 0.023626 | ML: above threshold (no LLM available) — 0.024 | leak [infrastructure]; leaking [infrastructure] | 0.023626 | 0 | 0
2026-03 | 2026-03-10 | Sutton Water Resource Recovery Facility | WW-NORTH | Changed filter feed start duty from 1.0m to 0.9m to match level bias minimum. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005235 | 0 | 0
2026-03 | 2026-03-12 | Sutton Water Resource Recovery Facility | WW-NORTH | 12:50 Stopped diverting High St SPS to lagoon. All flow going to plant Adjusted SBR Common Setpoints, Post DO low Setpoint: 2.1 ppm ==> 3.0 ppm DO is remaining high and causing the blowers to stay off during the on air cycle. Will continue to monitor and make further changes if required Cleaned DO probes Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tank Transferred Sludge thickening tank Inspected headworks: leveled grit bin and raked manual bar screen Filter 1a; filter and reject water line clogged. Cleared obstruction from reject line but filter requires further maintenance. 14:33 UV Channel 2A multiple lamp failure and not enough healthy bulbs available. Adjusted UV priorities. Channel 1= LEAD / Bank 1 = LEAD / Bank 2 = LAG Channel 2 = LAG / Bank 1 = LAG / Bank 2 = LEAD Will replace bulbs tomorrow. Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; oos [equipment_failure]; clog [infrastructure]; clogged [infrastructure] | failure [equipment_failure]; oos [equipment_failure]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 0
2026-03 | 2026-03-03 | Sutton Water Resource Recovery Facility | WW-NORTH | Test backflow preventers All passed | FLAG | stage2_low_confidence | 0.010767 | ML: above threshold (no LLM available) — 0.011 |  | 0.010767 | 0 | 0
2026-03 | 2026-03-07 | Sutton Water Resource Recovery Facility | WW-NORTH | Began diverting Woodriver bend SPS flows to the lagoon to alleviate load on plant. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070871 | 0 | 0
2026-03 | 2026-03-16 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: screenings bin swap & replacement and raked manual bar screen GFL hauled sludge = 51 m3 Filter B-F3 airlift isn't throwing sand, only bubbling up air. Removed airlift and lanced the bottom of the filter; was extremely clogged- black water and rags were coming up. Reinstalled airlift and placed module back in operation. It was only temporarily functioning, but then failed again. Will continue troubleshooting tomorrow Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; oos [equipment_failure]; clog [infrastructure]; clogged [infrastructure] | failed [equipment_failure]; oos [equipment_failure]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 0
2026-03 | 2026-03-25 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11690050) Raw @ 09:20 / Effluent @ 09:15 Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 50 m3 Rotated UV priorities: LEAD = Channel 1: BANKS- LEAD = A / LAG = B LAG = Channel 2: BANKS- LEAD = A / LAG = B Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-22 | Sutton Water Resource Recovery Facility | WW-NORTH | on site 0800hrs sludge handling checked site. wracked barscreen out 0845hrs | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0019695 | 0 | 0
2026-03 | 2026-03-18 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11672667) Raw @ 08:45 / Effluent @ 09:00 Received ALUM delivery: 2167 L ==> 15'274L Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Adjusted filter "Flow bias maximum": 16 L/s ==> 14 L/s Investigated filter B airlift supply air solenoid valve passing; solenoid requires replacing (burnt out). Breaker for the sand filters has been switched off. Supply air solenoid valves are in manual bypass- air will continuously run, when filter feed pumps are off. Maintenance team lead has been notified and parts have been ordered. UV channel 1 bank B, ballast fail and multiple lamp fault. Will replace ballast tomorrow. Adjusted UV Channel 1 priorities: 1A = LEAD / 1B = LAG Filter B-F3- continued troubleshooting; air lanced again from the side, with the airlift still installed- more rags came up and began throwing sand again. It was only temporarily functioning, but then failed again. Will continue troubleshooting tomorrow GFL hauled sludge = 51 m3 Completed monthly PM work orders: -EQ tank line flush -Decant arms 1 & 2 maintenance -SBR and Sludge blowers air relief inspection -Consolidated headworks inspection Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; fault [equipment_failure]; failed [equipment_failure]; oos [equipment_failure]; burnt out [equipment_failure]; work order [maintenance_action] | bypass [critical]; fault [equipment_failure]; failed [equipment_failure]; oos [equipment_failure]; burnt out [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-17 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 51 m3 Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-23 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: swapped out bar screen bins and raked manual bar screen GFL hauled sludge = 50 m3 Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-27 | Sutton Water Resource Recovery Facility | WW-NORTH | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Equipment OOS: Mechanical bar screen | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-23 | Sutton Water Resource Recovery Facility | WW-NORTH | On site to finish install of effluent pump. Ran tested and put back in service. | FLAG | stage2_low_confidence | 0.015071 | ML: above threshold (no LLM available) — 0.015 |  | 0.015071 | 0 | 0
2026-03 | 2026-03-12 | Sutton Water Resource Recovery Facility | WW-NORTH | UV 1A low intensity alarm came in again. Adjusted UV channel 1 priorities 1A = LAG / 1B = LEAD | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0044109 | 0 | 0
2026-03 | 2026-03-13 | Keswick Sewage Pumping Station | WW-NORTH | Found sewage p.2 running at 100% with no flow Ran all pumps @ 100% and notified ROC of work being completed Obtained flow greater than 205 L/s on all pumps except sewage p.1 (160 L/s). | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058891 | 0 | 0
2026-03 | 2026-03-12 | Keswick Sewage Pumping Station | WW-NORTH | Ran pump 3 at 100% in manual to clear slight blockage. Put other 3 pumps in manual. All back in auto and pump 3 discharged 215l/s | FLAG | stage1_keyword | 0.95 | Critical keyword match: blockage [infrastructure] | blockage [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | Keswick Sewage Pumping Station | WW-NORTH | On site to verify backup panel set-points. Removed obsolete backup panel elevation charts left current operating chart on PAC panel door. Cleaned toilet | FLAG | stage1_keyword | 0.95 | Critical keyword match: backup [infrastructure] | backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-05 | Keswick Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint Hazardous waste removal check Heat trace inspection OCU maintenance | FLAG | stage2_low_confidence | 0.016495 | ML: above threshold (no LLM available) — 0.016 | scada [control_system]; hazard [safety] | 0.016495 | 0 | 0
2026-03 | 2026-03-09 | Keswick Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint ROC call regarding p2 and p3 lolo flow alarms Test both pumps at 100% manual speed - no flow Manually backflush p2 and p3 Try to run again at 100% speed - no flow Consolidated drywell work orders - panel did mot receive drywell flood, will return later to retest P3 clog cleared remotely Back onsite to flush p2 and try drywell flood again Bleed air on p2 - pump runs at 100% 215L/s. Back in service Panel did not receive drywell flood. Will try again later date | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; clog [infrastructure] | flood [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; clog [infrastructure] |  | 1 | 0
2026-03 | 2026-03-13 | Keswick Sewage Pumping Station | WW-NORTH | Attended for sewage p.1 low flow Notified ROC of work being completed Backflushed p.1 and tested @ 100% - 208 L/s. | FLAG | stage2_low_confidence | 0.0096558 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096558 | 0 | 0
2026-03 | 2026-03-23 | Keswick Sewage Pumping Station | WW-NORTH | Onsite to check station and run generator Alert roc Transfer station to diesel power at 11:26hrs Review scada/trends Enter data in sharepoint Transfer station back to diesel power at 12:26hrs Diesel data in sharepoint | FLAG | stage2_low_confidence | 0.0084366 | ML: above threshold (no LLM available) — 0.008 | scada [control_system]; alert [control_system] | 0.0084366 | 0 | 0
2026-03 | 2026-03-16 | Keswick Sewage Pumping Station | WW-NORTH | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.1 running in duty Checked generator building - assisted Toromont tech with his investigation into generator issue from 12/24/2025 @ 00:51 Reviewed SCADA/trends - p.2 had no flow @ 100% speed, bled air and ran @ 100% (flow above 210 L/s for all). | FLAG | stage2_low_confidence | 0.020369 | ML: above threshold (no LLM available) — 0.02 | scada [control_system] | 0.020369 | 0 | 0
2026-03 | 2026-03-22 | Keswick Sewage Pumping Station | WW-NORTH | on site 0730hrs Responding to both channel grinder faults at 0644hrs ( VFD faults ). reset at MCC and then on scada. Both running now. 0739hrs while on site. Ultrasonic Hi and HI HI level alarms came in. RSP 1 and 2 now running at 272 l/s. Cleared ultrasonic alarms. cmu11750026. out 0745hrs | FLAG | stage2_low_confidence | 0.013048 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.013048 | 0 | 0
2026-03 | 2026-03-26 | Keswick Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter in sharepoint Clear outstanding alarms | FLAG | stage2_low_confidence | 0.01214 | ML: above threshold (no LLM available) — 0.012 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.01214 | 0 | 0
2026-03 | 2026-03-27 | Keswick Sewage Pumping Station | WW-NORTH | house keeping found water on floor in boiler room coming from condensate box behind boiler. mopped up . | FLAG | stage2_low_confidence | 0.014819 | ML: above threshold (no LLM available) — 0.015 |  | 0.014819 | 0 | 0
2026-03 | 2026-03-19 | Keswick Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint No outstandingp alarms | FLAG | stage2_low_confidence | 0.012334 | ML: above threshold (no LLM available) — 0.012 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.012334 | 0 | 0
2026-03 | 2026-03-02 | Keswick Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint Clear outstanding alarms - p2 lo flow Provide access to building for Eaton and Lexsan contractors to investigate OCU vfd issue Find p2 check valve leaking at the stem. Disable p2 from duty rotation and in manual off Eaton finds ocu drive is not operational and will be replaced JHSC inspection | FLAG | stage2_low_confidence | 0.02579 | ML: above threshold (no LLM available) — 0.026 | scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | 0.02579 | 0 | 0
2026-03 | 2026-03-06 | Keswick Sewage Pumping Station | WW-NORTH | Onsite to complete consolidated wetwell work order Alert roc 10:20hrs station overflow and wetwell mezzanine flood alarm came in on scada. Clear and reset Alert roc work complete | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; flood [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alert [control_system]; overflow [infrastructure] | overflow [critical]; flood [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alert [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-07 | Keswick Sewage Pumping Station | WW-NORTH | On site responding to Channel Grinder 2 overload fault. - Upon arrival the VFD was showing an OL fault - Reset alarm and attempted to run in auto but alarm came back in - Placed grinder in local and ran in reverse briefly - Reset alarm and placed back into Auto Channel Grinder 2 is now back running in auto | FLAG | stage2_low_confidence | 0.028376 | ML: above threshold (no LLM available) — 0.028 | fault [equipment_failure]; alarm [control_system] | 0.028376 | 0 | 0
2026-03 | 2026-03-30 | Sutton Woodriver Bend Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Equipment OOS: none | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-05 | Sutton Woodriver Bend Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Ran diesel generator Completed JHS inspection | FLAG | stage2_low_confidence | 0.010259 | ML: above threshold (no LLM available) — 0.01 |  | 0.010259 | 0 | 0
2026-03 | 2026-03-09 | Sutton Woodriver Bend Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Reviewed trends | FLAG | stage2_low_confidence | 0.010695 | ML: above threshold (no LLM available) — 0.011 |  | 0.010695 | 0 | 0
2026-03 | 2026-03-02 | Sutton Woodriver Bend Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-16 | Sutton Woodriver Bend Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-23 | Sutton Woodriver Bend Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-12 | Sutton Woodriver Bend Sewage Pumping Station | WW-NORTH | Performed station check' Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.012001 | ML: above threshold (no LLM available) — 0.012 |  | 0.012001 | 0 | 0
2026-03 | 2026-03-12 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Completed JHS inspection | FLAG | stage2_low_confidence | 0.011185 | ML: above threshold (no LLM available) — 0.011 |  | 0.011185 | 0 | 0
2026-03 | 2026-03-30 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Equipment OOS: none | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-09 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-02 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-19 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-23 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-05 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-16 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 |  | 0.011947 | 0 | 0
2026-03 | 2026-03-30 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Equipment OOS: none | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-26 | Sutton South River Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoiunt | FLAG | stage2_low_confidence | 0.011944 | ML: above threshold (no LLM available) — 0.012 |  | 0.011944 | 0 | 0
2026-03 | 2026-03-11 | Sutton High Street Sewage Pumping Station | WW-NORTH | Onsite for ocu media sampling with omar and contractor | FLAG | stage2_low_confidence | 0.014106 | ML: above threshold (no LLM available) — 0.014 |  | 0.014106 | 0 | 0
2026-03 | 2026-03-09 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Reviewed trends | FLAG | stage2_low_confidence | 0.010695 | ML: above threshold (no LLM available) — 0.011 |  | 0.010695 | 0 | 0
2026-03 | 2026-03-27 | Sutton High Street Sewage Pumping Station | WW-NORTH | Placed pump #1 in local off to inspect suction check valve as a potential cause of pump issues. Isolated discharge valve and opened drain in order to open inspection port. - Wiped off checked and rinsed with hose. - Closed inspection port and opened discharge valve to place pump back online. - Ran pump #1 in auto manual 100% for first start up to purge any air. - Placed pump #1 in auto duty 1 - Pump #1 ran normal with no alarms Will monitor the next few cycles to make sure pump continues to run properly. | FLAG | stage2_low_confidence | 0.031368 | ML: above threshold (no LLM available) — 0.031 | alarm [control_system]; alarms [control_system] | 0.031368 | 0 | 0
2026-03 | 2026-03-23 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Checked pump room and reviewed trends | FLAG | stage2_low_confidence | 0.011877 | ML: above threshold (no LLM available) — 0.012 |  | 0.011877 | 0 | 0
2026-03 | 2026-03-26 | Sutton High Street Sewage Pumping Station | WW-NORTH | Responding to CMU5 W11760566 P1 VFD fault Alarm came in at 00:00hrs vfd fault and no flow alarm. Ack reset vfd and pump Run pump 100% speed - wetwell level trending down. Place p1 in duty 1 - will monitor pump cycle P1 ran full pump cycle in auto no apparent issues | FLAG | stage2_low_confidence | 0.026054 | ML: above threshold (no LLM available) — 0.026 | fault [equipment_failure]; alarm [control_system] | 0.026054 | 0 | 0
2026-03 | 2026-03-12 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint Overflow kit inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; scada [control_system]; overflow [infrastructure] | overflow [critical]; scada [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-02 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Reviewed SCADA trends | FLAG | stage2_low_confidence | 0.014034 | ML: above threshold (no LLM available) — 0.014 | scada [control_system] | 0.014034 | 0 | 0
2026-03 | 2026-03-12 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed station check Pump #2 air relief was leaking, isolated air relief and notified maintenance. Completed assigned EZMax work orders: - Test ran diesel generator - JHS inspection Entered readings into SharePoint | FLAG | stage2_low_confidence | 0.024256 | ML: above threshold (no LLM available) — 0.024 | work order [maintenance_action]; notified maintenance [maintenance_action]; leak [infrastructure]; leaking [infrastructure] | 0.024256 | 0 | 0
2026-03 | 2026-03-05 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Collected davit arm for inspection | FLAG | stage2_low_confidence | 0.011695 | ML: above threshold (no LLM available) — 0.012 |  | 0.011695 | 0 | 0
2026-03 | 2026-03-13 | Sutton High Street Sewage Pumping Station | WW-NORTH | Changed pump duty levels back to original levels adjusted from December 10th 2025 to scour forcemain. High level influent alarm keeps coming in at the WRRF. Duty 1 was 1.85 start back to 1.65 stop was 1.0 now back to 1.3. Duty 2 start was 1.95 back to 1.85 and stop was 1 now back to 1.4m. Also minimum speed % on pumps was 100 now 0% | FLAG | stage2_low_confidence | 0.016455 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system] | 0.016455 | 0 | 0
2026-03 | 2026-03-19 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Checked pump room and reviewed trends | FLAG | stage2_low_confidence | 0.011877 | ML: above threshold (no LLM available) — 0.012 |  | 0.011877 | 0 | 0
2026-03 | 2026-03-26 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Checked pump room - ok | FLAG | stage2_low_confidence | 0.011106 | ML: above threshold (no LLM available) — 0.011 |  | 0.011106 | 0 | 0
2026-03 | 2026-03-16 | Sutton High Street Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Checked pump room - ok | FLAG | stage2_low_confidence | 0.011106 | ML: above threshold (no LLM available) — 0.011 |  | 0.011106 | 0 | 0
2026-03 | 2026-03-18 | Sutton High Street Sewage Pumping Station | WW-NORTH | Replaced broken 1? fitting from air relief on pump 2. Found connection leaking at union. Adjusted connection and checked during next run cycle okay. Complete. | FLAG | stage2_low_confidence | 0.01588 | ML: above threshold (no LLM available) — 0.016 | leak [infrastructure]; leaking [infrastructure] | 0.01588 | 0 | 0
2026-03 | 2026-03-18 | Sutton High Street Sewage Pumping Station | WW-NORTH | Completed vibration readings on both pumps and motors. | FLAG | stage2_low_confidence | 0.025814 | ML: above threshold (no LLM available) — 0.026 | vibration [equipment_failure] | 0.025814 | 0 | 0
2026-03 | 2026-03-27 | Sutton High Street Sewage Pumping Station | WW-NORTH | Responding to W11762134 p1 vfd fault. Alarm came in at 00:07hrs loss of prime no flow alarm vfd fault Reset all, check pump room Run pump 1 at 100% speed. Clear blockage and place in duty 1 Monitor full pump cycle in auto with pump speed set to manual 20% - no issues | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; blockage [infrastructure] | fault [equipment_failure]; alarm [control_system]; blockage [infrastructure] |  | 1 | 0
2026-03 | 2026-03-05 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint TSSA contractors onsite working on generator | FLAG | stage2_low_confidence | 0.013606 | ML: above threshold (no LLM available) — 0.014 | scada [control_system] | 0.013606 | 0 | 0
2026-03 | 2026-03-11 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | on site for OCU media sampling | FLAG | stage2_low_confidence | 0.011867 | ML: above threshold (no LLM available) — 0.012 |  | 0.011867 | 0 | 0
2026-03 | 2026-03-23 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint No alarms | FLAG | stage2_low_confidence | 0.011648 | ML: above threshold (no LLM available) — 0.012 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.011648 | 0 | 0
2026-03 | 2026-03-04 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Onsite to complete work orders Alert roc Review scada/trends hazardous waste removal OCU maintenance Consolidated drywell work order Diesel test run Transfer station to diesel power at 10:59hrs JHSC inspection Heat exchanger Radiator inspection Hi/low temp - came in on scada 11:12hrs Sump high level - came in on scada 11:35hrs Transfer station back to hydro power at 11:55hrs Hoist inspection Clear all alarms and reset dialer Diesel data in sharepoint Alert roc work complete | FLAG | stage2_low_confidence | 0.012931 | ML: above threshold (no LLM available) — 0.013 | work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; alert [control_system]; hazard [safety] | 0.012931 | 0 | 0
2026-03 | 2026-03-02 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint | FLAG | stage2_low_confidence | 0.013344 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013344 | 0 | 0
2026-03 | 2026-03-09 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint | FLAG | stage2_low_confidence | 0.013344 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013344 | 0 | 0
2026-03 | 2026-03-16 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry | FLAG | stage2_low_confidence | 0.010855 | ML: above threshold (no LLM available) — 0.011 |  | 0.010855 | 0 | 0
2026-03 | 2026-03-19 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint | FLAG | stage2_low_confidence | 0.013344 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013344 | 0 | 0
2026-03 | 2026-03-26 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends No alarms Enter data in sharepoint | FLAG | stage2_low_confidence | 0.01164 | ML: above threshold (no LLM available) — 0.012 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.01164 | 0 | 0
2026-03 | 2026-03-02 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint | FLAG | stage2_low_confidence | 0.013344 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013344 | 0 | 0
2026-03 | 2026-03-05 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint | FLAG | stage2_low_confidence | 0.013344 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013344 | 0 | 0
2026-03 | 2026-03-11 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite for ocu media sampling with Omar and contractor | FLAG | stage2_low_confidence | 0.014106 | ML: above threshold (no LLM available) — 0.014 |  | 0.014106 | 0 | 0
2026-03 | 2026-03-10 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Responding again to bar screen over torque fault alarm. Reset alarm and watched bar screen run a full cycle in auto. Due to higher flows adjusted run time of bar screen to run every 45 min rather than 1.5 hours. | FLAG | stage2_low_confidence | 0.047245 | ML: above threshold (no LLM available) — 0.047 | fault [equipment_failure]; alarm [control_system] | 0.047245 | 0 | 0
2026-03 | 2026-03-16 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Performed station check Entered readings into SharePoint Checked bar screen and bin | FLAG | stage2_low_confidence | 0.011398 | ML: above threshold (no LLM available) — 0.011 |  | 0.011398 | 0 | 0
2026-03 | 2026-03-19 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint | FLAG | stage2_low_confidence | 0.013344 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013344 | 0 | 0
2026-03 | 2026-03-11 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Attended for wet well high level alarms Opened forcemain 1 to allow for greater flow out of wetwell - station flow increased from 150 L/s to 250 L/s and forcemain 2 pressure dropped from ~555 to ~485 kPa (forcemain 1 also ~485 kPa) Checked bar screen for overload alarm and tightened bolts on scraper blade, reset alarms and ran. | FLAG | stage2_low_confidence | 0.029763 | ML: above threshold (no LLM available) — 0.03 | alarm [control_system]; alarms [control_system] | 0.029763 | 0 | 0
2026-03 | 2026-03-03 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite to complete work orders Alert roc Diesel test run - 10:08hrs transfer station to diesel power Jhsc Consolidated drywell work order -drywell flood - came in on dialer and scada 10:20hrs Building hi low temp - came in on scada 10:19hrs Check valve inspection RSP inspection Sump pit inspection Dialer test Hoist inspection Hazardous waste removal OCU maintenance Transfer station back to hydro power at 11:26hrs Diesel data in sharepoint Alert roc station back to normal operation Clear alarms/ reset dialer | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; alert [control_system]; hazard [safety] | flood [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; alert [control_system]; hazard [safety] |  | 1 | 0
2026-03 | 2026-03-12 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint Change barscreen run time back to every 1.5hrs from every 45 mins. Found p3 had been running continuously since yesterday. Manually swap pump duties - p1 - d1 Overflow kit inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; scada [control_system]; overflow [infrastructure] | overflow [critical]; scada [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-27 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint No alarms Barscreen and screw press maintenance | FLAG | stage2_low_confidence | 0.01158 | ML: above threshold (no LLM available) — 0.012 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.01158 | 0 | 0
2026-03 | 2026-03-09 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Responding to bar screen over torque fault - reset alarm and ran manually for a full cycle - placed back in auto and watched it run in auto | FLAG | stage2_low_confidence | 0.031176 | ML: above threshold (no LLM available) — 0.031 | fault [equipment_failure]; alarm [control_system] | 0.031176 | 0 | 0
2026-03 | 2026-03-31 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | Test | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049179 | 0 | 0
2026-03 | 2026-03-23 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint P1 run time higher than other pumps and running in duty 1 on arrival. Switch pump duties - p1-d3 | FLAG | stage2_low_confidence | 0.013346 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013346 | 0 | 0
2026-03 | 2026-03-09 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | Onsite to check station Review scada/trends Enter data in sharepoint Rake barscreen | FLAG | stage2_low_confidence | 0.011922 | ML: above threshold (no LLM available) — 0.012 | scada [control_system] | 0.011922 | 0 | 0
2026-03 | 2026-03-31 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check and to collect bacti sample w11705480 Residuals Treated Free Grab: 1.52mg/L, Analyzer 1.48mg/L Treated total 1.89mg/L Post Reservoir Free grab 1.56mg/L, Analyzer 1.60mg/L Pre Reservoir free grab 3.50mg/L, Analyzer 3.53mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045505 | 0 | 0
2026-03 | 2026-03-31 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | Test entry - IT investigation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055551 | 0 | 0
2026-03 | 2026-03-05 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | -on site to respond to discharge pressure LOLO alarm, treated water free chlorine LOLO and fault alarms, and post reservoir free chlorine LOLO and fault alarms -arrived on site and found all high lifts interlocked due to max # of starts -ran pump #1 in local, once pressure was restored chlorine analyzers began reading again -PCS disabled the high lift pump max # of starts interlock, reset alarms and pumps began running in auto -discharge pressure was low from 10:43 to 11:01, informed King on call operator -verified analyzers: 11:05 - treated water FCL analyzer = 1.61 mg/L Grab = 1.55 mg/L 11:13 - post reservoir FCL analyzer = 1.40 mg/L Grab = 1.53/1.58/1.56 mg/L 11:19 - adjusted post reservoir analyzer to 1.56 mg/L based on average of 3 grabs -reviewed trends, system appears to be experiencing unusually high demand which caused high number of pump starts, put two pumps into duty 3 to reduce amount of pump starts and stops -site back to normal operation, will continue to monitor | FLAG | stage2_low_confidence | 0.099796 | ML: above threshold (no LLM available) — 0.1 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.099796 | 0 | 0
2026-03 | 2026-03-12 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to check bladder tank pneumatic pressure. Notify ROC of running HLPs in local to maintain reasonable pressures while tanks isolated from system. Drain water from tanks, confirm pneumatic pressure: Tank 2 250kpa Tank 1 210kpa Manufacturer install instructions: set air pressure to 2psi below cut in (duty 1 start). Fill tanks to 296kPa. Place back in service and monitor. Clean Treated NTU analyzer vial (vial clarity alarm). NTU may spike due to pneumatic tank draining and running HLPs without tanks. HLP cycles appear to be 6-7 minute intervals, up from 3 minutes. No other issues. | FLAG | stage2_low_confidence | 0.018339 | ML: above threshold (no LLM available) — 0.018 | alarm [control_system] | 0.018339 | 0 | 0
2026-03 | 2026-03-04 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check and to collect bacti sample w11637320 Residuals Treated Free Grab: 1.56mg/L, Analyzer 1.34-1.56mg/L Total 1.76mg/L Adjusted treated free from 1.34-156mg/L after multiple grabs Post Reservoir Free grab 1.50mg/L, Analyzer 1.42mg/L Pre Reservoir Free grab 3.04mg/L, Analyzer 3.36mg/L No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042621 | 0 | 0
2026-03 | 2026-03-02 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified inlet analyzer 08:55 -analyzer: 3.48mg/l grab: 2.78mg/l - adjusted -verified post res analyzer 09:00 -analyzer: 1.55mg/l grab: 1.40mg/l - adjusted -verified treated analyzer 09:05 -analyzer: 1.59mg/l grab: 1.36mg/l - adjusted -total grab: 1.57mg/l -cleaned NTU analyzer -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053566 | 0 | 0
2026-03 | 2026-03-16 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check Residuals Treated Free Grab: 1.42mg/L, Analyzer 1.48mg/L Post Reservoir Free grab 1.43mg/L, Analyzer 1.39mg/L No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045662 | 0 | 0
2026-03 | 2026-03-20 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -inlet 08:25: 2.63mg/l grab: 2.80mg/l - adjusted -post res 08:30: 1.41mg/l grab: 1.39mg/l -treated free 08:35: 1.38mg/l grab: 1.36mg/l -total grab: 1.52mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054265 | 0 | 0
2026-03 | 2026-03-27 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check Residuals Treated Free Grab: 1.42mg/L, Analyzer 1.49mg/L Post Reservoir Free grab 1.46mg/L, Analyzer 1.52mg/L Pre Reservoir free grab 3.42mg/L, Analyzer 3.33mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039179 | 0 | 0
2026-03 | 2026-03-11 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check and complete weekly BacT sample - W1165875 Residuals Treated Free Grab: 1.34 mg/L, Analyzer 1.37mg/L Post Reservoir Free grab 1.33mg/L, Analyzer 1.39mg/L Pre Reservoir free grab 2.90 mg/L, Analyzer 2.90mg/L Topped up hypo tanks, 33 -> 52 L No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004247 | 0 | 0
2026-03 | 2026-03-03 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | -on site to complete work orders -informed ROC of work -completed Pumps 2 and 3 Strainer Inspection -completed Turbidity Analyzer TU5300 Maintenance and Calibration -cleaned turbidimeter vial, verified analyzer - passed -completed Siemens Depolox 5/Micro 2000 Chlorine Analyzer Maintenance -cleaned analyzers, checked electrolyte and grit sand -verified analyzers after maintenance: 10:00 - post reservoir FCL analyzer = 1.46 mg/L Grab = 1.46 mg/L 10:07 - reservoir inlet FCL analyzer = 3.43 mg/L Grab = 3.24/3.20/3.16 mg/L 10:14 - adjusted reservoir inlet analyzer to 3.20 mg/L based on average of 3 grabs 10:16 - treated water FCL analyzer = 1.40 mg/L Grab: = 1.45 mg/L -completed Pressure Regulating Valve Maintenance -completed JHSC Health and Safety Inspection -cleaned and tested well # 2 discharge air valve -power systems contractor on site for annual generator maintenance, performing load test on generator 10:32 - contractor started generator, generator hours = 312 hours 18 minutes -reservoir inlet chlorine hihi alarm came in, verified analyzer: 11:51 - reservoir inlet FCL analyzer = 4.13 mg/L Grab = 3.28/3.20/3.16 mg/L 12:05 - adjusted reservoir inlet analyzer to 3.21 mg/L based on average of 3 grabs 12:08 - generator hours = 313 hours 54 minutes -CMS on site to continue generator maintenance | FLAG | stage2_low_confidence | 0.014546 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action]; alarm [control_system] | 0.014546 | 0 | 0
2026-03 | 2026-03-06 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check Residuals Treated Free Grab: 1.41mg/L, Analyzer 1.40mg/L Post Reservoir Free grab 1.35mg/L, Analyzer 1.40mg/L No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045662 | 0 | 0
2026-03 | 2026-03-09 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check Residuals Treated Free Grab: 1.25mg/L, Analyzer 1.38mg/L Post Reservoir Free grab 1.19mg/L, Analyzer 1.32mg/L No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045662 | 0 | 0
2026-03 | 2026-03-03 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | On site for annual generator pm. | FLAG | stage2_low_confidence | 0.011944 | ML: above threshold (no LLM available) — 0.012 |  | 0.011944 | 0 | 0
2026-03 | 2026-03-04 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | Disable the Max No Starts for High Lift PMP1-PMP3 based on request from OIC. (Setting was 20/hr - something in the field may be causing surplus of starts - will leave disabled until told otherwise) | FLAG | stage2_low_confidence | 0.0076338 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076338 | 0 | 0
2026-03 | 2026-03-23 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ -verified analyzer -inlet 08:50: 2.77mg/l grab: 3.12mg/l - adjusted -post res08:45: 1.64mg/l grab: 1.54mg/l - adjusted -treated free 08:40: 1.56mg/l grab: 1.52mg/l - adjusted -total grab: 1.76mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057531 | 0 | 0
2026-03 | 2026-03-18 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | -on site to complete station check and weekly bacti W11672769 -checked trends: all ok -entered reading in PWQ : all ok -verified analzyser -inlet 08:40: 2.58mg/l grab 2.62mg/l -post res 08:45: 1.34mg/l grab: 1.31mg/l -treated free: 08:50: 1.48 grab: 1.33mg/l - adjusted -total grab: 1.53mg/l -increased dosage factor 150 -155% -cleaned NTU analyzer -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060331 | 0 | 0
2026-03 | 2026-03-30 | Aurora (East) First Commerce Elevated Tank | CENTRAL | System testing NOT real please ignore Revision 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031666 | 0 | 0
2026-03 | 2026-03-25 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check and to collect bacti sample w11690144 Residuals Treated Free Grab: 1.53mg/L, Analyzer 1.53mg/L Total 1.81mg/L Post Reservoir Free grab 1.54mg/L, Analyzer 1.53mg/L Pre Reservoir Free grab 3.12mg/L, Analyzer 3.03mg/L No other issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045098 | 0 | 0
2026-03 | 2026-03-13 | Ansnorveldt Wells 2, 3 & Reservoir | WEST | In to Complete Station Check Residuals Treated Free Grab: 1.36 mg/L, 1.43 Analyzer mg/L Treated total grab 1.53 mg/L Post Reservoir Free grab 1.40 mg/L, Analyzer 1.38mg/L Pre Reservoir free grab mg/L, Analyzer mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051363 | 0 | 0
2026-03 | 2026-03-11 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11657608: Sample results (08:10): Free- 0.03, Total- 2.72 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052756 | 0 | 0
2026-03 | 2026-03-31 | Aurora (East) First Commerce Elevated Tank | CENTRAL | This is a test | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051903 | 0 | 0
2026-03 | 2026-03-25 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11690776: Sample results (11:22): Free- 0.09, Total- 2.76 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052756 | 0 | 0
2026-03 | 2026-03-19 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp alarms Ventilation inspection Heat trace system inspection Portable generator test/inspection Manual valve exercise/inspection Depolox analyzer maintenance Dehumidifier inspection Performed station housekeeping Station/equipment- Ok | FLAG | stage2_low_confidence | 0.011228 | ML: above threshold (no LLM available) — 0.011 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.011228 | 0 | 0
2026-03 | 2026-03-18 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11673476: Treated sample results (08:20): Free- 0.08, Total- 2.84 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054769 | 0 | 0
2026-03 | 2026-03-30 | Aurora (East) Wellington Pumping Station | CENTRAL | Restarted the Operator Interface Terminal due to Windows Operating System software updates. | FLAG | stage2_low_confidence | 0.0073957 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073957 | 0 | 0
2026-03 | 2026-03-04 | Aurora (East) First Commerce Elevated Tank | CENTRAL | Onsite for station check/collect samples- WO# W11638288, W11638258: Sample results (08:12): Free- 0.06, Total- 2.80 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055881 | 0 | 0
2026-03 | 2026-03-02 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. 14:33 activated Aurora east zone duty. Well 5 forward low flow alarm triggered on start up but checkvalve opened during pump ramp up and alarm cleared. Pumps 5 running at 154.9 l/s and P4 in standby. Rotated to pump 4 in duty to compare electrical draw between both pumps. Found sump pumps in manual off. Placed back in auto and tested with no issues. Entered data into process sheets. No issues found. | FLAG | stage2_low_confidence | 0.015009 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.015009 | 0 | 0
2026-03 | 2026-03-12 | Aurora (East) Wellington Pumping Station | CENTRAL | Vibration readings | FLAG | stage2_low_confidence | 0.021831 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021831 | 0 | 0
2026-03 | 2026-03-10 | Aurora (East) Wellington Pumping Station | CENTRAL | Onsite to complete work orders: 08:40 hrs. Generator inspection and test run. Run hours: 373.3 to 374.8. Fuel level: 1761 L to 1726 L. Pre- inspection. Oil level ok. Coolant level ok. Recirculation pump ok. Battery ok. 08:59 Placed pump 4 and 5 in manual off and notified ROC of work being done. 09:01 Initiated generator test. 09:21 Ran well 5 in manual. Pump and motor inspection ok. Sump pit inpsection ok. Building flood alarm remains OOS with previous work order created W11692965 09:37 Low building temp alarm. Triggered and cleared alarm. JHSC inspection ok. 10:20 placed pump 5 manual off. 10:30 completed generator run with no issues. Ventillation system inspection. Generator room ef-1 tripped after generator run. Reset. No other issues found on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; work order created [maintenance_action]; alarm [control_system] | flood [critical]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; work order created [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-06 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. Pump 4 running in duty at 165 l/s. Pump 5 in standby. Entered data into process sheets. No issues found. | FLAG | stage2_low_confidence | 0.008398 | ML: above threshold (no LLM available) — 0.008 |  | 0.008398 | 0 | 0
2026-03 | 2026-03-13 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. No issues found. | FLAG | stage2_low_confidence | 0.0073169 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073169 | 0 | 0
2026-03 | 2026-03-09 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. No issues found. | FLAG | stage2_low_confidence | 0.0073169 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073169 | 0 | 0
2026-03 | 2026-03-27 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. 07:38 Pump 5 running at 164 l/s. Pump 4 in standby. Entered data into process sheets. No other issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071658 | 0 | 0
2026-03 | 2026-03-23 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. No other issues found. | FLAG | stage2_low_confidence | 0.0075283 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075283 | 0 | 0
2026-03 | 2026-03-23 | Aurora (East) Wellington Pumping Station | CENTRAL | Check leaking backflow Backflow preventer passed, flushed water out of the dump port Not leaking | FLAG | stage2_low_confidence | 0.01809 | ML: above threshold (no LLM available) — 0.018 | leak [infrastructure]; leaking [infrastructure] | 0.01809 | 0 | 0
2026-03 | 2026-03-16 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. Found small drip on backflow prevention assembly. Created W11737138. No other issues found. | FLAG | stage2_low_confidence | 0.014274 | ML: above threshold (no LLM available) — 0.014 | drip [infrastructure] | 0.014274 | 0 | 0
2026-03 | 2026-03-20 | Aurora (East) Wellington Pumping Station | CENTRAL | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. No other issues found. | FLAG | stage2_low_confidence | 0.0075283 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075283 | 0 | 0
2026-03 | 2026-03-30 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Informed ROC. Onsite to install and setup ultrasonic flowmeter. Informed ROC, armed the building and left the site. | FLAG | stage2_low_confidence | 0.0090199 | ML: above threshold (no LLM available) — 0.009 |  | 0.0090199 | 0 | 0
2026-03 | 2026-03-16 | Aurora (East) Wellington Pumping Station | CENTRAL | On site to investigate malfunctioning building flood alarm. ROC notified. Found float switch to be faulty. Replaced float and tested with assistance from Ian Williams from PCS. Building flood alarm now functional. Work completed. Building flood alarm acknowledged and reset. ROC notified. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; fault [equipment_failure]; alarm [control_system] | flood [critical]; fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite for station check/collect samples- WO# W11706313, W11706283: Sample results (13:28): Free- 0.09, Total- 2.84 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055881 | 0 | 0
2026-03 | 2026-03-18 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Comprehensive House Cleaning PM: completed | FLAG | stage2_low_confidence | 0.013406 | ML: above threshold (no LLM available) — 0.013 |  | 0.013406 | 0 | 0
2026-03 | 2026-03-04 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite for station check/collect samples- WO# W11638288, W11638258: Sample results (13:12): Free- 0.07, Total- 3.02 * Adjusted total analyzer from 2.80 to 3.02 based on multiple grabs (3.02, 3.02, 3.04) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058064 | 0 | 0
2026-03 | 2026-03-12 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite to complete assigned work orders- informed ROC: H/S inspection Low/high temp test Sump system inspection Depolox analyzer maintenance Manual valve exercise/inspection Drain valve exercise/inspection Station/equipment- Ok | FLAG | stage2_low_confidence | 0.010029 | ML: above threshold (no LLM available) — 0.01 | work order [maintenance_action] | 0.010029 | 0 | 0
2026-03 | 2026-03-18 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO W11673476: Sample results (13:45): Free- 0.08, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052505 | 0 | 0
2026-03 | 2026-03-25 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11690776: Sample results (09:00): Free- 0.09, Total- 2.82 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052756 | 0 | 0
2026-03 | 2026-03-11 | Aurora (North) Orchard Heights Elevated Tank | CENTRAL | Onsite for station check/collect sample- WO# W11657608: Treated sample results (14:10): Free- 0.04, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054769 | 0 | 0
2026-03 | 2026-03-30 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Restarted the Operator Interface Terminal due to Windows Operating System software updates. | FLAG | stage2_low_confidence | 0.0073957 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073957 | 0 | 0
2026-03 | 2026-03-28 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | TESTING NEW MAXIMO SYSTEM NOT REAL ENTRY PLEASE IGNORE REVISION 1 REVISION 2 | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-05 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Onsite to complete work orders: Notified ROC of work being done. Topped up ammonia tank 2 from 222 L to 1270L. Joint health and safety inspection. Found ammonia room, chlorine vestibule and reservoir basement emergency lights OOS. Notified team lead. Sump pit inspection. Dehumidifier cleaning and inpsection. Ammonia peristaltic pump 1 and pump 2 inspection. Pump 1 max pump rate 1520 ml/min. P2 max pump rate 1460 ml/min. Adjusted SCADA setpoints to match. 11:22 deactivated chloramine dosing system. 11:41 Chlorine leak detection test. Gas leak Alarm triggered using tester. Halogen shut off system actuated. Bank 2 actuators B shorted and D timed out. D failed to close. Retested and all acutators worked without issues. 11:47 Repopened chlorine cylinders and placed chemical systems back in auto. No issues remain. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; gas leak [critical]; failed [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; leak [infrastructure] | emergency [critical]; gas leak [critical]; failed [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-31 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and reservoir sampling. W117705787 and W11705378. Reservoir flow at 358 l.s and rechloramination boosting is on. Reservoir level at 46%. Topped up ammonia tank 1. Replaced chemscan Ammonia reagent. Verified residuals (mg/l): 10:12 Pre-injection/outlet grabs: Free grab: 0.08. Depolox 5: 0.05. Total grab: 1.64 Micro2000: 1.61 Chemscan: 1.61. Monochloramine grab: 1.51. Chemscan: 1.59. Free ammonia grab: 0.07. Chemscan: 0.08. Total ammonia grab: 0.37. Chemscan: 0.39. Nitrite: 0.003. temperature: 6.6 celsius. 10:23 Post-injection chlorine grabs. Free grab: 0.03. Depolox 5: 0.0\3. Total grab: 3.26 Micro2000: 3.26. Chemscan: 3.09. Monochloramine grab: 2.73. Chemscan: 2.91. Adjsuted chemscan to match grab. Free ammonia grab: 0.04. Chemscan: 0.02. Total ammonia grab: 0.58. Chemscan: 0.56. Recorded data into process sheets. No issues found on site. | FLAG | stage2_low_confidence | 0.014314 | ML: above threshold (no LLM available) — 0.014 | oos [equipment_failure] | 0.014314 | 0 | 0
2026-03 | 2026-03-05 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | -Performed ammonia system inspection | FLAG | stage2_low_confidence | 0.012966 | ML: above threshold (no LLM available) — 0.013 |  | 0.012966 | 0 | 0
2026-03 | 2026-03-11 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and sampling. W11656795. 11:36 outlet flow at 414 L/s. Rechloramination boosting on. Reservoir level at 51%. Verified residuals (mg/l): 11:45 Pre-injection/outlet grabs. Collected sample. Free grab: 0.08. Depolox 5: 0.06. Total grab: 1.64. Micro2000: 1.54 Chemscan: 1.60. Monochloramine grab: 1.54. Chemscan: 1.58. Free ammonia grab: 0.07. Chemscan: 0.08. Total ammonia grab: 0.37. Chemscan: 0.39. 11:55 Post-injection chlorine grabs. Free grab: 0.02. Depolox 5: 0.04. Total grab: 3.26 Micro2000: 3.19. Chemscan: 3.31. Monochloramine grab: 2.76. Chemscan: 2.90. Free ammonia grab: 0.01. Chemscan: 0.04. Total ammonia grab: 0.56. Chemscan: 0.58. Calculated ammonia dosage is since March 9th is 0.18 mg/l. Total ammonia dose calculated on SCADA is 0.29. Post injection ammonia grab: 0.01 while ammonia pump 2 is running. 12:10 rotated to ammonia pump 1. Disabled duty auto rotate. 12:30 retested free ammonia on post injection. Grab: 0.05. Chemscan: 0.05. Completed drawdowns for both pumps. p1 max drawdown 1490 ml/min. Adjusted SCADA to match from 1520 ml/min. Will re-evaluate next station check. Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. 10:29 outlet flow at 0 L/s. Rechloramination boosting off. Reservoir level at 64%. Topped up ammonia tank 2. Topped up micro2000 pre injection total analyzer acetate reagent. Verified residuals (mg/l): 10:50 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.06. Total grab: 1.65 Micro2000: 1.58 Chemscan: 1.65. Monochloramine grab: 1.55. Chemscan: 1.59. Free ammonia grab: 0.07. Chemscan: 0.07. Total ammonia grab: 0.37. Chemscan: 0.44. 11:02 Post-injection chlorine grabs. Free grab: 0.03. Depolox 5: 0.04. Total grab: 3.24 Micro2000: 3.20. Chemscan: 3.32. Monochloramine grab: 2.85. Chemscan: 3.03. Adjusted to match grab. Free ammonia grab: 0.08. Chemscan: 0.07. Total ammonia grab: 0.64. Chemscan: 0.59. With ammonia p1 in duty calculated ammonia dosage is 0.28 mg/l. SCADA Ammonia dose is 0.29 mg/l. Rotated to ammonia pump 2 in duty 1 and will evaluate ammonia p2 performance on next sation check . Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-06 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. 12:23 outlet flow at 329 L/s. Rechloramination boosting on. Reservoir level at 48%. Verified residuals (mg/l): 12:25 Pre-injection/outlet grabs. Collected samples. Free grab: 0.02 Depolox 5: 0.06. Total grab: 1.57. Micro2000: 1.59 Chemscan: 1.61. Monochloramine grab: 1.49 Chemscan: 1.58. Free ammonia grab: 0.07. Chemscan: 0.09. Total ammonia grab: 0.37. Chemscan: 0.41. 12:30 Post-injection chlorine grabs. Free grab: 0.04/0.04/0.05. Depolox 5: 0.16. Adjusted to match grab average Total grab: 3.30/3.26/3.26. Micro2000: 3.18. Chemscan: 3.29. adjusted to match grab average. Monochloramine grab: 2.80 Chemscan: 2.78. Free ammonia grab: 0.05. Chemscan: 0.07. Total ammonia grab: 0.60. Chemscan: 0.61. Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-02 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. 11:16 outlet flow at 0 L/s. Rechloramination boosting off. Reservoir level at 87%. Topped up ammonia tank 1. Generated W11700364 to replaced the ammonia mixer switch as its no longer working to turn off the mixer. Unplugged the mixer from recepticle once mixing was completed. received 20 chlorine cylinders and removed 20 empty cylinders. Verified residuals (mg/l): 11:35 Pre-injection/outlet grabs. Free grab: 0.09 Depolox 5: 0.06. Total grab: 1.62/1.61/1.62 Micro2000: 1.70 Chemscan: 1.62. Adjusted micro2000 to match grab averages. Monochloramine grab: 1.54 Chemscan: 1.60. Free ammonia grab: 0.10. Chemscan: 0.06. Total ammonia grab: 0.41. Chemscan: 0.35. 11:42 Post-injection chlorine grabs. Rechloramination has stopped dosing. Free grab: 0.06. Depolox 5: 0.01. Total grab: 1.62. Micro2000: 1.67. Chemscan: 1.67 Monochloramine grab: 1.57 Chemscan: 1.58. Free ammonia grab: 0.07. Chemscan: 0.11. Total ammonia grab: 0.38. Chemscan: 0.50. No other new issues found on site. | FLAG | stage2_low_confidence | 0.05847 | ML: above threshold (no LLM available) — 0.058 | oos [equipment_failure]; plugged [infrastructure] | 0.05847 | 0 | 0
2026-03 | 2026-03-04 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and sampling. W11637647 and W11637218. 10:14 outlet flow at 400 L/s. Rechloramination boosting on. Reservoir level at 49%. Verified residuals (mg/l): 10:18 Pre-injection/outlet grabs. Collected samples. Free grab: 0.07 Depolox 5: 0.06. Total grab: 1.75. Micro2000: 1.68 Chemscan: 1.71. Monochloramine grab: 1.58 Chemscan: 1.64. Free ammonia grab: 0.08. Chemscan: 0.07. Total ammonia grab: 0.39. Chemscan: 0.37. 10:38 Post-injection chlorine grabs. Free grab: 0.03. Depolox 5: 0.07. Total grab: 3.30. Micro2000: 3.23. Chemscan: 3.29. Monochloramine grab: 2.86 Chemscan: 2.95. Free ammonia grab: 0.04. Chemscan: 0.05. Total ammonia grab: 0.61. Chemscan: 0.59. Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-09 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. Replaced chlorine cylinder bank B with Joe DeMarco. Topped up ammonia tank 1, 222L to 12767 L. 13:53 outlet flow at 412 L/s. Rechloramination boosting on. Reservoir level at 55%.. Verified residuals (mg/l): 13:54 Pre-injection/outlet grabs. Collected samples. Free grab: 0.10 Depolox 5: 0.06. Total grab: 1.63. Micro2000: 1.66 Chemscan: 1.60. Monochloramine grab: 1.55. Chemscan: 1.58. Free ammonia grab: 0.07. Chemscan: 0.08. Total ammonia grab: 0.37. Chemscan: 0.40. 14:02 Post-injection chlorine grabs. Free grab: 0.03. Depolox 5: 0.04. Total grab: 3.24 Micro2000: 3.29. Chemscan: 3.31. Monochloramine grab: 2.82. Chemscan: 2.79. Free ammonia grab: 0.03. Chemscan: 0.05. Total ammonia grab: 0.59. Chemscan: 0.59. Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and to collect sample. W11672681. 12:28 outlet flow at 450 L/s. Rechloramination boosting on. Reservoir level at 54%. Verified residuals (mg/l): 12:41 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.05. Total grab: 1.62 Micro2000: 1.63 Chemscan: 1.61. Monochloramine grab: 1.51. Chemscan: 1.57. Free ammonia grab: 0.12. Chemscan: 0.10. Total ammonia grab: 0.41. Chemscan: 0.40. 12:53 Post-injection chlorine grabs. Free grab: 0.06. Depolox 5: 0.04. Total grab: 3.26 Micro2000: 3.28. Chemscan: 3.31. Monochloramine grab: 2.77. Chemscan: 2.70 Free ammonia grab: 0.02. Chemscan: 0.06. Total ammonia grab: 0.57. Chemscan: 0.62. Adjusted chlorine/ammonia ratio from 4.8 to 4.7. No issues found on site. | FLAG | stage2_low_confidence | 0.011054 | ML: above threshold (no LLM available) — 0.011 | oos [equipment_failure] | 0.011054 | 0 | 0
2026-03 | 2026-03-16 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Replaced left chlorine cylinder bank with Kyle Rae. | FLAG | stage2_low_confidence | 0.013918 | ML: above threshold (no LLM available) — 0.014 |  | 0.013918 | 0 | 0
2026-03 | 2026-03-16 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. 10:20 outlet flow at 389 L/s. Rechloramination boosting off. Reservoir level at 55%. Topped up ammonia tank 1. Topped up chemscan sulphuric acid and potassium iodine reagent. Verified residuals (mg/l): 11:07 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.06. Total grab: 1.62 Micro2000: 1.67 Chemscan: 1.59. Monochloramine grab: 1.51. Chemscan: 1.59. Free ammonia grab: 0.08. Chemscan: 0.07. Total ammonia grab: 0.37. Chemscan: 0.40. 11:20 Post-injection chlorine grabs. Free grab: 0.04. Depolox 5: 0.04. Total grab: 3.24 Micro2000: 3.23. Chemscan: 3.10. Monochloramine grab: 2.79. Chemscan: 2.82 Free ammonia grab: 0.11. Chemscan: 0.06 Adjusted to match grabs. Total ammonia grab: 0.66. Chemscan: 0.57. Adjusted to match grabs. Adjusted chlorine/ammonia ratio from 4.7 to 4.8. With ammonia p2 in duty calculated ammonia dosage is 0.28 mg/l. SCADA Ammonia dose is 0.29 mg/l. No issues found with ammonia pumps. Placed ammonia pump duty back to all stop rotate setting. Kyle Rae on site to repair ammonia tank mixer 1 switch. No other new issues found on site. | FLAG | stage2_low_confidence | 0.062077 | ML: above threshold (no LLM available) — 0.062 | oos [equipment_failure]; repair [maintenance_action]; scada [control_system] | 0.062077 | 0 | 0
2026-03 | 2026-03-21 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | 21:34 ROC informed me that chlorine booster pump 2 failed to start. Roc attempted to restart with no luck. 21:42 remotely restarted chlorine train 2 with no issues. Dosing appears normal. Notified Roc.. | FLAG | stage2_low_confidence | 0.0096209 | ML: above threshold (no LLM available) — 0.01 | failed [equipment_failure]; oos [equipment_failure] | 0.0096209 | 0 | 0
2026-03 | 2026-03-20 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. 07:38 outlet flow at 0 L/s. Rechloramination boosting of. Reservoir level at 87%. Aurora Duty has just activated and station flow will be starting shortly once vavle opens. Topped up ammonia tank 2. Topped up micro2000 KI and acetate reagents for pre and post injection analyzers. Verified residuals (mg/l): 07:41 Pre-injection/outlet grabs. Collected sample. Free grab: 0.07. Depolox 5: 0.06. Total grab: 1.60 Micro2000: 1.52 Chemscan: 1.61. Monochloramine grab: 1.45. Chemscan: 1.54. Free ammonia grab: 0.08. Chemscan: 0.06. Total ammonia grab: 0.36. Chemscan: 0.38. 08:38 Post-injection chlorine grabs. Free grab: 0.05. Depolox 5: 0.04. Total grab: 3.24 Micro2000: 3.26. Chemscan: 3.31. Monochloramine grab: 2.84. Chemscan: 2.90. Free ammonia grab: 0.06. Chemscan: 0.09. Adjusted to match grab. Total ammonia grab: 0.66. Chemscan: 0.66. No issues found on site. | FLAG | stage2_low_confidence | 0.024451 | ML: above threshold (no LLM available) — 0.024 | oos [equipment_failure] | 0.024451 | 0 | 0
2026-03 | 2026-03-27 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | on site to troubleshoot the uncommanded starts and the pumps inability to start locally. initially we found that the contactor was making a very audible buzzing noise. i took the contactor out and found that there was a damaged part inside it and binding the movement of the contactor and not allowing it to close. i repaired the part and tested it with Donny. no issues were present during our testing and pump has run for approximately 20mins. under direction of oic | FLAG | stage2_low_confidence | 0.19996 | ML: above threshold (no LLM available) — 0.2 | noise [equipment_failure]; repair [maintenance_action] | 0.19996 | 0 | 0
2026-03 | 2026-03-17 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Onsite to receive delivery of ammonia sulphate. 48 bags delivered. | FLAG | stage2_low_confidence | 0.011345 | ML: above threshold (no LLM available) — 0.011 |  | 0.011345 | 0 | 0
2026-03 | 2026-03-26 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Onsite to test chlorine booster pump 2. Unconnected stop alarm triggered trying to run pump remotely. Pump won?t start locally. 11:50 Put chlorine pump 1 back in service and notified roc. | FLAG | stage2_low_confidence | 0.028205 | ML: above threshold (no LLM available) — 0.028 | oos [equipment_failure]; alarm [control_system] | 0.028205 | 0 | 0
2026-03 | 2026-03-05 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | Onsite you complete work orders: 13:17 Placed chlorine/ammonia dosing system offline. Aurora central duty is currently not active and outlet flow is 0 l/s. Siemens depolox 5 and micro2000 inspection. chemscan analyzer maintenance. No issues found. 13:40 verified analyzers: Pre injection free: 0.02. Analyzer: 0.06. Pre injection total: 1.65. Micro2000: 1.68. Chemscan: 1.67. 13:45 Post injection free: 0.02. Analyzer: 0.01. Post injection total: 1.66. Micro2000: 1.65. Chemscan: 1.65. 13:57 Chemical storage tank inspection. Tested flood alarm. Chlorine system inspection. Tested vacuum. Placed all systems back to auto once complete. No new issues found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check. 10:20 outlet flow at 0 L/s. Rechloramination boosting of. Reservoir level at 51%. Topped up ammonia tank 1. Changed chlorine cylinder bank 2 with Ben Hess. 11:00 With Ben Hess and Chris scott tested chlorine dosing system and lo vaccum alarms. Found alarms failing to trigger. Ran chlorine sytem to storm and not into system after placing dechlorination pucks at outlet. Off gassing at outlet triggerd chlorine briefly triggered chlorinel leak detection hihi alarm with detector spiking at 2.90 PPM. Verified chlorine booster pump 2 running with no issues. Verified residuals (mg/l): 12:05 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.05. Total grab: 1.62 Micro2000: 1.52 Chemscan: 1.65. Monochloramine grab: 1.56. Chemscan: 1.61. Free ammonia grab: 0.06.. Chemscan: 0.07. Total ammonia grab: 0.37 Chemscan: 0.37. 12:15 Post-injection chlorine grabs. Free grab: 0.04. Depolox 5: 0.00. Total grab: 1.63 Micro2000: 1.65. Chemscan: 1.65 Monochloramine grab: 1.54. Chemscan: 1.56. Free ammonia grab: 0.08. Chemscan: 0.12. Total ammonia grab: 0.38. Chemscan: 0.53. adjusted to match grab. No issues found on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-25 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | 13:52 received call from roc (Christian). Chlorine pump 2 failed to start. Station unable to chlorine boost. 13:58 attempted to start remotely. Failed again. 13:59 placed chlorine train 1 back in service. Lowered chlorine target setpoint to 3.00 mg/L as chlorinate is smaller. | FLAG | stage2_low_confidence | 0.014009 | ML: above threshold (no LLM available) — 0.014 | failed [equipment_failure]; oos [equipment_failure] | 0.014009 | 0 | 0
2026-03 | 2026-03-25 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and reservoir sampling. W11690064 08:16 outlet flow at 456 L/s. Rechloramination boosting on. Reservoir level at 44%. Verified residuals (mg/l): 08:35 Pre-injection/outlet grabs. Collected sample. Free grab: 0.05. Depolox 5: 0.05. Total grab: 1.68 Micro2000: 1.72 Chemscan: 1.66. Monochloramine grab: 1.54. Chemscan: 1.59. Free ammonia grab: 0.0. Chemscan: 0.07. Total ammonia grab: 0.37 Chemscan: 0.38. 08:45 Post-injection chlorine grabs. Free grab: 0.07. Depolox 5: 0.03. Total grab: 3.24/3.26/3.26 Micro2000: 3.06. Chemscan: 3.20 Adjusted micro2000 to match grab. Monochloramine grab: 2.80. Chemscan: 2.60. Adjusted chemscan to match grab. Free ammonia grab: 0.02. Chemscan: 0.08. Adjusted chemscan to match grab. Total ammonia grab: 0.58. Chemscan: 0.56. No issues found on site. Recorded readings in process sheets. | FLAG | stage2_low_confidence | 0.026145 | ML: above threshold (no LLM available) — 0.026 | oos [equipment_failure] | 0.026145 | 0 | 0
2026-03 | 2026-03-18 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and to collect sample. W11672681. 12:28 outlet flow at 450 L/s. Rechloramination boosting on. Reservoir level at 54%. Topped up ammonia tank 2. Verified residuals (mg/l): 12:41 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.05. Total grab: 1.62 Micro2000: 1.63 Chemscan: 1.61. Monochloramine grab: 1.51. Chemscan: 1.57. Free ammonia grab: 0.12. Chemscan: 0.10. Total ammonia grab: 0.41. Chemscan: 0.40. 12:53 Post-injection chlorine grabs. Free grab: 0.06. Depolox 5: 0.04. Total grab: 3.26 Micro2000: 3.28. Chemscan: 3.31. Monochloramine grab: 2.77. Chemscan: 2.70 Free ammonia grab: 0.02. Chemscan: 0.06. Total ammonia grab: 0.57. Chemscan: 0.62. Adjusted chlorine/ammonia ratio from 4.8 to 4.7. No issues found on site. | FLAG | stage2_low_confidence | 0.010351 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure] | 0.010351 | 0 | 0
2026-03 | 2026-03-25 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | 14:20 onsite to respond to chlorine booster pump 1 failing to start. Stopped all chemical dosing. Valved chlorinator 2 to chlorine booster pump 1. Changed SCADA chlorine cfg: to booster pump 1 to chlorinator 2 and restarted dosing. Adjusted chlorine target setpoint to 3.30. Placed chlorine booster p2 in local. Created work order for maintenance to investigate chlorine booster pump 2. | FLAG | stage2_low_confidence | 0.071564 | ML: above threshold (no LLM available) — 0.072 | oos [equipment_failure]; work order [maintenance_action]; scada [control_system] | 0.071564 | 0 | 0
2026-03 | 2026-03-31 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | On site for station check and sampling. W117705787 and W11705378.. 15:00 Tower level at 46% and draining at 0 l/s. 15:01 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.04. Analyzer: 0.05. Total chlorine grab: 1.98. Analyzer: 1.91. Monochloramine: 1.93. Free ammonia: 0.06. Total ammonia: 0.44. Nitrite: 0.004. Replaced micro 2000 analyzer acetate reagent. No issues on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041592 | 0 | 0
2026-03 | 2026-03-16 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site to investigate ammonia mixer switch. Found switch cover plate to be damaged. Replaced cover plate and tested operation. | FLAG | stage2_low_confidence | 0.012941 | ML: above threshold (no LLM available) — 0.013 |  | 0.012941 | 0 | 0
2026-03 | 2026-03-27 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | On site for station check and chlorine booster pump 2 testing with Tyler Z. 09:26 Notified ROC to place bathurst/wellington valve manual off. Set chlorine train and valving back to normal ops mode to allow tyler to test/repair chlorine pump 2. No flow from reservoir and rechloramination boosting is off. Reservoir level at 52%. Topped up ammonia tank 2. Verified residuals (mg/l): 10:15 Pre-injection/outlet grabs: Free grab: 0.06. Depolox 5: 0.05. Total grab: 1.65 Micro2000: 1.65 Chemscan: 1.58. Monochloramine grab: 1.53. Chemscan: 1.61. Free ammonia grab: 0.08. Chemscan: 0.07. Total ammonia grab: 0.38 Chemscan: 0.40. 10:30 Post-injection chlorine grabs. Free grab: 0.02. Depolox 5: 0.00. Total grab: 1.65 Micro2000: 1.69. Chemscan: 1.65. Monochloramine grab: 1.53. Chemscan: 1.62. Free ammonia grab: 0.07. Chemscan: 0.09. Total ammonia grab: 0.37. Chemscan: 0.48. Adjusted to match grab. 10:52 placed Bathurst/wellington valve back to auto, placed chlorine train 1 back in service. Set chlorine dosage point to 2.85 mg/l. 11:22 hours. Tyler repaired contactor to chlorine booster pump 2. Placed back in servcie. Chlorine train 1 back to manual off in standby. Chlorine train dosing in normal mode. Chlorine dosage setpoint back to 3.30 mg/l. No issues found on site. | FLAG | stage2_low_confidence | 0.081312 | ML: above threshold (no LLM available) — 0.081 | oos [equipment_failure]; repair [maintenance_action] | 0.081312 | 0 | 0
2026-03 | 2026-03-05 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | -Finished the following work orders *Tested low temp alarm *Valve exercises *Depolox analyzer maintenance *Tested portable generator *Heat trace inspection *H&S inspection | FLAG | stage2_low_confidence | 0.015301 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action]; alarm [control_system] | 0.015301 | 0 | 0
2026-03 | 2026-03-04 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | On site for station check and sampling. W11637647 and W11637218.. 11:28 Tower level at 56% and draining. 11:34 Verified chlorine analyzer (mg/l) and collected samples. Free chlorine grab: 0.05. Analyzer: 0.01. Total chlorine grab: 2.16 analyzer: 2.19. Nitrite grab: 0.003 Free ammonia: 0.07 Total ammonia: 0.46. Monochloramine: 1.98. Temperature: 4.3 celsius. pH: 8.03. No issues on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038367 | 0 | 0
2026-03 | 2026-03-11 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | On site for station check and sampling. W11656795. 13:38 Tower level at 60% and draining. 11:42 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.03. Analyzer: 0.00. Total chlorine grab: 2.17. Analyzer: 2.12. No issues on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006176 | 0 | 0
2026-03 | 2026-03-25 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | On site for station check and sampling. W11690064. 11:03 Tower level at 63% and draining at 0 l/s. 11:10 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.03. Analyzer: 0.05. Total chlorine grab: 2.12. Analyzer: 2.09. Monochloramine: 1.94. Free ammonia: 0.06. Total ammonia: 0.44. No issues on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004987 | 0 | 0
2026-03 | 2026-03-18 | Aurora (Southwest) Allenvale Elevated Tank | CENTRAL | On site for station check and sampling. W11672681. 09:27 Tower level at 60% and draining at 5.2 l/s. 09:35 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.08. Analyzer: 0.07. Total chlorine grab: 2.13. Analyzer: 2.13. Monochloramine: 1.97. Free ammonia: 0.06. Total ammonia: 0.45. Nitrite: 0.004 pH: 7.99 Temp: 3.8 celsius. No issues on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035571 | 0 | 0
2026-03 | 2026-03-31 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/collect samples- WO# W11706313, W11706283: Sample results (12:25): Free- 0.09, Total- 3.00 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055881 | 0 | 0
2026-03 | 2026-03-02 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-03 | 2026-03-30 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Restarted the Operator Interface Terminal due to Windows Operating System software updates. | FLAG | stage2_low_confidence | 0.0073957 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073957 | 0 | 0
2026-03 | 2026-03-06 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-03 | 2026-03-12 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite to complete assigned work orders- informed ROC: H/S inspection Low/high temp test Ventilation inspection Depolox analyzer maintenance Pump and motor inspection Manual valve exercise/inspection Dehumidifier inspection Generator test: Start time- 09:46 Stop time- 10:53 Start hours- 205.8 Stop hours- 206.9 Start fuel- 2,460 L (85cm) Stop fuel- 2,450 L (84cm) Pre inspection completed prior to generator test run- no abnormalities * Generator operating stats (under load P4): 1798 rpm 603 V 60 Hz 58 A 444 kpa- oil pressure 87 C- coolant temp Placed generator back into auto once test run completed- no abnormalities during test/inspection * Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.00061952 | 0 | 0
2026-03 | 2026-03-04 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/collect samples- WO# W11638288, W11638258: Sample results (12:30): Free- 0.09, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055881 | 0 | 0
2026-03 | 2026-03-13 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-03 | 2026-03-11 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/collect sample- WO# W11657608: Treated sample results (13:34): Free- 0.06, Total- 3.04 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054769 | 0 | 0
2026-03 | 2026-03-27 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-03 | 2026-03-20 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for CMU5. Free AIT loosing electrolyte rapidly Informed ROC Put AITs to cal mode on scada Removed electrode holder and found membrane to have popped out of socket causing the leak. Replaced membrane and filled holder with new electrolyte Replaced assembly and put back in service Found very low flow to Free AIT. Grit not swirling in sample cell and very low flow to drain. Flushed main sample line. Lots of flow and pressure. Removed pressure reducing valve, disassembled and cleaned. Returned to service and adjusted. Flow much better now. Took multiple grabs for Free AIT and adjusted G =0.07mg/L A =0.07mg/L Removed AITs from cal mode Informed ROC, armed building and left site | FLAG | stage2_low_confidence | 0.11911 | ML: above threshold (no LLM available) — 0.119 | oos [equipment_failure]; scada [control_system]; leak [infrastructure] | 0.11911 | 0 | 0
2026-03 | 2026-03-25 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/collect sample- WO# W11690776: Sample results (08:28): Free- 0.05, Total- 2.96 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052756 | 0 | 0
2026-03 | 2026-03-31 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. W117705787 and W11705378. 12:58 reservoir inlet at 59 l/s. Rechloramination dosing on. Zone 3 pumps 1 and 2 in standby. Topped up ammonia tank 2. Verified analyzer residuals (mg/l): 13:25 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.03. Total Chlorine grab: 1.85 CL17: 1.88. Chemscan: Monochloramine grab: 1.69 Chemscan: 1.70 Free ammonia grab: 0.11. Chemscan: 0.10 Total ammonia: 0.45. Chemsca: 0.46. 13:30 Post-injection grabs. Free chlorine grab: 0.03. Analyzer: 0.06. Total Chlorine grab: 2.68 CL17: 2.61. Chemscan: 2.66. 13:40 Outlet grab Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.30 Analyzer: 2.37 Monochloramine grab: 2.08 Free ammonia grab: 0.05 Total ammonia: 0.45 Nitrite: 0.003. 13:40 Zone 3 grab: Free chlorine: 0.02. Analyzer: 0.04. Total Chlorine: 2.30. Analyzer: 2.31 Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.002275 | 0 | 0
2026-03 | 2026-03-09 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-03 | 2026-03-20 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Replaced depolox KI reagent * Verified analyzers Depolox reagents- Ok Performed station housekeeping Noticed potential crack in depolox free probe- electrolyte gel draining quickly after filling. Informed instrumentation- will create work order to further investigate | FLAG | stage2_low_confidence | 0.017216 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action] | 0.017216 | 0 | 0
2026-03 | 2026-03-18 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check/collect sample- WO# W11673476: Sample results (13:05): Free- 0.01, Total- 3.18 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052756 | 0 | 0
2026-03 | 2026-03-16 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-03 | 2026-03-23 | Aurora Orchard Heights Pumping Station & Reservoir | CENTRAL | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0078188 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078188 | 0 | 0
2026-03 | 2026-03-31 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Restarted the operator interface terminal due to windows operating system updates. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070878 | 0 | 0
2026-03 | 2026-03-13 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. 09:10 reservoir outlet at 32 l/s. Rechloramination dosing off. Zone 3 pumps 1 and 2 in standby. Replaced outlet total chlorione analyzer reagent. Verified analyzer residuals (mg/l): 09:36 Pre-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.04. Total Chlorine grab: 2.26 CL17: 2.33. Chemscan: 2.41. Monochloramine grab: 2.06 Chemscan: 2.02 Free ammonia grab: 0.06. Chemscan: 0.03. Total ammonia: 0.47. Chemscan: 0.49 09:41 Post-injection grabs. Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 2.36 CL17: 2.39. Chemscan: 2.50 Monochloramine grab: 2.05 Chemscan: 2.04 Free ammonia grab: 0.07. Chemscan: 0.02 Total ammonia: 0.47. Chemscan: 0.51. 09:45 Outlet grab and sample collected. Free chlorine grab: 0.03. Analyzer: 0.03. Total Chlorine grab: 2.38. Analyzer: 2.35. 09:50 Zone 3 grab: Free chlorine: 0.03. Analyzer: 0.04. Total Chlorine: 2.38. Analyzer: 2.30. Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.024099 | ML: above threshold (no LLM available) — 0.024 | fault [equipment_failure]; faulted [equipment_failure]; work order [maintenance_action]; sample collected [regulatory] | 0.024099 | 0 | 0
2026-03 | 2026-03-06 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check/ 07:45 Reservoir draining at 30 l/s. Rechloramination dosing off. Zone 3 pumps 1 and 2 in standby. Topped up ammonia tank 1. Verified analyzer residuals (mg/l): 08:36.Pre-injection grabs: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.40 CL17: 2.36. Chemscan: 2.46. Monochloramine grab: 2.09. Chemscan: 2.04 Free ammonia grab: 0.06. Chemscan: 0.04. Total ammonia: 0.48. Chemscan: 0.47. 09:06 Post-injection grabs. Chloriamination dosing system now running. Free chlorine grab: 0.05. Analyzer: 0.06. Total Chlorine grab: 2.66. CL17: 2.56. Chemscan: 2.47. Monochloramine grab: 2.28. Chemscan: 2.24 Free ammonia grab: 0.07. Chemscan: 0.02. Total ammonia: 0.52. Chemscan: 0.60. 09:09 Outlet grab: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.32. Analyzer: 2.38. 09:13 Zone 3 grab: Free chlorine: 0.07. Analyzer: 0.04. Total Chlorine: 2.32. Analyzer: 2.33 Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031896 | 0 | 0
2026-03 | 2026-03-10 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite to complete work orders: Notified roc of work. 13:56 placed all chemical dosing systems offline. 13:59 tested chlorine emergency shut off valves. Ok. 14:00 tested Chlorine leak detection. Ok 14:04 turned dosing system back online. No issues found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action]; leak [infrastructure] | emergency [critical]; work order [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-04 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check and sampling. W11637647 and W11637218. 08:25 Reservoir filling at 71 l/s. Rechloramination dosing on. Zone 3 pumps both in standby. Verified analyzer residuals (mg/l): 08:35.Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 1.83 CL17: 1.86. Chemscan: 1.88. 08:42 Post-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.06. Total Chlorine grab: 2.56 CL17: 2.61. Chemscan: 2.69. 08:57 Outlet grab: Free chlorine grab: 0.02. Analyzer: 0.03 Total Chlorine grab: 2.36. Analyzer: 2.39 monochloramine grab: 2.08. Free ammonia grab: 0.04. Total Ammonia: 0.45. Nitirite: 0.002. Temperature: 4.9 Celsius. pH: 7.98. 09:13 Zone 3 grab: Free chlorine: 0.02 Analyzer: 0.04 Total Chlorine: 2.36. Analyzer: 2.39 Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0021935 | 0 | 0
2026-03 | 2026-03-02 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. 07:52 Reservoir filling at 48 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 73%. EF-01 overload tripped. Reset with no issues. Verified analyzer residuals (mg/l): 08:50 Pre-injection grabs: Free chlorine grab: 0.05. Analyzer: 0.03. Total Chlorine grab: 1.81 CL17: 1.87. Chemscan: 1.89. Monochloramine grab: 1.65 Chemscan: 1.69. Free ammonia grab: 0.08. Chemscan: 0.06. Total Ammonia: 0.41. Chemscan: 0.45. 09:00 Post-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.06. Total Chlorine grab: 2.54 CL17: 2.52. Chemscan: 2.57. monochloramine grab: 2.18. Chemscan: 2.17. Free ammonia grab: 0.05. Chemscan: 0.02. Total Ammonia: 0.48. Chemscan: 0.52. 09:13 Outlet grab: Free chlorine grab: 0.02. Analyzer: 0.03 Total Chlorine grab: 2.36. Analyzer: 2.39 09:13 Zone 3 grab: Free chlorine: 0.02 Analyzer: 0.04 Total Chlorine: 2.36. Analyzer: 2.39 Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.0090178 | ML: above threshold (no LLM available) — 0.009 | tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure] | 0.0090178 | 0 | 0
2026-03 | 2026-03-09 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. 10:30 reservoir filling at 37 l/s. Rechloramination dosing on. Zone 3 pumps 1 running at 69.9 l/s. Pump 3 in standby. replaced post injection total chlorine analyzer reagent. Verified analyzer residuals (mg/l): 10:42 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 1.83 CL17: 1.85. Chemscan: 1.87. Monochloramine grab: 1.66. Chemscan: 1.66 Free ammonia grab: 0.09. Chemscan: 0.13. Total ammonia: 0.42. Chemscan: 0.46. 10:56 Post-injection grabs. Rechloramination boosting off now. Free chlorine grab: 0.06. Analyzer: 0.03. Total Chlorine grab: 1.84. CL17: 1.89. Chemscan: 1.9. Monochloramine grab: 1.66. Chemscan: 1.71 Free ammonia grab: 0.11. Chemscan: 0.07. Total ammonia: 0.44. Chemscan: 0.51. 11:08 Outlet grab: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.42. Analyzer: 2.37. 11:10 Zone 3 grab: Free chlorine: 0.07. Analyzer: 0.03. Total Chlorine: 2.42. Analyzer: 2.37 Found EF-1 faulted again. Created work order for maintenance to investigate. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.018183 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action] | 0.018183 | 0 | 0
2026-03 | 2026-03-11 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. 07:40 reservoir filling at 24 l/s. Rechloramination dosing off. Zone 3 pumps 1 running at 70 l/s. Pump 2 in standby. Verified analyzer residuals (mg/l): 07:47 Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.05. Total Chlorine grab: 2.32 CL17: 2.31. Chemscan: 2.40. 07:58 Post-injection grabs. Rechloramination boosting off now. Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.34 CL17: 2.37. Chemscan: 2.47 08:04 Outlet grab and sample collected. Free chlorine grab: 0.05. Analyzer: 0.04. Total Chlorine grab: 2.32. Analyzer: 2.37. Monochloramine grab: 2.06 Free ammonia grab: 0.06. Total ammonia: 0.47. Nitrite: 0.003. pH: 8.00. Temperature: 5.9 08:15 Zone 3 grab: Free chlorine: 0.05. Analyzer: 0.04. Total Chlorine: 2.44. Analyzer: 2.35. Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.013628 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; sample collected [regulatory] | 0.013628 | 0 | 0
2026-03 | 2026-03-23 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. 08:56 reservoir inlet at 72 l/s. Rechloramination dosing on. Zone 3 pumps 2 running at 70.1 l/s. P1 in standby. Replaced zone 3 CL17 free analzyer reagent. Topped up chemscan distilled water. Verified analyzer residuals (mg/l): 09:13 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.03. Total Chlorine grab: 1.85 CL17: 1.87. Chemscan: 1.93 Monochloramine grab: 1.68 Chemscan: 1.66. Free ammonia grab: 0.10. Chemscan: 0.09. Total ammonia: 0.43. Chemscan: 0.46. 09:44 Post-injection grabs. Free chlorine grab: 0.05. Analyzer: 0.06. Total Chlorine grab: 2.60 CL17: 2.63. Chemscan: 2.67. Monochloramine grab: 2.25. Chemscan: 2.18.. Free ammonia grab: 0.05. Chemscan: 0.02. Total ammonia: 0.50. Chemscan: 0.54.. 09:49 Outlet grab: Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.32 Analyzer: 2.34 09:49 (corrected time typo) Zone 3 grab: Free chlorine: 0.02. Analyzer: 0.04. Total Chlorine: 2.32. Analyzer: 2.35. . Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.013945 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; faulted [equipment_failure]; work order [maintenance_action] | 0.013945 | 0 | 0
2026-03 | 2026-03-16 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite to adjust metro flow control valve Adjusted speed pilots on valve, both now set to 3 turns from fully closed. | FLAG | stage2_low_confidence | 0.011929 | ML: above threshold (no LLM available) — 0.012 |  | 0.011929 | 0 | 0
2026-03 | 2026-03-26 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite to complete CL17 analyzer maintenance. Topped up chemscan sulphuric acid reagent. Replaced outlet free cl17 analyzer reagent. 09:45 Notified ROC, placed free analyzers in calibration mode and completed all free cl17 analyzer maintenance. 10:28 Verified zone 3 analyzer (mg/l): 0.05. Analyzer 0.04. 10:30 Outlet free grab: 0.03. Analyzer: 0.07. 10:32 Preinjection free grab: 0.05. Analyzer: 0.04. 10:34 Post injection free grab: 0.08. Analyzer: 0.04. completed site cleaning. No issues found. Topped up No issues found. | FLAG | stage2_low_confidence | 0.012878 | ML: above threshold (no LLM available) — 0.013 |  | 0.012878 | 0 | 0
2026-03 | 2026-03-20 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. 10:15 reservoir inlet at o l/s. Rechloramination dosing off. Reservoir outlet 18 l/s. Zone 3 pumps 1 and 2 in standby. Verified analyzer residuals (mg/l): 10:38 Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.34 CL17: 2.34. Chemscan 2.35. Monochloramine grab: 2.01 Chemscan: 1.99 Free ammonia grab: 0.08. Chemscan: 0.14. Analyzers next reading 0.03 with grab 0.06. Adjusted analyzer offset up to match grab. Total ammonia: 0.47. Chemscan: 0.50. 10:48 Post-injection grabs. Free chlorine grab: 0.03. Analyzer: 0.04. Total Chlorine grab: 2.36 CL17: 2.39. Chemscan: 2.51. Adjusted chemscan to match grabs. Monochloramine grab: 2.05. Chemscan: 2.10. Free ammonia grab: 0.07. Chemscan: 0.02. Adjusted to match grab. Total ammonia: 0.47. Chemscan: 0.50. 10:57 Outlet grab and sample collected. Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.40 Analyzer: 2.35 10:57 Zone 3 grab: Free chlorine: 0.07.. Analyzer: 0.04. Total Chlorine: 2.40. Analyzer: 2.35. . Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.042536 | ML: above threshold (no LLM available) — 0.043 | fault [equipment_failure]; faulted [equipment_failure]; work order [maintenance_action]; sample collected [regulatory] | 0.042536 | 0 | 0
2026-03 | 2026-03-17 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite to complete work orders and to adjust metro valve speed setpoints. 10:50 Notified ROC of work being performed. Adjusted closing and opening speed pilots from 3 turns opened from close to 4.5 turns open. Exercised speed pilots. Tested valve and opened with no issues. Placed valve back into auto. Valve flow trend initially appears less erratic. JHSC inspection ok. Visual chemical injection point inspection. ok. No issues found. | FLAG | stage2_low_confidence | 0.040998 | ML: above threshold (no LLM available) — 0.041 | work order [maintenance_action] | 0.040998 | 0 | 0
2026-03 | 2026-03-17 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite for chlorine cylinder change. Changed left chlorine cylinder with Alex B. 13:45 Notified roc and ran diesel generator under load. Fuel level: 2158 to 2137L. Run hours: 240.53 to 241.57. Preinspection: Oil level ok. Coolant level ok. Battery terminals ok. Recirculaiton pump ok. 14:48 completed generator run. No new issues found. | FLAG | stage2_low_confidence | 0.013036 | ML: above threshold (no LLM available) — 0.013 |  | 0.013036 | 0 | 0
2026-03 | 2026-03-18 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check and sampling. W11672681 13:58 reservoir inlet at 61 l/s. Rechloramination dosing on. Zone 3 pumps 1 and 2 in standby. Replaced pre-injection cl17sc total analyzer reagent. Verified analyzer residuals (mg/l): 14:21 Pre-injection grabs: Free chlorine grab: 0.05. Analyzer: 0.03. Total Chlorine grab: 1.87 CL17: 1.85. Chemscan: 1.88 14:25 Post-injection grabs. Free chlorine grab: 0.06. Analyzer: 0.09. Total Chlorine grab: 2.68 CL17: 2.62. Chemscan: 2.79. 14:30 Outlet grab and sample collected. Free chlorine grab: 0.03. Analyzer: 0.03. Total Chlorine grab: 2.40. Analyzer: 2.38. Monochloramine grab: 2.14 Free ammonia grab: 0.06. Total ammonia: 0.49. Nitrite: 0.000 pH: 8.06. Temperature: 4.6 celsius. 14:30 Zone 3 grab: Free chlorine: 0.03. Analyzer: 0.04. Total Chlorine: 2.40. Analyzer: 2.38 . Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.012998 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; faulted [equipment_failure]; work order [maintenance_action]; sample collected [regulatory] | 0.012998 | 0 | 0
2026-03 | 2026-03-25 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check and sampling of reservoir. W11690064. 13:00 reservoir outlet at 52 l/s. Rechloramination dosing off. Zone 3 pumps 1 and 2 in standby. Verified analyzer residuals (mg/l): 13:05 Pre-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.03. Total Chlorine grab: 2.28 CL17: 2.32. Chemscan: 2.38. 13:11 Post-injection grabs. Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.30 CL17: 2.38. Chemscan: 2.32. 13:15 Outlet grab and sample collected. Free chlorine grab: 0.06. Analyzer: 0.03. Total Chlorine grab: 2.36 Analyzer: 2.33. Monochloramine grab: 2.07 Free ammonia grab: 0.05. Total ammonia: 0.45. 13:15 Zone 3 grab: Free chlorine: 0.06. Analyzer: 0.04. Total Chlorine: 2.36. Analyzer: 2.29. . Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.017793 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; faulted [equipment_failure]; work order [maintenance_action]; sample collected [regulatory] | 0.017793 | 0 | 0
2026-03 | 2026-03-19 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | Onsite to complete Chemscan and cl17sc maintenance. 13:54 notified roc of work and shut down all chemical dosing pumps. Placed analyzers in calibration mode and performed Chemscan maintenance and clean flush. Cleaned all cl17sc total chlorine analyzers. Verified analyzers. 14:18 zone 3 outlet total: 2.38. Analyzer: 2.35. 14:21 outlet total: 2.30. Analyzer: 2.34. 14:27 pre injection total: 1.83. Analyzer: 1.88 14:30 post injection total: 1.86. Analyzer: 1.91. 14:41 placed all analyzers systems back in service. No issues found. | FLAG | stage2_low_confidence | 0.013241 | ML: above threshold (no LLM available) — 0.013 |  | 0.013241 | 0 | 0
2026-03 | 2026-03-27 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. 12:28 reservoir inlet at 62 l/s. Rechloramination dosing on. Zone 3 pumps 1 and 2 in standby. Verified analyzer residuals (mg/l): 12:36 Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.03. Total Chlorine grab: 1.84 CL17: 1.89. Chemscan: 1.96. Adjusted chemscan to match grabs. Monochloramine grab: 1.69 Chemscan: 1.70 Free ammonia grab: 0.11. Chemscan: 0.10 Total ammonia: 0.45. Chemsca: 0.46. 12:43 Post-injection grabs. Free chlorine grab: 0.04. Analyzer: 0.06. Total Chlorine grab: 2.70 CL17: 2.72. Chemscan: 2.90. Chemscan dropped next reading to 2.74. Monochloramine grab: 2.28. Chemscan: 2.31 Free ammonia grab: 0.04. Anlayzer: 0.02. Adjusted to match grab. Total ammonia: 0.49. Chemscan: 0.54. 12:52 Outlet grab Free chlorine grab: 0.02. Analyzer: 0.03. Total Chlorine grab: 2.34 Analyzer: 2.30 12:52 Zone 3 grab: Free chlorine: 0.02. Analyzer: 0.04. Total Chlorine: 2.34. Analyzer: 2.31 13:14 stopped dosing to complete chlorine to perform chlorine system inspectino. Notified ROC. Triggered a high vaccum switch alarm during vacuum test. 13:34 No issues found. Placed chemical dosing systems back in auto . Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.008729 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.008729 | 0 | 0
2026-03 | 2026-03-26 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site to respond to chlorine room exhaust fan, EF1, reports of it tripping. Found exhaust fan tripped on MCC. Inspected motor fan belt and blower wheel. Found all to be in good working order. Inspected motor nameplate current draw and compared that to the overload on the motor starter in the MCC. Found that the trip setting on the overload was set too low. Adjusted setting and tested for proper operation. Chlorine room exhaust fan should be working correctly now. | FLAG | stage2_low_confidence | 0.10449 | ML: above threshold (no LLM available) — 0.104 | tripped [equipment_failure]; trip [equipment_failure] | 0.10449 | 0 | 0
2026-03 | 2026-03-16 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | CENTRAL | On site for station check. 09:01 reservoir inlet at 68 l/s. Rechloramination dosing on. Zone 3 pumps 1 running at 70 l/s and P2 in standby. Replaced pre injection free chlorione analyzer reagent. Verified analyzer residuals (mg/l): 09:10 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 1.85 CL17: 1.88. Chemscan: 1.91 Monochloramine grab: 1.67 Chemscan: 1.64 Free ammonia grab: 0.11. Chemscan: 0.10. Total ammonia: 0.44. Chemscan: 0.47 09:22 Post-injection grabs. Free chlorine grab: 0.05. Analyzer: 0.07. Total Chlorine grab: 2.58 CL17: 2.66. Chemscan: 2.81 Monochloramine grab: 2.26 Chemscan: 2.29 Free ammonia grab: 0.06. Chemscan: 0.04 Total ammonia: 0.50. Chemscan: 0.57. 09:33 Outlet grab and sample collected. Free chlorine grab: 0.06. Analyzer: 0.03. Total Chlorine grab: 2.34. Analyzer: 2.36. 09:33 Zone 3 grab: Free chlorine: 0.06. Analyzer: 0.04. Total Chlorine: 2.34. Analyzer: 2.36. Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | FLAG | stage2_low_confidence | 0.026536 | ML: above threshold (no LLM available) — 0.027 | fault [equipment_failure]; faulted [equipment_failure]; work order [maintenance_action]; sample collected [regulatory] | 0.026536 | 0 | 0
2026-03 | 2026-03-30 | Aurora Well 5 | CENTRAL | Restarted the Operator Interface Terminal due to Windows Operating System software updates. Well was not running during the work. | FLAG | stage2_low_confidence | 0.016018 | ML: above threshold (no LLM available) — 0.016 | not running [equipment_failure] | 0.016018 | 0 | 0
2026-03 | 2026-03-06 | Aurora Well 5 | CENTRAL | Attending site to check chlorinator#2 (W11714177). Replaced broken 1/4" tubing section. This was repaired earlier this week but broke again. Left a loop in the tubing this time to reduce stress on the tubing. Joe DeMarco called to advise that the dosing required adjustment after the repair which he performed remotely. Influent Free residual is back within normal limits. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.10567 | ML: above threshold (no LLM available) — 0.106 | repair [maintenance_action] | 0.10567 | 0 | 0
2026-03 | 2026-03-03 | Aurora Well 5 | CENTRAL | silicate top up: before 1805L after 2315L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070212 | 0 | 0
2026-03 | 2026-03-09 | Aurora Well 5 | CENTRAL | Onsite for station check: Changed CL2 cylinders: 0/48 kg to 68/48 kg * Adjusted treated total analyzer from 3.17 to 2.88 based on multiple grabs (2.86, 2.88, 2.88) * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004491 | 0 | 0
2026-03 | 2026-03-02 | Aurora Well 5 | CENTRAL | Onsite for station check: Collected enhanced operational sample * Adjusted influent free analyzer from 2.74 to 2.60 based on multiple grabs (2.60, 2.60, 2.58) * Adjusted effluent free analyzer from 2.38 to 2.20 based on multiple grabs (2.20, 2.20, 2.20) * Replaced effluent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Changed CL2 cylinders: 58/0 kg to 58/68 kg * | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033701 | 0 | 0
2026-03 | 2026-03-09 | Aurora Well 5 | CENTRAL | Adjusted ammonia startup dosage setpoint from 42.76 mL/min to 44.00 mL/min | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051552 | 0 | 0
2026-03 | 2026-03-12 | Aurora Well 5 | CENTRAL | Onsite to repair ammonia mixer pump 2 Replaced propeller on shaft Mixed ammonia tank 2, back in service Investigate Silicate pump 1 fault ?Ruptured diaphragm? Will get new from inventory and replace, remains OOS Ops normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; repair [maintenance_action] | fault [equipment_failure]; oos [equipment_failure]; repair [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-13 | Aurora Well 5 | CENTRAL | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Silicate P1 man/off OOS- will replace diaphragm | FLAG | stage2_low_confidence | 0.0091474 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure] | 0.0091474 | 0 | 0
2026-03 | 2026-03-11 | Aurora Well 5 | CENTRAL | Onsite for station check/collect samples- WO# W11657608: Treated sample results (09:58): Free- 0.14, Total- 2.96 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045207 | 0 | 0
2026-03 | 2026-03-18 | Aurora Well 5 | CENTRAL | Onsite for station check/collect samples- WO# W11673476: Treated sample results (12:04): Free- 0.09, Total- 3.08 * Adjusted treated total analyzer from 2.83 to 3.08 based on multiple grabs (3.08, 3.04, 3.08) * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004878 | 0 | 0
2026-03 | 2026-03-20 | Aurora Well 5 | CENTRAL | Onsite for station check: Changed CL2 cylinders: 0/56 kg to 68/56 kg * Replaced influent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034644 | 0 | 0
2026-03 | 2026-03-24 | Aurora Well 5 | CENTRAL | Attending site to check silicate pump#2 (W11737102). When operated, pump stops after a few strokes then displays power supply error. Pump was removed for evaluation my the manufacturer's representative. | FLAG | stage2_low_confidence | 0.02255 | ML: above threshold (no LLM available) — 0.023 |  | 0.02255 | 0 | 0
2026-03 | 2026-03-05 | Aurora Well 5 | CENTRAL | Onsite to troubleshoot chlorine booster/chlorinator #2- informed ROC: Tried running chlorine booster #2 and chlorinator #2- no flow to chlorinator. Placed well 5 in man/off. Locally ran chlorine booster pump #2 and manually opened chlorinator #2- still no flow to chlorinator. Placed chlorine booster #2 and chlorinator #2 in local/off- Informed Eric S. Chlorine system will require further troubleshooting. Well 5 placed back into auto once investigation completed | FLAG | stage2_low_confidence | 0.024432 | ML: above threshold (no LLM available) — 0.024 | oos [equipment_failure] | 0.024432 | 0 | 0
2026-03 | 2026-03-06 | Aurora Well 5 | CENTRAL | Onsite for station check/complete assigned WO: H/S inspection Placed chlorine booster #2 and chlorinator #2 back into auto duty 1. Further investigation completed by Eric S. Placed back into normal operation and will monitor performance during next run cycle. Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.012651 | ML: above threshold (no LLM available) — 0.013 | oos [equipment_failure] | 0.012651 | 0 | 0
2026-03 | 2026-03-10 | Aurora Well 5 | CENTRAL | Onsite to complete assigned work orders: Deep well exhaust inspection Exhaust fan/damper inspection CL17 analyzer maintenance Turbidimeter maintenance Silicate system inspection - Adjusted silicate P1 max flow from 150 to 140 based on multiple drawdown attempts * - Adjusted silicate P2 max flow from 150 to 140 based on multiple drawdown attempts * Ammonia system inspection Chlorine system inspection CL2 leak alarm test Performed station housekeeping Work order created for ammonia tank #2 mixer damaged propeller * Jason G onsite filling silicate tank * Station/equipment- Ok | FLAG | stage2_low_confidence | 0.014525 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action]; work order created [maintenance_action]; alarm [control_system]; leak [infrastructure] | 0.014525 | 0 | 0
2026-03 | 2026-03-03 | Aurora Well 5 | CENTRAL | Attending site to check issue with chlorinator #2 (W11692934). Found broken 1/4" tubing where the local vacuum gauge is bypassed. Replaced broken tubing and tested. Could not put back to Auto due to SCADA communication issue. Wil notify Operations. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.071803 | ML: above threshold (no LLM available) — 0.072 | bypass [critical]; scada [control_system] | 0.071803 | 0 | 0
2026-03 | 2026-03-04 | Aurora Well 5 | CENTRAL | Onsite for station check/collect samples- WO# W11638288: Treated sample results (11:32): Free- 0.06, Total- 3.04 * Replaced treated total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003759 | 0 | 0
2026-03 | 2026-03-27 | Aurora Well 5 | CENTRAL | Onsite for station check/complete assigned work orders: Changed CL2 cylinders: 34/0 kg to 34/68 kg * Eyewash cleaning/inspection Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.0062797 | 0 | 0
2026-03 | 2026-03-23 | Aurora Well 5 | CENTRAL | Onsite for station check: Received multiple high FA readings during operational sampling (0.13, 0.11, 0.12)- Adjusted CL2/AMM ratio from 3.7 to 3.9. Once adjustments made FA reading 0.08. Performed ammonia drawdowns during monthly maintenance, no abnormalities. Will continue to monitor changes * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_low_confidence | 0.01227 | ML: above threshold (no LLM available) — 0.012 |  | 0.01227 | 0 | 0
2026-03 | 2026-03-16 | Aurora Well 5 | CENTRAL | Onsite for station check and troubleshoot silicate pump fault alarms: Silicate pump 1 diaphragm rupture alarm- replaced diaphragm and primed lines. Completed a drawdown to verify pump output. Pump placed back into auto duty 1. Silicate pump 2 diaphragm rupture alarm- replaced diaphragm but unable to prime lines. Pump display reading power error- will create work order for pump to be further investigated. Pump placed OOS. Changed CL2 cylinders: 41/0 kg to 41/68 kg Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; pump fault [infrastructure] | fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-03 | 2026-03-24 | Aurora Well 5 | CENTRAL | Silicate top up (44 to 52cm) | FLAG | stage2_low_confidence | 0.0095377 | ML: above threshold (no LLM available) — 0.01 |  | 0.0095377 | 0 | 0
2026-03 | 2026-03-25 | Aurora Well 5 | CENTRAL | Onsite for station check/collect samples- WO# W11690776: Sample results (13:00): Free- 0.07, Total- 3.08 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043537 | 0 | 0
2026-03 | 2026-03-31 | Aurora Well 6 | CENTRAL | Onsite for station check: Station offline * Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0084887 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084887 | 0 | 0
2026-03 | 2026-03-12 | Aurora Well 6 | CENTRAL | Onsite to ?borrow? ammonia pump Ops normal Well 6 OOS | FLAG | stage2_low_confidence | 0.016166 | ML: above threshold (no LLM available) — 0.016 | oos [equipment_failure] | 0.016166 | 0 | 0
2026-03 | 2026-03-30 | Aurora Well 6 | CENTRAL | Restarted the Operator Interface Terminal due to Windows Operating System software updates. Well was off. | FLAG | stage2_low_confidence | 0.0078886 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078886 | 0 | 0
2026-03 | 2026-03-11 | Aurora Well 6 | CENTRAL | Onsite for station check: Station offline * Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070744 | 0 | 0
2026-03 | 2026-03-03 | Aurora Well 6 | CENTRAL | Onsite for station check/complete assigned work orders: H/S inspection Performed station housekeeping Station/equipment- Ok | FLAG | stage2_low_confidence | 0.012862 | ML: above threshold (no LLM available) — 0.013 | work order [maintenance_action] | 0.012862 | 0 | 0
2026-03 | 2026-03-18 | Aurora Well 6 | CENTRAL | Onsite for station check: Station offline * Station/equipment- Ok | FLAG | stage2_low_confidence | 0.0084887 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084887 | 0 | 0
2026-03 | 2026-03-23 | Aurora Well 6 | CENTRAL | Station and equipment check Well remains OOS as per normal ops All ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-31 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Received 24 chlorine cylinders. Returned 24 empties. | FLAG | stage2_low_confidence | 0.010607 | ML: above threshold (no LLM available) — 0.011 |  | 0.010607 | 0 | 0
2026-03 | 2026-03-05 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite to complete assigned work orders- informed ROC: H/S inspection Performed station housekeeping Generator test run: Start hours- 92.50 Stop hours- 93.75 Start fuel- 6,750 L (25.5 cm) Stop fuel- Start time- 12:36 Stop time- 13:53 Generator pre test inspection completed- no abnormalities * Generator operating stats (under load P2/P3): 1800 rpm 600 V 60 Hz 962 A Oil pressure- 79 psi Oil temp- 187 F Coolant temp- 177 F Fuel pressure- 103 psi Fuel temp- 68 F No abnormalities during generator test run- returned generator and station pumps back to auto once test run completed * Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.0006883 | 0 | 0
2026-03 | 2026-03-09 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Fuel inspection | FLAG | stage2_low_confidence | 0.011833 | ML: above threshold (no LLM available) — 0.012 |  | 0.011833 | 0 | 0
2026-03 | 2026-03-11 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for raw station check/collect samples- WO# W11657608: Station/equipment- Ok Onsite for station check/collect sample- WO# W11657608: Treated sample results (11:45): Free- 0.12, Total- 2.90 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032065 | 0 | 0
2026-03 | 2026-03-04 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check/collect samples- WO# W11638288: Treated sample results (09:40): Free- 0.06, Total- 2.92 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/collect samples- WO# W11638288: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033564 | 0 | 0
2026-03 | 2026-03-03 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite to complete assigned work orders- informed ROC: H/S inspection CL17 analyzer maintenance Turbidimeter maintenance CL2 leak alarm test Silicate system inspections Ammonia system inspections Chlorine system inspections Eyewash cleaning/solution replacement (treated building) Performed cleaning/maintenance on chemical boards Station/equipment- Ok | FLAG | stage2_low_confidence | 0.014388 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | 0.014388 | 0 | 0
2026-03 | 2026-03-09 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030966 | 0 | 0
2026-03 | 2026-03-06 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Changed CL2 cylinders: 0/59 kg to 68/59 kg * Replaced effluent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/complete WO: Air relief valve inspection Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0018468 | 0 | 0
2026-03 | 2026-03-02 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Collected enhanced operational sample * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004226 | 0 | 0
2026-03 | 2026-03-13 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for station check: Replaced treated free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/complete WO: Eyewash cleaning/inspection Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0020688 | 0 | 0
2026-03 | 2026-03-17 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Received silicate delivery. Bulk tank 41.7 ¦ 40.7cm -> 83.0 ¦ 81.7cm | FLAG | stage2_low_confidence | 0.01151 | ML: above threshold (no LLM available) — 0.012 |  | 0.01151 | 0 | 0
2026-03 | 2026-03-16 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for station check: Changed CL2 cylinders: 45/0 kg to 45/68kg (Donald M and Ben H) Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045313 | 0 | 0
2026-03 | 2026-03-20 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030966 | 0 | 0
2026-03 | 2026-03-23 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite to change CL2 cylinders: 0/53 kg to 68/53 kg * | FLAG | stage2_low_confidence | 0.010699 | ML: above threshold (no LLM available) — 0.011 |  | 0.010699 | 0 | 0
2026-03 | 2026-03-26 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite to perform ammonia pump maintenance- informed ROC: Replaced ammonia pump diaphragms, primed ammonia pumps once completed Station/equipment- Ok | FLAG | stage2_low_confidence | 0.010569 | ML: above threshold (no LLM available) — 0.011 |  | 0.010569 | 0 | 0
2026-03 | 2026-03-17 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Received ammonia delivery with Donny M. | FLAG | stage2_low_confidence | 0.013189 | ML: above threshold (no LLM available) — 0.013 |  | 0.013189 | 0 | 0
2026-03 | 2026-03-27 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030966 | 0 | 0
2026-03 | 2026-03-18 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for raw station check/collect raw samples- WO# W11673476: Station/equipment- Ok Onsite for treated station check/collect treated samples- WO# W11673476: Treated sample results (10:40): Free- 0.14, Total- 3.06 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Noticed burning smell coming from electrical room- informed Ben H and Tyler Z- electrician will attend station to further investigate * | FLAG | stage2_low_confidence | 0.0080831 | ML: above threshold (no LLM available) — 0.008 | burning smell [equipment_failure] | 0.0080831 | 0 | 0
2026-03 | 2026-03-25 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check/collect sample- WO# W11690776: Sample results (09:45): Free- 0.10, Total- 2.90 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/collect samples- WO# W11690776: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032094 | 0 | 0
2026-03 | 2026-03-23 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | Onsite for treated station check: Replaced influent free CL17 reagents * Replaced treated total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025689 | 0 | 0
2026-03 | 2026-03-04 | Aurora Wells 1-4 Water Treatment Plant | CENTRAL | On site to transfer silicate.? Before level: 0.84 / 0.86cm After level: 0.80 / 0.81 cm | FLAG | stage2_low_confidence | 0.0081299 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081299 | 0 | 0
2026-03 | 2026-03-28 | Bayview Pumping Station | EAST | SYSTEM TESTING - PLEASE IGNORE | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055287 | 0 | 0
2026-03 | 2026-03-28 | Bayview Pumping Station | EAST | SYSTEM TESTING - PLEASE IGNORE | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055287 | 0 | 0
2026-03 | 2026-03-30 | Bayview Pumping Station | EAST | Attended site for preventative maintenance with Phil DeGroot. Tested discharge surge valves Exercised Sycamore chamber PRV Station and equipment okay | FLAG | stage2_low_confidence | 0.0072969 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072969 | 0 | 0
2026-03 | 2026-03-30 | Bayview Pumping Station | EAST | On site to complete station check. Time: 11:40 Grab (mg/l) Analyzer (mg/l) Free: 0.05 0.01 Total: 1.47 1.49 Verified analyzer with grabs. Checked station and trends. Pump 2 OOS due to it being rebuilt. All alarms on site are due to pump 2 being offline. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | Bayview Pumping Station | EAST | On site to facilitate Diesel load test with generator contractor. | FLAG | stage2_low_confidence | 0.013871 | ML: above threshold (no LLM available) — 0.014 |  | 0.013871 | 0 | 0
2026-03 | 2026-03-11 | Bayview Pumping Station | EAST | Duty rotated pumps - Placed pump #3 in duty 1, pump #4 to duty 2. Duty is currently not active. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057549 | 0 | 0
2026-03 | 2026-03-31 | Bayview Pumping Station | EAST | On site to wire up temperature sensors on pump two. Also facilitate generator fluid maintenance with generator contractor. Transfer test to test for proper operation of the standby power system. | FLAG | stage2_low_confidence | 0.025368 | ML: above threshold (no LLM available) — 0.025 |  | 0.025368 | 0 | 0
2026-03 | 2026-03-31 | Bayview Pumping Station | EAST | On site to respond to Pump #3 suction valve not open interlock, and the chlorine / temperature analyzer OOR / Low alarms Electrical is on site for generator service / load test with Total Power. Chlorine analyzer dropped to 0.00 mg/L @13:41, and recovered @13:46. Was caused during station power transfer to generator. Between the power transfer, an alarm came up on the generator, causing a delay to the transfer. During that period, the chlorine analyzer lost power, causing the OOR alarms. No further issues with Chlorine analyzer Pump #3 discharge valve was backed off by about half a turn from fully open, causing the position indicator to send a signal to SCADA to interlock Pump #3. Fully opened valve, and the interlock on pump #3 cleared Activated system duty to test pumps while on generator power @14:15 Deactivated system duty @14:32 | FLAG | stage2_low_confidence | 0.082424 | ML: above threshold (no LLM available) — 0.082 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.082424 | 0 | 0
2026-03 | 2026-03-09 | Bayview Pumping Station | EAST | On site for facility station check and equipment verifications Duty is active - RHRSTR Level - 82% Pumps 1 and 4 running, 1245 L/s Recorded station readings in PWQ sheets Verified analyzer readings @11:50 (Grab / Analyzer mg/L) Free: 0.05 / 0.03 Total: 1.58 / 1.63 Reviewed trends - observed that trending on the electrical room OIT (upstairs). Lower OIT is trending okay, as well as remote SCADA trends. Informed TL to create WO for PCs Equipment OOS: Pump #2 for rebuild Station operation ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | Bayview Pumping Station | EAST | On site for facility station check and equipment verifications Duty is active - RHRSTR Level - 80% Pumps 1 and 3 running in D1 - 1277 L/s, 644 kpa discharge pressure Recorded data in PWQ sheets Verified analyzer readings with grab residuals: @14:00 Grab free: 0.07 mg/L / Analyzer: 0.04 mg/L Grab total: 1.48 mg/L / Analyzer: 1.55 mg/L Observed water leaking from grease nipple on check valve for pump #1. Was able to slow the leak, but will need mechanical support to fix. Pump is still able to run. Created W11733142 to address the issue Reviewed trends Equipment OOS: Pump #2 for rebuild Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; leak [infrastructure]; leaking [infrastructure] | oos [equipment_failure]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-06 | Bayview Pumping Station | EAST | On site for facility station check and equipment verifications Duty is active - RHRSTR Level - 77% Pumps 1 and 4 running in D1 - 1265 L/s, Discharge pressure - 634 kpa Verified chlorine analyzer readings: @11:55 Grab free: 0.05 mg/L / Analyzer: 0.03 mg/L Grab total: 1.51 mg/L / Analyzer: 1.49 mg/L Reviewed trends Equipment OOS: Pump #2 for rebuild Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-16 | Bayview Pumping Station | EAST | On site for facility station check and equipment verifications Duty is active - RHRSTR level - 73% Pumps 1 and 3 running in D1, 1285 L/s, 638 kpa discharge pressure Recorded data in PWQ sheets Verified analyzer readings @13:48 Grab FCL: 0.06 / Analyzer: 0.04 mg/L Grab TCL: 1.47 / Analyzer: 1.53 mg/L Reviewed trends, equipment OOS: Pump 2 for rebuild Station operations normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-16 | Bayview Pumping Station | EAST | Vibration readings | FLAG | stage2_low_confidence | 0.021831 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021831 | 0 | 0
2026-03 | 2026-03-26 | Bayview Pumping Station | EAST | On site for installation of rtd?s, conduit and wiring for pump #2 rebuild. | FLAG | stage2_low_confidence | 0.011116 | ML: above threshold (no LLM available) — 0.011 |  | 0.011116 | 0 | 0
2026-03 | 2026-03-20 | Bayview Pumping Station | EAST | Station Check (no issues found) Input data to PWQ 11:40 Verified Depolox (mg/l) Free: Grab 0.04, A 0.02 Total: Grab 1.51, A 1.46 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050566 | 0 | 0
2026-03 | 2026-03-02 | Bayview Pumping Station | EAST | On site to check station and equipment. P1 and P4 are running in duty 1. 14:13 chlorine residuals grab/analyzer in mg/l: Total: 1.51/1.53 Free: 0.04/0.03 Other station readings are in PWQ sheets. Reviewed trends, Station is under normal operation. Equipment OOS: Pump 2. | FLAG | stage2_low_confidence | 0.0095465 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure] | 0.0095465 | 0 | 0
2026-03 | 2026-03-23 | Bayview Pumping Station | EAST | On site for station check, equipment verifications, and to complete monthly PMs - Diesel generator test run and hours log Duty is not active - RHRSTR level is 78% Pre checks: Oil Level - Ok Coolant Level - Ok Battery Terminals / cables - Ok Battery Cell levels - N/A Coolant Recirculation pump - Ok Fluid leaks - None Start hours: 138.8 hours Start Fuel: 4081 / 4092 L (152 / 153 cm) Start time: @11:43 Activated system duty while generator running to test station operation under generator power Generator readings while running: @12:50 Voltage: 4.16 kV Current: 165 amps Frequency: 60 hz Engine speed: 1800 RPM Oil pressure: 65.5 psi Oil temperature: 210 F Coolant temperature: 190 F Exhaust: 612 C / 624 C Deactivated system duty @12:59 - pumps 1 and 3 stopped in auto Stop Hours: 140.4 hours Stop time: 13:18 Stop Fuel: 3888 / 3950 (145 / 147 cm) No issues with generator test run or transfer test Verified analyzer readings @12:55 (Grab/analyzer mg/L) FCL: 0.06 / 0.00 TCL: 1.50 / 1.43 No adjustments needed Recorded station data in PWQ sheets @13:43 / 13:45 tested Surge relief valves - pumps are all off. No issues with test, cleared alarms Reviewed trends, equipment OOS: Pump #2 for rebuild Station operation normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.0037893 | 0 | 0
2026-03 | 2026-03-19 | Bayview Pumping Station | EAST | On site for monthly PMs - Informed ROC while on site Station is currently off - duty is not active - Completed Pressure gauge test WO - Pumps 1-4 centrifugal pumps inspection - Ventilation system inspection - Dehumidifier inspection - Check valves inspections / maintenance - Manual valves exercises - Discharge valve actuators exercise to test check valve function with pumps off. When exercising pump #3 discharge valve, the check valve slammed closed aggressively. Created WO to maintenance to look at the check valve. (W11746694) - Flood alarms test (tested high and hihi) Suction and discharge valves closed when triggered flood alarms, and reopened in auto after alarms cleared - JHSC Health and safety inspection - 5 tonne hoist system inspection - Chlorine analyzer maintenance (Depolox) Verified analyzer with grab residuals after maintenance (mg/L) Free Grab: 0.06 mg/L / Analyzer: 0.03 Total Grab: 1.53 / Analyzer: 1.59 Adjusted TCL analyzer to average of 3 grabs Duty activated at 12:30 - Pumps 1 and 3 in duty 1. Completed facility station check and equipment verifications - Readings in PWQ sheets Equipment OOS: Pump #2 for rebuild Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | flood [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | East Vaughan Teston Pumping Station | WEST | On site for station check Check trends: All okay 11:30- Verified analyzer Grab free CL2- 0.04 mg/L Analyzer Free Cl2- 0.02 mg/L Grab Total CL2- 2.05 mg/L Analyzer Total CL2- 2.10 mg/L Reagents all good Entered values in PWQ sheet. Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039398 | 0 | 0
2026-03 | 2026-03-30 | East Vaughan Teston Pumping Station | WEST | On site for station check Check trends: All okay 14:40- Verified analyzer Grab free CL2- 0.05 mg/L Analyzer Free Cl2- 0.05 mg/L Grab Total CL2- 2.16 mg/L Analyzer Total CL2- 2.08 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039561 | 0 | 0
2026-03 | 2026-03-02 | East Vaughan Teston Pumping Station | WEST | On site for station check Check trends: All okay 12:50- Verified analyzer Grab free CL2- 0.04 mg/L Analyzer Free Cl2- 0.04 mg/L Grab Total CL2- 2.09 mg/L Analyzer Total CL2- 2.13 mg/L Reagents all good Entered values in PWQ sheet. Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039398 | 0 | 0
2026-03 | 2026-03-12 | East Vaughan Teston Pumping Station | WEST | Reset Sanitary sump pump alarms. W11633103- Charlatte Surge tanks. Isolated both tanks. Tank 1- pressure v/s level looks good before draining. After drain, pressure dropped down below 54 psi, added compressed air to make it 54 psi. Tank 2- pressure v/s level looks good before draining. pressure v/s level looks good after draining. Put both tanks back to service. Informed ROC before and after the work. | FLAG | stage2_low_confidence | 0.014239 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system]; alarms [control_system] | 0.014239 | 0 | 0
2026-03 | 2026-03-23 | East Vaughan Teston Pumping Station | WEST | Station Check (no issues found) Input data to PWQ 11:00 Verified Depolox (mg/l) Free: Grab 0.04, A 0.00 (adjusted to match grabs) Total: Grab 2.07, A 2.05 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057011 | 0 | 0
2026-03 | 2026-03-16 | East Vaughan Teston Pumping Station | WEST | On site for station check Check trends: All okay 09:20- Verified analyzer Grab free CL2- 0.06 mg/L Analyzer Free Cl2- 0.03 mg/L Grab Total CL2- 2.09 mg/L Analyzer Total CL2- 2.07 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039561 | 0 | 0
2026-03 | 2026-03-17 | East Vaughan Teston Pumping Station | WEST | On site for Scheduled PM workorders, Informed ROC about the works being done. W11632905 VNPS, PD7/PD8 VFD Air Filter Change, East Vaughan Pumping Station (3M) W11632945 VNPS, Process Mechanical Lubrication - PD8, East Vaughan Pumping Station (6M) W11632874 VNPS, Process Mechanical Air valve flush and inspection - PD7, East Vaughan Pumping Station(1M) W11632890 VNPS, Process Mechanical Air valve flush and inspection - PD8, East Vaughan Pumping Station(1M) W11632834 VNPS, Chlorine Analyzer maintenance 14:30-Verified Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.02 mg/L Grab Total Cl2- 2.04mg/L; Analyzer- 2.05 mg/L W11632860 VNPS, Standby Power Generator Test Run and Run Hours log, East Vaughan Pumping Station(1M) Pre check Battery okay- 26.9V Coolant- Okay Oil - Okay Before Start Start time- 10:45 Run time- 237.6 hr Fuel level Bulk Tank- 12763.2L/85.6% Day Tank- 2229L/89.9% Put one pump on load from PD7 and PD8 After Stop Stop time- 12:30 Run time- 239.2 hr Fuel level Bulk Tank- 12659L/84.9% Day Tank- 1937L/76.7% | FLAG | stage2_low_confidence | 0.0076061 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076061 | 0 | 0
2026-03 | 2026-03-20 | East Vaughan Teston Pumping Station | WEST | On site for station check Check trends: All okay 13:30- Verified analyzer Grab free CL2- 0.02 mg/L Analyzer Free Cl2- 0.01 mg/L Grab Total CL2- 2.15 mg/L Analyzer Total CL2- 2.10 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. W11749626- VNPS pd8 pump 2 not avaliable - CMU created. Sanitary pit flush complete | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042833 | 0 | 0
2026-03 | 2026-03-05 | East Vaughan Teston Pumping Station | WEST | On site to respond to outstanding fault on PD8 pump 4 VFD. Found F 25 watchdog fault. Manufacturers troubleshooting guide indicates that this is a micro processor overload fault. The troubleshooting guide recommends that if this is not a persistent problem, which it has not been, to just go ahead and try a reset and see if the problem goes away. Reset the drive and the fault is clear. If the problem persists we will have to look further at the main control board. Also, installed vibration dampening screws on fuel system outside, and inside, audible alarms in an effort to reduce the volume from these alarm horns. | FLAG | stage2_low_confidence | 0.26378 | ML: above threshold (no LLM available) — 0.264 | sso [critical]; fault [equipment_failure]; vibration [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.26378 | 0 | 0
2026-03 | 2026-03-06 | East Vaughan Teston Pumping Station | WEST | On site for station check Check trends: All okay 11:15- Verified analyzer Grab free CL2- 0.03 mg/L Analyzer Free Cl2- 0.04 mg/L Grab Total CL2- 2.02 mg/L Analyzer Total CL2- 2.03 mg/L Reagents all good Entered values in PWQ sheet. Equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039398 | 0 | 0
2026-03 | 2026-03-13 | East Vaughan Teston Pumping Station | WEST | On site for station check Check trends: All okay 09:55- Verified analyzer Grab free CL2- 0.05 mg/L Analyzer Free Cl2- 0.02 mg/L Grab Total CL2- 2.03 mg/L Analyzer Total CL2- 2.07 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. W11663655- Sanitary pit flush complete | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041497 | 0 | 0
2026-03 | 2026-03-27 | East Vaughan Teston Pumping Station | WEST | On site for station check Check trends: All okay Zero calibrated free cl2 analyzer 12:00- Verified analyzer Grab free CL2- 0.05 mg/L (Avg:0.03,0.07,0.05) Analyzer Free Cl2- 0.15 mg/L Adjusted the value to 0.05 mg/L Grab Total CL2- 2.04 mg/L Analyzer Total CL2- 2.06 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. Sanitary pit flush complete | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038809 | 0 | 0
2026-03 | 2026-03-11 | Holland Landing East Elevated Tank | WEST | On site for station check Site offline all ok | FLAG | stage2_low_confidence | 0.0087843 | ML: above threshold (no LLM available) — 0.009 |  | 0.0087843 | 0 | 0
2026-03 | 2026-03-19 | Holland Landing East Elevated Tank | WEST | -on site to complete following work order -JHSC inspection: all ok -chamber inspection: tested flood and temp alarm - tower still double isolated -generator run: no issues - topped up gas - low temp alarm: all ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | Holland Landing East Elevated Tank | WEST | -on site for station check -tower isolated -no issues | FLAG | stage2_low_confidence | 0.0090513 | ML: above threshold (no LLM available) — 0.009 |  | 0.0090513 | 0 | 0
2026-03 | 2026-03-05 | Holland Landing East Elevated Tank | WEST | On site for station check Site offline all ok | FLAG | stage2_low_confidence | 0.0087843 | ML: above threshold (no LLM available) — 0.009 |  | 0.0087843 | 0 | 0
2026-03 | 2026-03-16 | Holland Landing East Elevated Tank | WEST | On site to complete station check. Site offline all ok | FLAG | stage2_low_confidence | 0.0091899 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091899 | 0 | 0
2026-03 | 2026-03-13 | Holland Landing Sherwood Pumping Station | WEST | On site to complete station check. Free Chlorine 0.06mg/L Total Chlorine 1.10mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049212 | 0 | 0
2026-03 | 2026-03-09 | Holland Landing Sherwood Pumping Station | WEST | On site to complete station check. Free Chlorine 0.08mg/L Total Chlorine 1.36mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049212 | 0 | 0
2026-03 | 2026-03-02 | Holland Landing Sherwood Pumping Station | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 11:45 -free cl: 0.11mg/l -total cl: 1.45mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047077 | 0 | 0
2026-03 | 2026-03-16 | Holland Landing Sherwood Pumping Station | WEST | On site to complete station check. Free Chlorine 0.06mg/L Total Chlorine 1.41mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049212 | 0 | 0
2026-03 | 2026-03-17 | Holland Landing Sherwood Pumping Station | WEST | On site for the following work orders Diesel test run - elec and contractor on site to run generator for annual inspection Gen start hrs 1431.6 stop 1433.7 Gen start fuel 667L stop 623L Valve exercise Prv Y screen House keeping Low temp alarm Jhsc inspection No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; alarm [control_system] | 0.0066338 | 0 | 0
2026-03 | 2026-03-17 | Holland Landing Sherwood Pumping Station | WEST | On site to facilitate the load testing of the generator. Test complete. System back to normal with no outstanding alarms. | FLAG | stage2_low_confidence | 0.018348 | ML: above threshold (no LLM available) — 0.018 | alarm [control_system]; alarms [control_system] | 0.018348 | 0 | 0
2026-03 | 2026-03-23 | Holland Landing Sherwood Pumping Station | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 14:10 -free cl: 0.04mg/l -total cl: 1.14mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046926 | 0 | 0
2026-03 | 2026-03-06 | Holland Landing Sherwood Pumping Station | WEST | Details: -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 10:10 -free cl: 0. 07 mg/l -total cl: 1.46 mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041735 | 0 | 0
2026-03 | 2026-03-20 | Holland Landing Sherwood Pumping Station | WEST | -on site for station check -checked trends: all ok -took reading in PWQ: all ok -took chlorine grab 13:05 -free cl: 0.07mg/l -total cl: 1.67mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046343 | 0 | 0
2026-03 | 2026-03-30 | Holland Landing Well No. 1 | WEST | Silicate top up: (from 0.469/0.447 to 0.816/0.855cm) | FLAG | stage2_low_confidence | 0.010579 | ML: above threshold (no LLM available) — 0.011 |  | 0.010579 | 0 | 0
2026-03 | 2026-03-10 | Holland Landing Sherwood Pumping Station | WEST | On site for hypo delivery | FLAG | stage2_low_confidence | 0.011568 | ML: above threshold (no LLM available) — 0.012 |  | 0.011568 | 0 | 0
2026-03 | 2026-03-30 | Holland Landing Well No. 1 | WEST | - on site to troubleshoot ammonia pump 1 and silicate pump 1 - replaced element in silicate pump 1 and cleaned silicate system -cleaned injection points, tested check valves and reprimed pumps - ammonia pump 1 airlocked - purged air the relief line and adjusted relief valve - | FLAG | stage2_low_confidence | 0.013696 | ML: above threshold (no LLM available) — 0.014 |  | 0.013696 | 0 | 0
2026-03 | 2026-03-02 | Holland Landing Well No. 1 | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer -influent 10:05: 2.92mg/l grab:2.92mg/l -effluent 10:35: 2.74mg/l grab: 2.78mg/l -treated free 10:10: 0.14mg/l grab: 0.16mg/l -treated total 10:15: 3.28mg/l grab: 3.24mg/l -reagents all ok -topped up ammonia tank 1 16cm - 76cm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057589 | 0 | 0
2026-03 | 2026-03-31 | Holland Landing Well No. 1 | WEST | On site responding to low treated analyzers Verified analyzers started back flushing at 14:10hrs placed dechlor in chamber. Well was off and not directing to user during this time. | FLAG | stage2_low_confidence | 0.012483 | ML: above threshold (no LLM available) — 0.012 |  | 0.012483 | 0 | 0
2026-03 | 2026-03-31 | Holland Landing Well No. 1 | WEST | On site for station check Residuals Treated Total Grab: 2.84mg/L Analyzer: 3.04mg/L Treated Free Grab: 0.15mg/L, Analyzer: 0.34mg/L Effluent Free Grabs: 2.82mg/L, Analyzer: 2.79mg/L Influent Free Grabs: 2.56mg/L, Analyzer: 2.45mg/L Unable to adjust analyzer as buttons aren?t working will create workorder for inst Site in manual off after sampling for main break | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046667 | 0 | 0
2026-03 | 2026-03-11 | Holland Landing Well No. 1 | WEST | On site for station check Residuals Treated Total Grab: 3.30mg/L Analyzer: 3.26mg/L Treated Free Grab: 0.2mg/L, Analyzer: 0.19mg/L Effluent Free Grabs: 2.54mg/L, Analyzer: 2.61mg/L Influent Free Grabs: 2.75mg/L, Analyzer: 2.81mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.30mg/L Mono 2.69mg/L FA 0.04mg/L TA 0.57mg/L found leak on ammonia pump 1, repaired leak and adjusted pump stroke from 85 to 100 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | repair [maintenance_action]; leak [infrastructure] | 0.0046375 | 0 | 0
2026-03 | 2026-03-06 | Holland Landing Well No. 1 | WEST | Details: On site for station check Residuals Treated Total Grab: 3.20 mg/L Analyzer: 3.28mg/L Treated Free Grab: 0.14mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.82 mg/L, Analyzer: 2.74mg/L Influent Free Grabs: 2.94 mg/L, Analyzer: 2. 83mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.55mg/L Mono 2.93mg/L FA 0.09mg/L TA 0.67mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0018538 | 0 | 0
2026-03 | 2026-03-13 | Holland Landing Well No. 1 | WEST | On site for station check Residuals Treated Total Grab: 2.62mg/L Analyzer: 2.55mg/L Treated Free Grab: 0.20mg/L, Analyzer: 0.14mg/L Effluent Free Grabs: 2.12mg/L, Analyzer: 2.03mg/L Influent Free Grabs: 2.78mg/L, Analyzer: 2.78mg/L Performed advanced monitoring (SL1000) Total Chlorine 2.68mg/L Mono 2.10mg/L FA 0.05mg/L TA 0.42mg/L Found leak on ammonia p1 discharge - changed out fitting and pressure tested all seemed ok - placed pump in duty 1 will monitor No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | leak [infrastructure] | 0.0034346 | 0 | 0
2026-03 | 2026-03-10 | Holland Landing Well No. 1 | WEST | On site for the following HLW1, JHSC Health and Safety Inspection, Holland Landi HLW1, Flow Control Valve, Test, Holland Landing W1 (1M) HLW1, Chlorine Scrubber, Check, Holland Landing W1 (1M) HLW1, Chlorine Gas Detector, Test, Holland Landing W1 (1M) HLW1, Chlorine Analyzer, Maintenance, Holland Landing W1 (1M) HLW1, Chlorinator, Inspection, Holland Landing, Well 1 (6M) HLW1, Turbidity Analyzer TU5300, Maintenance and Calibration, Holland Landing W1 (1M) HLW1, Chemical System Inspection - Chlorine , Holland Landing W1 (1M) HLW1, Chemical System Inspection - Silicate, Holland Landing W1 (1M) HLW1, CIZ Emergency Repair Kit Inspection, Holland Landing W1 (1M) HLW1, Chemical System Inspection - Ammonia, Holland Landing Well 1 (1M) Changed chlorine cylinder 1 with Tim Hudson from 0-68kg | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; repair [maintenance_action] | emergency [critical]; repair [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-09 | Holland Landing Well No. 1 | WEST | On site for station check Residuals Treated Total Grab: 3.42mg/L Analyzer: 3.36mg/L Treated Free Grab: 0.11mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.68mg/L, Analyzer: 2.73mg/L Influent Free Grabs: 2.90mg/L, Analyzer: 2.82mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.51mg/L Mono 2.94mg/L FA 0.12mg/L TA 0.70mg/L Changed out treated free reagents No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0014285 | 0 | 0
2026-03 | 2026-03-16 | Holland Landing Well No. 1 | WEST | **Disregard the following entry meant for hlw2** On site for station check Residuals Treated Total Grab: 1.50mg/L Analyzer: 1.45mg/L Treated Free Grab: 0.05mg/L, Analyzer: 0.03mg/L Effluent Free Grabs: 0.93mg/L, Analyzer: 0.83mg/L Influent Free Grabs: 2.58mg/L, Analyzer: 2.57mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034318 | 0 | 0
2026-03 | 2026-03-23 | Holland Landing Well No. 1 | WEST | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 10:05: 2.93mg/l grab: 2.80mg/l - adjusted -effluent 10:10: 2.53mg/l grab: 2.50mg/l -treated free 10:15: 0.14mg/l grab: 0.15mg/l -treated total 10:20: 3.17mg/l grab: 3.10mg/l -adjusted -reagents all ok -investigated ammonia pump 1 - airlocked - adjusted air relief and purged air -man/started well -completed general housekeeping and washroom inspection -equipment all ok | FLAG | stage2_low_confidence | 0.0073146 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073146 | 0 | 0
2026-03 | 2026-03-04 | Holland Landing Well No. 1 | WEST | Details: On site for station check and to collect bacti sample w11637907 Residuals Treated Total Grab: 3.36mg/L Analyzer: 3.41mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.52mg/L, Analyzer: 2.64mg/L Influent Free Grabs: 2.84mg/L, Analyzer: 2.79mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.35mg/L Mono 2.81mg/L FA 0.09mg/L TA 0.65mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0019173 | 0 | 0
2026-03 | 2026-03-20 | Holland Landing Well No. 1 | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: silicate dose low - placed Nasi pump 1 man/off -verified analyzer -influent 11:30: 2.74mg/l grab: 2.70mg/l -effluent 11:35: 2.56mg/l grab: 2.54mg/l -treated free 11:40: 0.19mg/l grab: 0.16mg/l -treated total 11:45: 3.11mg/l grab: 3.08mg/l -reagents all ok -installed air relief line on ammonia pump 1 -ammonia pump 2 max flow set 145ml/min -ammonia pump 1 max flow 110ml/min | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070794 | 0 | 0
2026-03 | 2026-03-27 | Holland Landing Well No. 1 | WEST | On site for station check Residuals Treated Total Grab: 3.30mg/L Analyzer: 3.12mg/L Treated Free Grab: 0.15mg/L, Analyzer: 0.21mg/L Effluent Free Grabs: 2.82mg/L, Analyzer: 2.79mg/L Influent Free Grabs: 2.80mg/L, Analyzer: 2.82mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.30mg/L Mono 2.45mg/L FA 0.00mg/L TA 0.47mg/L Changed out effluent reagents Primed ammonia p1 as it?s air locked No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011563 | 0 | 0
2026-03 | 2026-03-18 | Holland Landing Well No. 1 | WEST | -on site to complete station check and collect weekly bacti W11673099 -checked trends: all ok -entered readings in PWQ -verified analyzer -influent 11.50: 2.84mg/l grab: 2.88mg/l -effluent 11.55: 2.54mg/l grab: 2.64mg/l - adjusted -treated free 12:00: 0.16mg/l grab: 0.14mg/l -treated total 12:05: 3.04mg/l grab: 3.06mg/l -reagents all ok -topped up ammonia tank 2 17cm - 77cm -ammonia pump 1 airlock when tank switch over - purged air -equipment all ok | FLAG | stage2_low_confidence | 0.0075544 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075544 | 0 | 0
2026-03 | 2026-03-25 | Holland Landing Well No. 1 | WEST | On site for station check and to collect bacti sample w11690350 Residuals Treated Total Grab: 3.14mg/L Analyzer: 3.15mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.76mg/L, Analyzer: 2.78mg/L Influent Free Grabs: 2.84mg/L, Analyzer: 2.84mg/L Performed advanced monitoring (SL1000) Mono 2.79mg/L FA 0.04mg/L TA 0.59mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0023657 | 0 | 0
2026-03 | 2026-03-16 | Holland Landing Well No. 1 | WEST | On site for station check Residuals Treated Total Grab: 3.20mg/L Analyzer: 3.28mg/L Treated Free Grab: 0.11mg/L, Analyzer: 0.16mg/L Effluent Free Grabs: 2.58mg/L, Analyzer: 2.65mg/L Influent Free Grabs: 2.78mg/L, Analyzer: 2.81mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.11mg/L Mono 2.80mg/L FA 0.01mg/L TA 0.56mg/L Changed out influent reagents No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0014026 | 0 | 0
2026-03 | 2026-03-30 | Holland Landing Well No. 2 | WEST | Silicate top up (Before: 23.8cm), (after still equalizing) | FLAG | stage2_low_confidence | 0.010906 | ML: above threshold (no LLM available) — 0.011 |  | 0.010906 | 0 | 0
2026-03 | 2026-03-31 | Holland Landing Well No. 2 | WEST | On site for station check and to collect bacti sample w1170616 Residuals Treated Total Grab: 3.08mg/L Analyzer: 3.04mg/L Treated Free Grab: 0.11mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.52mg/L, Analyzer: 2.45mg/L Influent Free Grabs: 2.70mg/L, Analyzer: 2.68mg/L No issues on site. site in manual off for main break. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058208 | 0 | 0
2026-03 | 2026-03-30 | Holland Landing Well No. 2 | WEST | -on sit to change cylinder and troubleshoot silicate leak alarm - changed cylinder - 43kg-97.3kg - silicate pump 1 check valve was passing - cleaned check valves/replaced tubing element/ tested check valves and reprimed both pumps/reset alarms -cleaned water out of room | FLAG | stage2_low_confidence | 0.030148 | ML: above threshold (no LLM available) — 0.03 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.030148 | 0 | 0
2026-03 | 2026-03-02 | Holland Landing Well No. 2 | WEST | -on site to complete station -checked trends: all ok -entered reading in PWQ: all ok -verified analyzers -influent 13:35: 2.69mg/l grab: 2.60mg/l - adjusted -effluent 13.30: 2.40mg/l grab 2.34mg/l - adjusted -treated free 13:35: 0.12mg/l grab: 0.13mg/l -treated total 13:40: 3.06mg/l grab: 3.06mg/l -reagents all ok -topped up ammonia tank 1 16 -76cm -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057871 | 0 | 0
2026-03 | 2026-03-31 | Holland Landing Well No. 2 | WEST | On site to top up ammonia tank 2 from 20-80cm Installed knew check on ammonia p1 suction | FLAG | stage2_low_confidence | 0.0082375 | ML: above threshold (no LLM available) — 0.008 |  | 0.0082375 | 0 | 0
2026-03 | 2026-03-13 | Holland Landing Well No. 2 | WEST | On site to complete chlorinator overhaul (annual). Rebuilt chlorinators 1 and 2 with annual kits, rotameter stoppers, and orifice. Completed 11 point calibration on chlorinators. Tested for vacuum and capacity, all appears good. Backflush small volume with dechlor in outfall chamber, to remove highly chlorinated slugs from influent (purging and calibration). Run HLW2 manual on to test chlorination. Used backwash reset button to account for distribution water in CT after backflush. Residuals: mg/L 1354 Effluent Cl G: FCl 0.30 tcl 1.71 A: FCl 0.31 (Confirming distribution water at effluent after backflush). | FLAG | stage2_low_confidence | 0.010846 | ML: above threshold (no LLM available) — 0.011 |  | 0.010846 | 0 | 0
2026-03 | 2026-03-13 | Holland Landing Well No. 2 | WEST | On site for station check Residuals Treated Total Grab: 1.54 mg/L Analyzer: 1.53 mg/L Treated Free Grab: 0.01 mg/L, Analyzer: 0.03mg/L Effluent Free Grabs: 1.72mg/L, Analyzer: 1.79mg/ L Sl1000 readings - time: 2:43 pm Nitrite 0.005mg/L Total ammonia 0.40 mg/L Free ammonia 0.09 mg/L Mono 1.56 mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0028643 | 0 | 0
2026-03 | 2026-03-04 | Holland Landing Well No. 2 | WEST | On site for station check and bacti sample w11637907 Residuals Treated Total Grab: 3.18mg/L Analyzer: 3.09mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.48mg/L, Analyzer: 2.45mg/L Influent Free Grabs: 2.62mg/L, Analyzer: 2.65mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.28mg/L Mono 2.32mg/L FA 0.00mg/L TA 0.45mg/L Sharon Valve grab Total Chlorine 2.09mg/L Changed out influent free reagents | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0016076 | 0 | 0
2026-03 | 2026-03-20 | Holland Landing Well No. 2 | WEST | -on site to complete station check -check trends all ok -entered readings in PWQ: all ok -verified analyzer -influent 10:00: 2.69mg/l grab: 2.70mg/l -effluent 10:05: 1.92mg/l grab: 1.95mg/l -treated free 10:10: 0.16mg/l grab: 0.14mg/l -treated total 10:15: 2.64mg/l grab: 2.62mg/l -changed treated free reagents -troubleshoot ammonia pump 1 - tried new check valve - did not fit - informed team lead - installed air relief line on pump head - completed draw down 80ml/min -topped up ammonia tank 1 16-76cm -man/started well -no other issues | FLAG | stage2_low_confidence | 0.0090126 | ML: above threshold (no LLM available) — 0.009 |  | 0.0090126 | 0 | 0
2026-03 | 2026-03-23 | Holland Landing Well No. 2 | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer -influent 10:55: 2.66mg/l grab: 2.56mg/l - adjusted -effluent 11:00: 2.38mg/l grab: 2.38mg/l -treated free 11:05: 0.15mg/l grab: 0.15mg/l -treated total 11:10: 3.12mg/l grab: 3.10mg/l -reagents all ok -Sharon grab 11:15: 1.39mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052928 | 0 | 0
2026-03 | 2026-03-17 | Holland Landing Well No. 2 | WEST | On site to change chlorine cylinder. | FLAG | stage2_low_confidence | 0.012138 | ML: above threshold (no LLM available) — 0.012 |  | 0.012138 | 0 | 0
2026-03 | 2026-03-27 | Holland Landing Well No. 2 | WEST | On site for station check Residuals Treated Total Grab: 3.32mg/L Analyzer: 3.20mg/L Treated Free Grab: 0.16mg/L, Analyzer: 0.16mg/L Effluent Free Grabs: 2.58mg/L, Analyzer: 2.62mg/L Influent Free Grabs: 2.76mg/L, Analyzer: 2.74mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.38mg/L Mono 2.59mg/L FA 0.00mg/L TA 0.51mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0017552 | 0 | 0
2026-03 | 2026-03-26 | Holland Landing Well No. 2 | WEST | -on site to investigate chlorinated to opening to 100% -checked trends - appeared influent dropped causing unit to run to 100% -switched chlorinator and observed switch over no issues -no issues with regulators as well - purged air from ammonia pump 1 | FLAG | stage2_low_confidence | 0.012086 | ML: above threshold (no LLM available) — 0.012 |  | 0.012086 | 0 | 0
2026-03 | 2026-03-18 | Holland Landing Well No. 2 | WEST | -on site for station check and weekly bacti W11673090 -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 13:45 : 2.68mg/l grab: 2.64mg/l -effluent 13:50: 2.44mg/l grab: 2.42mg/l -treated free 13:55: 0.14mg/l grab: 0.12mg/l -treated total: 14:00: 3.14mg/l grab: 3.12mg/l -reagents all ok -investigated ammonia pump 1 - airlocks - purged air -investigated ammonia pump 2 - found air relief valve passing - cleaned check valves and stop leaking | FLAG | stage2_low_confidence | 0.015796 | ML: above threshold (no LLM available) — 0.016 | leak [infrastructure]; leaking [infrastructure] | 0.015796 | 0 | 0
2026-03 | 2026-03-09 | Holland Landing Well No. 2 | WEST | On site for station check Residuals Treated Total Grab: 2.68mg/L Analyzer: 2.71mg/L Treated Free Grab: 0.12mg/L, Analyzer: 0.11mg/L Effluent Free Grabs: 0.22mg/L, Analyzer: 0.19mg/L Influent Free Grabs: 3.16mg/L, Analyzer: 3.18mg/L Sharon Valve grab Total Chlorine 1.83mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036724 | 0 | 0
2026-03 | 2026-03-10 | Holland Landing Well No. 2 | WEST | -on site to change cylinder -32.2kg -100.2kg | FLAG | stage2_low_confidence | 0.0079941 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079941 | 0 | 0
2026-03 | 2026-03-12 | Holland Landing Well No. 2 | WEST | On site for the following HLW2, JHSC Health and Safety Inspection, Holland Landing Well 2 (1M) HLW2, Chlorine Gas Detector, Test, Holland Landing, Well 2 (1M) HLW2, Chlorine Analyzer Maintenance, Holland Landing, Well 2 (1M) HLW2, Silicate Peristaltic Pump Inspection, Holland Landing Well 2 (1200 Hrs.) HLW2, Chemical System Inspection - Chlorine, Holland Landing W2 (1M) HLW2, Pressure Relief Valve, Maintenance, Holland Landing, Well 2 (1M) HLW2, Chlorine Scrubber, Check, Holland Landing, Well 2 (1M) HLW2, Low/High Temperature Alarm, Test, Holland Landing Well 2 (1M) HLW2, Turbidimeter, Maintenance, Holland Landing, Well 2 (1M) HLW2, HLW2 Chemical System Inspection - Silicate, Holland Landing W2 (1M) HLW2, Chemical System Inspection - Ammonia, Holland Landing Well 2 (1M) HLW2, Pressure Relief Valve, Maintenance, Holland Landing, Well 2 (1M) HLW2, Eye Wash, Cleaning & Solution Replacement, Holland Landing Well 2 (6M) HLW2, Ammonia Diaphragm Pump Inspection, Holland Landing W2 (1200 Hrs.) Changed out effluent free reagents. No issues on site | FLAG | stage2_low_confidence | 0.019594 | ML: above threshold (no LLM available) — 0.02 | alarm [control_system] | 0.019594 | 0 | 0
2026-03 | 2026-03-06 | Holland Landing Well No. 2 | WEST | On site for station check Residuals Treated Total Grab: 3.04mg/L Analyzer: 2.95mg/L Treated Free Grab: 0.15mg/L, Analyzer: 0.13mg/L Effluent Free Grabs: 2.38mg/L, Analyzer: 2.32mg/L Influent Free Grabs: 2.44mg/L, Analyzer: 2.51mg/L Performed advanced monitoring (SL1000) Mono 2.32mg/L FA 0.00mg/L TA 0.44mg/L Sharon Valve grab Total Chlorine 2.02mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.001763 | 0 | 0
2026-03 | 2026-03-17 | Holland Landing Well No. 2 | WEST | **entrys not remote just was put in hlw1 elog by mistake** On site for station check Residuals Treated Total Grab: 1.50mg/L Analyzer: 1.45mg/L Treated Free Grab: 0.05mg/L, Analyzer: 0.03mg/L Effluent Free Grabs: 0.93mg/L, Analyzer: 0.83mg/L Influent Free Grabs: 2.58mg/L, Analyzer: 2.57mg/L No issues on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0015798 | 0 | 0
2026-03 | 2026-03-11 | Holland Landing Well No. 2 | WEST | On site for station check Residuals Treated Total Grab: 2.68mg/L Analyzer: 2.71mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.13mg/L Effluent Free Grabs: 2.30mg/L, Analyzer: 2.37mg/L Influent Free Grabs: 2.52mg/L, Analyzer: 2.59mg/L Sharon Valve grab | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039431 | 0 | 0
2026-03 | 2026-03-03 | Holland Landing Well No. 2 | WEST | - change chlorine cylinder 35.6kg - 103.6kg | FLAG | stage2_low_confidence | 0.010152 | ML: above threshold (no LLM available) — 0.01 |  | 0.010152 | 0 | 0
2026-03 | 2026-03-31 | Holland Landing West Elevated Tank | WEST | Onsite to troubleshoot Post Injection AIT. Informed ROC. Noticed the Post Injection AIT lost the program. Cycled the power, reprogrammed the AIT and Enabled analog outputs. Readings came back to normal. No issues. Noticed there was minimal flow to the Post-free AIT. removed the diaphragm and cleaned it. put it back in service. Flow much better. AL Post total AIT - 2.32 mg/l AL POST free AIT - 0.08 mg/l Put the POST AIT back in service. No issues. Informed ROC, Armed the building and left the site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039009 | 0 | 0
2026-03 | 2026-03-31 | Holland Landing West Elevated Tank | WEST | Respond to site power failure, comm failures. Unable to access electrical room, ekey is validated. Re-validated ekey and gained access 0450. All breakers in HLPSYS, HLETYS pipe gallery and electrical room are in closed positions, no obvious signs of tripped equipment (LPA, fed from LPB, all appears normal). Communicated with on call electrician, currently responding to multiple power outages and priority calls. There is a manual transfer switch that can be used with portable generator if necessary (requires electrician for transfer). Power restored approximately 0540. Outstanding historian heartbeat alarm, and post-inj analyzer value on SCADA is OOR. Analyzer is powered on and appears to be working. Cycled power to analyzer. Unable to calibrate Post Depolox Cl analyzer; -calibration menu shows ?bias? set at 7.50mg/L instead of span calibrate option. Grabs: mg/L Post 0558 Grab: FCl 0.04 tcl 2.36 Analyzer: FCl 0.06 tcl 3.60 Pre 0604 G: FCl 0.05 tcl 2.30 A: FCl 0.08 tcl 2.38 Request INST troubleshoot post-injection chlorine analyzer (CMU to be issued). Request w-MAINT inspect issue with site power out while generator was running. | FLAG | stage2_low_confidence | 0.03137 | ML: above threshold (no LLM available) — 0.031 | failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; scada [control_system]; alarm [control_system] | 0.03137 | 0 | 0
2026-03 | 2026-03-31 | Holland Landing West Elevated Tank | WEST | On site to complete station checks and collect bacti sample w11706016 Verified analyzers @09:15 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.08mg/L Total chlorine Grab: 2.36mg/L Analyzer: 2.35mg/L Post-Injection - inst on site to fix analyzer Free chlorine Grab: 0.05mg/L Analyzer: 0.08mg/L Total chlorine Grab: 2.32mg/L Analyzer 2.35mg/L No other issues on site - wells off unable to do advanced monitoring | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00085113 | 0 | 0
2026-03 | 2026-03-13 | Holland Landing West Elevated Tank | WEST | On site to complete station checks Verified analyzers @ 11:27 Pre-injection Free chlorine Grab: 0.04mg/L Analyzer: 0.04mg/L Total chlorine Grab: 1.71mg/L Analyzer: 1.77mg/L Mono 0.37mg/L FA 0.28mg/L TA 0.35mg/L Nitrite 0.009mg/L Post-Injection Free chlorine Grab: 0.04mg/L Analyzer: 0.02mg/L SL1000 Total chlorine Grab: 2.64mg/L Analyzer 2.77mg/L Mono 1.62mg/L FA 0.19mg/L TA 0.50mg/L Nitrite 0.000mg/L Tank TCL 1.61mg/L Mono 0.42mg/L Nitrite 0.009mg/L FA 0.30mg/L TA 0.38mg/L Nitrate 0.066mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 5.3895e-05 | 0 | 0
2026-03 | 2026-03-01 | Holland Landing West Elevated Tank | WEST | 14:47-logged in remotely to investigate pre injection low cl2 After discussion with ORO, decided to run the system till pre total cl2 go below 0.45 mg/L or Post total cl2 goes above 4.00 mg/L and hold the value for more than 2 minutes. | FLAG | stage2_low_confidence | 0.0076133 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076133 | 0 | 0
2026-03 | 2026-03-04 | Holland Landing West Elevated Tank | WEST | On site to complete station check and to collect w11637907 Verified analyzers @0830 Pre-injection while draining Free chlorine Grab: 0.04mg/L Analyzer: 0.05mg/L Total chlorine Grab: 2.40mg/L Analyzer: 2.44mg/L SL1000 while filling as of 08:39hrs Mono 0.44mg/L FA 0.10mg/L TA 0.18mg/L Nitrite 0.004mg/L Post-Injection Free chlorine Grab: 0.08mg/L Analyzer: 0.06mg/L Total chlorine Grab: 2.57mg/L Analyzer 2.88mg/L SL1000 Mono 1.35mg/L FA 0.00mg/L TA 0.26mg/L Nitrite 0.000mg/L Tank TCL 1.70mg/L Mono 0.45mg/L Nitrite 0.004mg/L FA 0.13mg/L TA 0.22mg/L Nitrate 0.128mg/L Reran, post injection ammonia @09:45hrs Mono 1.80mg/L FA 0mg/L TA 0.30mg/L Reagents all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 2.8566e-05 | 0 | 0
2026-03 | 2026-03-02 | Holland Landing West Elevated Tank | WEST | -on site to complete station check -checked trends: all ok -entered reading in PWQ: all ok -verified post injection 11:55 -analyzer free: 0.06mg/l grab: 0.07mg/l -analyzer total: 2.58mg/l grab: 2.54 mg/l -reagents all ok -verified pre injection 12:05 -analyzer free: 0.05mg/l grab: 0.03mg/l -analyzer total: 2.77mg/l grab: 2.74mg/l -reagents all ok -completed water quality lab | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050408 | 0 | 0
2026-03 | 2026-03-11 | Holland Landing West Elevated Tank | WEST | On site to complete station check and complete BacT sampling, W11658071 Verified analyzers @ 10:35 Pre-injection Free chlorine Grab: 0.08mg/L Analyzer: 0.05mg/L Total chlorine Grab: 1.88mg/L Analyzer: 1.78mg/L Mono 0.38mg/L FA 0.17mg/L TA 0.24mg/L Nitrite 0.005mg/L Post-Injection Free chlorine Grab: 0.04mg/L Analyzer: 0.03mg/L SL1000 Total chlorine Grab: 2.95mg/L Analyzer 3.13mg/L Mono 1.76mg/L FA 0.07mg/L TA 0.42mg/L Nitrite 0.002mg/L Tank TCL 1.69mg/L Mono 0.43mg/L Nitrite 0.003mg/L FA 0.23mg/L TA 0.32mg/L Nitrate 0.093mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 6.6999e-05 | 0 | 0
2026-03 | 2026-03-04 | Holland Landing West Elevated Tank | WEST | On site to respond to fault on tank mixer VFD panel. Upon inspection found burnt wire connections inside VFD control panel. Assessed that a temporary repair could be made and executed said repair. Documented findings and repair for possible warranty claim. | FLAG | stage2_low_confidence | 0.094015 | ML: above threshold (no LLM available) — 0.094 | fault [equipment_failure]; repair [maintenance_action] | 0.094015 | 0 | 0
2026-03 | 2026-03-06 | Holland Landing West Elevated Tank | WEST | On site to complete station check Verified analyzers @0900hrs Pre-injection Free chlorine Grab: 0.03mg/L Analyzer: 0.03mg/L Total chlorine Grab: 1.35mg/L Analyzer: 1.40mg/L Mono 0.26mg/L FA 0.21mg/L TA 0.24mg/L Nitrite 0.000mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.03mg/L SL1000 Total chlorine Grab: 3.13mg/L Analyzer 2.12mg/L Mono 2.01mg/L FA 0.10mg/L TA 0.49mg/L Nitrite 0.002mg/L Tank TCL 1.60mg/L Mono 0.48mg/L Nitrite 0.002mg/L FA 0.13mg/L TA 0.23mg/L Nitrate 0.099mg/L Reagents all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 4.0464e-05 | 0 | 0
2026-03 | 2026-03-05 | Holland Landing West Elevated Tank | WEST | On site to complete the following: HLETYS, High & Low Water Level Alarm, Test, Holland Landing West ET (2M) HLETYS, Sensing Line Heat Trace System, Maintenance, Holland Landing West, ET [WINTER] (1M) HLETYS, Low Temperature Alarm, Test, Holland Landing West, ET (1M) HLETYS, Ammonia System Inspection, Holland Landing West ET (1M) HLETYS, Sodium Hypochlorite System Inspection, Holland Landing West ET (1M) HLETYS, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Holland Landing West ET (1M) HLETYS, Sump Pit System Inspection, Holland Landing West ET (1M) HLETYS, Comprehensive Housekeeping, Holland Landing West ET (1M) No issues found Replaced acetate in post analyzer | FLAG | stage2_low_confidence | 0.014186 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system] | 0.014186 | 0 | 0
2026-03 | 2026-03-03 | Holland Landing West Elevated Tank | WEST | -on site to respond to mixer uncommanded stop / fault alarms -found mixer with F021 output phase loss fault -tried to reset but fault immediately comes back in -informed CMS to investigate | FLAG | stage2_low_confidence | 0.022733 | ML: above threshold (no LLM available) — 0.023 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.022733 | 0 | 0
2026-03 | 2026-03-09 | Holland Landing West Elevated Tank | WEST | On site to complete station check Verified analyzers @1005hrs Pre-injection Free chlorine Grab: 0.03mg/L Analyzer: 0.03mg/L Total chlorine Grab: 1.52mg/L Analyzer: 1.63mg/L Mono 0.39mg/L FA 0.23mg/L TA 0.30mg/L Nitrite 0.005mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.02mg/L SL1000 Total chlorine Grab: 1.68mg/L Analyzer 1.88mg/L Mono 0.40mg/L FA 0.24mg/L TA 0.32mg/L Nitrite 0.006mg/L * chemical dosing turned off as flow was less than 20L/s going into the tower Tank TCL 1.75mg/L Mono 0.48mg/L Nitrite 0.004mg/L FA 0.18mg/L TA 0.27mg/L Nitrate 0.118mg/L Reagents all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 4.0593e-05 | 0 | 0
2026-03 | 2026-03-25 | Holland Landing West Elevated Tank | WEST | On site to complete station checks and collect bacti sample w11690350 Verified analyzers @09:40 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.04mg/L Total chlorine Grab: 1.78mg/L Analyzer: 1.98mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.02mg/L SL1000 Total chlorine Grab: 2.84mg/L Analyzer 3.08mg/L All Readings entered into pwq sheet | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00054623 | 0 | 0
2026-03 | 2026-03-23 | Holland Landing West Elevated Tank | WEST | -on site to re-verify pre total reading 14:20 -analyzer 2.84mg/l - grab: 2.46mg/l - adjusted | FLAG | stage2_low_confidence | 0.0083249 | ML: above threshold (no LLM available) — 0.008 |  | 0.0083249 | 0 | 0
2026-03 | 2026-03-18 | Holland Landing West Elevated Tank | WEST | -on site for station check and weekly bacti W11673909 -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer -post analyzer 09:45 -free: 0.03mg/l grab: 0.06mg/l -total: 2.56mg/l grad 2.60mg/l -topped up reagents -pre analyzer 10:00 -free: 0.06mg/l grab: 0.05mg/l -total: 2.28mg/l grab: 2.48mg/l - adjusted -topped up reagents -equipment all ok -will follow up with team lead regarding water quality results | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046067 | 0 | 0
2026-03 | 2026-03-27 | Holland Landing West Elevated Tank | WEST | On site for station check Verified analyzers Readings in pwq sheet - adjusted inlet free ammonia from 0.30-0.25mg/L as post ammonia grabs were low Reagents all okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055323 | 0 | 0
2026-03 | 2026-03-23 | Holland Landing West Elevated Tank | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified pre analyzer 12:20 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 1.13mg/l grab: 1.30mg/l -reagents all ok -verified post analyzer 12:40 -analyzer free: 0.01mg/l grab: 0.03mg/l -analyzer total: 2.83mg/l grab: 2.80mg/l -reagents all ok -made following adjustments - hypo pump 1 195- 175ml/min -hypo pump 2 195 - 185ml/min -inlet free ammonia 0.25mg/l - .30mg/l -topped up hypo tank - 249-304L -no other issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037644 | 0 | 0
2026-03 | 2026-03-16 | Holland Landing West Elevated Tank | WEST | On site to complete station checks Verified analyzers @ 10:30 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.04mg/L Total chlorine Grab: 1.79mg/L Analyzer: 1.70mg/L Mono 0.42mg/L FA 0.24mg/L TA 0.32mg/L Nitrite 0.006mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.03mg/L SL1000 Total chlorine Grab: 3.14mg/L Analyzer 3.29mg/L Mono 1.69mg/L FA 0.0.03mg/L TA 0.0.36mg/L Nitrite 0.000mg/L Tank TCL 1.85mg/L Mono 0.48mg/L Nitrite 0.004mg/L FA 0.24mg/L TA 0.33mg/L Nitrate 0.134mg/L Adjusted pre free ammonia on scada from 0.28-0.25mg/L based off the pre and post results above. Topped up ammonia tank from 38-68cms | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 6.1629e-05 | 0 | 0
2026-03 | 2026-03-20 | Holland Landing West Elevated Tank | WEST | -on site to complete station check -checked trends: all ok -entered readings in PWQ -verified analyzer -pre injection 13.20 -analyzer free: 0.03mg/l grab: 0.04mg/l -analyzer total: 1.20mg/l grab: 1.28mg/l- adjusted -reagents all ok -post injection 13:30 -analyzer free 0.02mg/l grab: 0.04mg/l -analyzer total: 3.02mg/l grab: 3.00mg/l -reagents all ok -due to high incoming ammonia adjusted hypo pump 2 195ml/min to 185ml/min - will monitor -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050966 | 0 | 0
2026-03 | 2026-03-24 | Holland Landing West Elevated Tank | WEST | -on site to meet hypo delivery -290 - 600 - top up level bouncing due to high level | FLAG | stage2_low_confidence | 0.0097302 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097302 | 0 | 0
2026-03 | 2026-03-30 | Jefferson Pumping Station & Reservoir | WEST | conducted station check checked trends: all ok Station duty active; Pump 1 and 4 running. 11:50- Grabs taken Grab free Cl2: 0.08mg/l Grab total Cl2: 2.00mg/l equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00519 | 0 | 0
2026-03 | 2026-03-31 | Jefferson Pumping Station & Reservoir | WEST | On site to complete station check, operational sample and weekly bacti W11705742 Checked trends: all ok Took chlorine grab and sample West cell 14:45 Free CL2: 0.06mg/l Total CL2: 2.02mg/l East cell 14:50 Free CL2: 0.05mg/l Total CL2: 2.10 mg/l Equipment all ok Entered reading PWQ: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005069 | 0 | 0
2026-03 | 2026-03-31 | Jefferson Pumping Station & Reservoir | WEST | -Responded P1,P2, P3 fault alarm -P1 control voltage low, P2 &P3 valve fail to open - reset alarms in MCC - P1 started in auto duty 1 | FLAG | stage2_low_confidence | 0.032811 | ML: above threshold (no LLM available) — 0.033 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.032811 | 0 | 0
2026-03 | 2026-03-03 | Jefferson Pumping Station & Reservoir | WEST | -reset power alarms -generator currently -pump 3 fail to start - will attend | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-10 | Jefferson Pumping Station & Reservoir | WEST | On site for the following PM work orders. Informed ROC about the works being done. W11650338 JFPS, Standby Power Generator Test Run and Run Hours log Pre check Battery okay- 26.52V Coolant- Okay Oil - Okay Before Start Start time- 09:45 Run time- 671.1 hr Fuel level-9023L/167.2cm JFPS pump 3 running manual. After Stop Stop time- 11:00 Run time- 672.6 hr Fuel level-8963L/165.9 cm W11651916 JFPS, Dehumidifier Inspection & Cleaning, W11650352 JFPS, Sump Pit System Inspection W11650887 JFPS, Manual Valves Exercise W11650901 JFPS, Actuated Valves Exercise & Inspection, W11651273 JFPS, Pump & Motor Inspection W11651760 JFPS, Ventilation System Inspection W11651770 JFPS, Low Temperature Alarm Test W11651781 JFPS, Hoist System Inspection W11650643 JFRS, Sump Pit System Inspection W11650656 JFRS, Ventilation System Inspection W11651841 JFRS, Dehumidifier Inspection & Cleaning, W11651235 JFRS, JHSC Health and Safety Inspection, W11652030 JFRS, External Venting Screens Inspection, W11651245 JFRS, Sump Pit System Inspection, ValveHouse W11651258 JFRS, Actuated Valve Exercise & Inspection,ValveHouse W11651722 JFRS, Flood Alarm Test Jefferson Valve House, ValveHouse W11651732 JFRS, Manual Valves Exercise, Jefferson, ValveHouse W11651746 JFRS, Dehumidifier Inspection & Cleaning,ValveHouse | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | Jefferson Pumping Station & Reservoir | WEST | -on site to complete station check and weekly bacti W11637582 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample from west cell 14:15 -free cl: 0.08mg/l -total cl: 2.01mg/l -east cell chlorine grab 14:20 -free cl: 0.11mg/l -total cl: 1.95mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052577 | 0 | 0
2026-03 | 2026-03-06 | Jefferson Pumping Station & Reservoir | WEST | On site for station check Check trends; All okay Station duty active; Pump 3 & 4 running 14:05 grabs taken Free cl2- 0.07 mg/l total cl2- 1.84 mg/l entered values in PWQ sheet. equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044394 | 0 | 0
2026-03 | 2026-03-09 | Jefferson Pumping Station & Reservoir | WEST | On site for station check Check trends; All okay Station duty active; Pump 3 & 4 running 14:44 grabs taken Free cl2- 0.04 mg/l total cl2- 1.79 mg/l entered values in PWQ sheet. equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044394 | 0 | 0
2026-03 | 2026-03-03 | Jefferson Pumping Station & Reservoir | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 10:00 -free cl: 0.07mg/l -total cl: 2.05mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047077 | 0 | 0
2026-03 | 2026-03-17 | Jefferson Pumping Station & Reservoir | WEST | Vibration readings | FLAG | stage2_low_confidence | 0.021831 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021831 | 0 | 0
2026-03 | 2026-03-11 | Jefferson Pumping Station & Reservoir | WEST | On site to complete station check and weekly bacti W11657067 Checked trends: all ok Took chlorine grab and sample East cell 14:00 Free CL2: 0.05mg/l Total CL2: 2.04mg/l West cell 14:00 Free CL2: 0.03mg/l Total CL2: 2.00 mg/l Equipment all ok Entered reading PWQ: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046368 | 0 | 0
2026-03 | 2026-03-20 | Jefferson Pumping Station & Reservoir | WEST | Chris Iliohan Tyler Smith into take Pump 2 out of service. Rebuild is required | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-23 | Jefferson Pumping Station & Reservoir | WEST | Station Check (pumping station) (no issues found) Input data to PWQ 14:00 Chlorine grab (mg/l) Free: 0.04, Total 1.99 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057269 | 0 | 0
2026-03 | 2026-03-27 | Jefferson Pumping Station & Reservoir | WEST | On site for station check Check trends; All okay Station duty active; Pump 3 & 4 running 14:45 grabs taken Free cl2- 0.06 mg/l total cl2- 2.03 mg/l entered values in PWQ sheet. equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044394 | 0 | 0
2026-03 | 2026-03-27 | Jefferson Pumping Station & Reservoir | WEST | Vibration readings and grease pump 1 and two | FLAG | stage2_low_confidence | 0.018888 | ML: above threshold (no LLM available) — 0.019 | vibration [equipment_failure] | 0.018888 | 0 | 0
2026-03 | 2026-03-24 | Jefferson Pumping Station & Reservoir | WEST | Vibration readings 3 and 4 Help with pump 2 | FLAG | stage2_low_confidence | 0.015715 | ML: above threshold (no LLM available) — 0.016 | vibration [equipment_failure] | 0.015715 | 0 | 0
2026-03 | 2026-03-18 | Jefferson Pumping Station & Reservoir | WEST | On site to complete station check, operational sample and weekly bacti W11672961 Checked trends: all ok Took chlorine grab and sample West cell 14:45 Free CL2: 0.01mg/l Total CL2: 1.88mg/l East cell 14:40 Free CL2: 0.07mg/l Total CL2: 1.95 mg/l Equipment all ok Entered reading PWQ: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005069 | 0 | 0
2026-03 | 2026-03-20 | Jefferson Pumping Station & Reservoir | WEST | On site for station check Check trends; All okay Station duty active; Pump 1 & 4 running 14:22 grabs taken Free cl2- 0.00 mg/l total cl2- 2.17 mg/l entered values in PWQ sheet. equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044394 | 0 | 0
2026-03 | 2026-03-25 | Jefferson Pumping Station & Reservoir | WEST | On site to complete station check and weekly bacti W11690336 Checked trends: all ok Took chlorine grab and sample East cell 14:50 Free CL2: 0.02mg/l Total CL2: 2.06mg/l West cell 14:55 Free CL2: 0.05mg/l Total CL2: 2.06 mg/l Equipment all ok Entered reading PWQ: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046368 | 0 | 0
2026-03 | 2026-03-16 | Jefferson Pumping Station & Reservoir | WEST | On site for station check Check trends; All okay Station duty active; Pump 3 & 4 running 14:00 grabs taken Free cl2- 0.07 mg/l total cl2- 2.07 mg/l entered values in PWQ sheet. equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044394 | 0 | 0
2026-03 | 2026-03-25 | Jefferson Pumping Station & Reservoir | WEST | - on site to reconnect pump 2. connected and tested to confirm rotation. left pump in manual off for the time being and let Cole W know that we should put an interm procedure in to run that pump an hour a day for a week to break in the bearings. under direction of oic | FLAG | stage2_low_confidence | 0.027841 | ML: above threshold (no LLM available) — 0.028 |  | 0.027841 | 0 | 0
2026-03 | 2026-03-30 | King City Dufferin Booster Pumping Station | WEST | Restarted the Operator Interface Terminal due to Windows Operating System software updates. | FLAG | stage2_low_confidence | 0.0073957 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073957 | 0 | 0
2026-03 | 2026-03-25 | Holland Landing Well No. 2 | WEST | On site for station check and bacti sample w11690350 Residuals Treated Total Grab: 2.98mg/L Analyzer: 3.07mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.16mg/L Effluent Free Grabs: 2.35mg/L, Analyzer: 2.28mg/L Influent Free Grabs: 3.52mg/L, Analyzer: 3.39mg/L Performed advanced monitoring (SL1000) Mono 2.34mg/L FA 0.05mg/L TA 0.51mg/L Changed out chlorine cylinder 1 with Tim Hudson from 0-68kg Changed out treated total reagents Treated total analyzer climbing took another grab at 13:35hrs of 3.44mg/L adjusted analyzer from 3.65-3.44mg/L after multiple grabs | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029612 | 0 | 0
2026-03 | 2026-03-01 | Holland Landing West Elevated Tank | WEST | On site to investigate pre injection low cl2 - CMU W11697567. Up on initial assessment, identified the pre injection analyzer ran out of acetate buffer solution. Topped the acetate buffer solution and waited for the value to climb up naturally. 17:30- verified post injection analyzer Grab free Cl2- 0.04 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 2.56 mg/L Analyzer Total Cl2- 2.55 mg/L 17:38- verified pre injection analyzer Grab free Cl2- 0.05 mg/L (Avg 0.04,0.05,0.06) Analyzer free Cl2- 0.06 mg/L Adjusted analyzer down to 0.05 mg/l Grab Total Cl2- 2.50 mg/L Analyzer Total Cl2- 2.55 mg/L Activated duty. Cl2 pump kicked on, post injection total values climbing. Everything looks normal. Pre inj Low cl2 was due to analyzer malfunction. | FLAG | stage2_low_confidence | 0.0083261 | ML: above threshold (no LLM available) — 0.008 |  | 0.0083261 | 0 | 0
2026-03 | 2026-03-13 | King City Dufferin Booster Pumping Station | WEST | Station check (no issues found) entered data to PWQ 10:00 Chlorine Residual Grab (mg/L) Free 0.03, Total 1.70 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006623 | 0 | 0
2026-03 | 2026-03-06 | King City Dufferin Booster Pumping Station | WEST | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 14:05 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.80 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036632 | 0 | 0
2026-03 | 2026-03-09 | King City Dufferin Booster Pumping Station | WEST | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 09:43 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.82 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036632 | 0 | 0
2026-03 | 2026-03-19 | King City Dufferin Booster Pumping Station | WEST | Check no hot water 600 V sending electrician to service unit | FLAG | stage2_low_confidence | 0.0092522 | ML: above threshold (no LLM available) — 0.009 |  | 0.0092522 | 0 | 0
2026-03 | 2026-03-20 | King City Dufferin Booster Pumping Station | WEST | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 09:41 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.74 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035942 | 0 | 0
2026-03 | 2026-03-23 | King City Dufferin Booster Pumping Station | WEST | On site to troubleshoot and repair tankless water heater. Found flow switch out of adjustment. Corrected and tested for proper operation. | FLAG | stage2_low_confidence | 0.034412 | ML: above threshold (no LLM available) — 0.034 | repair [maintenance_action] | 0.034412 | 0 | 0
2026-03 | 2026-03-27 | King City Dufferin Booster Pumping Station | WEST | -on site for station check -check trends: -entered reading in PWQ: all ok -took chlorine grab:08:30 -free cl: 0.08mg/l -total cl: 1.52mg/l -started sump pump at KCETDS to clear flood alarm -no other issues | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | King City Dufferin Booster Pumping Station | WEST | In to complete station check. Enter data into PWQ. No issues. | FLAG | stage2_low_confidence | 0.012116 | ML: above threshold (no LLM available) — 0.012 |  | 0.012116 | 0 | 0
2026-03 | 2026-03-31 | King City Dufferin Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 75 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:36 - Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.74 mg/L 13:36 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.68 mg/L MCL = 1.53 mg/L TNH3 = 0.36 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 6.9 C 13:43 - collected weekly regulatory micro. sample - W/O # W11705494 -recorded readings in PWQ sheet -no issues found -ran meter chamber sump pump in local | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0026424 | 0 | 0
2026-03 | 2026-03-02 | King City Dufferin Booster Pumping Station | WEST | -on site to complete station check -system duty not active -found pump 2 discharge valve stuck open, closed valve and returned to auto -tested both pumps due to multiple fail to start alarms, no issues observed -checked equipment -reviewed trends -recorded readings in PWQ sheet -pump #1 hours = 6991.1 -pump #2 hours = 6621.8 -checked residuals: 09:12 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.85 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system]; valve stuck [infrastructure] | 0.0054485 | 0 | 0
2026-03 | 2026-03-13 | King City Dufferin Booster Pumping Station | WEST | Responded to Meter chamber flood alarm. Pump not running in auto, ran in hand and verified flow, pumped below flood level and placed back in auto | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; not running [equipment_failure]; alarm [control_system]; pump not running [infrastructure] | flood [critical]; not running [equipment_failure]; alarm [control_system]; pump not running [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | King City Dufferin Booster Pumping Station | WEST | -on site to complete work orders -completed JHSC Health and Safety Inspection -found water heater not producing tempered water for eyewash, created work order for CMS -completed Critical Air Valve Flush and Inspection | FLAG | stage2_low_confidence | 0.021361 | ML: above threshold (no LLM available) — 0.021 | work order [maintenance_action] | 0.021361 | 0 | 0
2026-03 | 2026-03-16 | King City Dufferin Booster Pumping Station | WEST | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 13:19 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.78 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036632 | 0 | 0
2026-03 | 2026-03-11 | King City Dufferin Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 67 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:16 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.65 mg/L 13:16 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.68 mg/L MCL = 1.59 mg/L TNH3 = 0.36 mg/L FNH3 = 0.05 mg/L NO2 = 0.004 mg/L temp = 7.0 C 13:21 - collected weekly regulatory micro. sample - W/O # W11657053 -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0031505 | 0 | 0
2026-03 | 2026-03-23 | King City Dufferin Elevated Tank | WEST | On site to replace UPS batteries inside PAC panel. Site was offline due to planned maintenance, After the batteries were replaced, UPS was tested for 10 min on battery worked ok. | FLAG | stage2_low_confidence | 0.010436 | ML: above threshold (no LLM available) — 0.01 |  | 0.010436 | 0 | 0
2026-03 | 2026-03-18 | King City Dufferin Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 47 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:31 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.59 mg/L 13:31 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.62 mg/L MCL = 1.47 mg/L TNH3 = 0.36 mg/L FNH3 = 0.07 mg/L NO2 = 0.004 mg/L temp = 5.4 C 13:35 - collected weekly regulatory micro. sample - W/O # W11672783 -recorded readings in PWQ sheet -no issues found -ran meter chamber sump pump in local while on site -completed Eye Wash Cleaning & Solution Replacement | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0024731 | 0 | 0
2026-03 | 2026-03-23 | King City Dufferin Elevated Tank | WEST | In to start filling of KCETDS for sampling following condition assessment, cleaning, and disinfection. IAM / Landmark spray disinfected 200mg/L chlorine solution to storage at 1232. Flushed riser / drain piping and started filling 1310. Isolated ET at 1430, will continue filling tomorrow morning. | FLAG | stage2_low_confidence | 0.013479 | ML: above threshold (no LLM available) — 0.013 |  | 0.013479 | 0 | 0
2026-03 | 2026-03-25 | King City Dufferin Elevated Tank | WEST | -On-site to complete station check -tower currently isolated awaiting sample results post inspection -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:13 - Analyzer readings: Free Chlorine = 0.07 mg/L Total Chlorine = 2.11 mg/L 13:13 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.65/1.62/1.63 mg/L 13:23 - adjusted total chlorine analyzer to 1.63 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no issues found -ran meter chamber sump pump in local | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054259 | 0 | 0
2026-03 | 2026-03-20 | King City Dufferin Elevated Tank | WEST | -on site to isolate tower for inspection -closed inlet valve -put altitude valve into manual and isolated stem ball valve to pin closed -monitored system pressures -switched controlling tower to KCETFS and adjusted duty 60 - 80% 08:45 - tower level = 35%, open KCETFS isolation valve and close KCETDS outlet valve 08:46 - placed dechlorination pucks at tower outfall and began draining tower to waste at 10 l/s 09:20 - collected grab from drainage pond outlet, total chlorine = 0.00 mg/L -put site offline and powered off chlorine analyzers -added dechlorination pucks to tower outfall -leaving tower draining at 10 l/s, will monitor remotely | FLAG | stage2_low_confidence | 0.010064 | ML: above threshold (no LLM available) — 0.01 |  | 0.010064 | 0 | 0
2026-03 | 2026-03-17 | King City Dufferin Elevated Tank | WEST | On site to respond to reports of inlet line heat trace low temperature alarm. Found no active alarms. Verified proper operation of heat trace system. Verified proper unit configuration including set points. | FLAG | stage2_low_confidence | 0.023831 | ML: above threshold (no LLM available) — 0.024 | alarm [control_system]; alarms [control_system] | 0.023831 | 0 | 0
2026-03 | 2026-03-24 | King City Dufferin Elevated Tank | WEST | -on site to fill the tower to overflow and collect sample W11753096 -man/started pump at 100% at KCPSDs -opened altitude valve 100% -opened inlet isolation valve -no flow to system -flushed all sample taps and cleaned -turned on analyzer verified at 08:30 -analyzer total: 1.27mg/l grab: 1.67mg/l -primed analyzers -verified analyzer 10:15 -analyzer total: -analyzer free: -reagents all ok -added dechlor to pond for overflow -tower hit overflow at 10:15 -closed inlet valve/open tie valve - placed KCPSDS in auto -verified analyzer at 10:20 -analyzer free: 0mg/l grab: 0.03mg/l - unable to adjust analyzer -analyzer total: 1.51mg/l grab: 1.83mg/l - adjusted -reagents all ok - | FLAG | stage2_low_confidence | 0.010027 | ML: above threshold (no LLM available) — 0.01 | overflow [critical]; overflow [infrastructure] | 0.010027 | 0 | 0
2026-03 | 2026-03-12 | King City Dufferin Elevated Tank | WEST | -on site to complete work orders -informed ROC of work -completed CL17 Chlorine Analyzer, Maintenance 10:04 - analyzers in clean mode -cleaned analyzers, flushed sample lines -replaced tubing in TCL analyzer and primed 11:02 - collected grab: FCL = 0.00 mg/L TCL = 1.82 mg/L 11:43 - analyzers back online -verified analyzers after maintenance: 11:47 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.69 mg/L 11:47 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.65 mg/L -tested isolation of tower in preparation for taking tower offline for inspection/ maintenance -opened bypass valve and isolated inlet and outlet valves -monitored system pressures - ok -set KCETFS as controlling tower and activated system duty -no system issues observed running on KCETFS -completed Inlet/Outlet Heat Trace System, Inspection -completed JHSC Health and Safety Inspection -completed Actuated Valve, Exercise & Inspection -completed Low Temperature Alarm Test -completed Ventilation System, Inspection -completed High & Low Water Level Alarm, Test -completed Drain Valve Exercise -completed Dehumidifier, Cleaning & Inspection -returned tower valving to normal operation and set KCETDS to controlling tower -site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; work order [maintenance_action]; alarm [control_system] | bypass [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | King City Dufferin Elevated Tank | WEST | -on site to put tower back online after passing resultsW11753096 -verified analyzer 14:40 -analyzer free: 0.06mg/l grab: 0.08mg/l -analyzer total: 1.58mg/l grab: 1.68mg/l - adjusted -opened inlet and outlet isolation valves -close the tie valve -no issues -informed control panel | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066487 | 0 | 0
2026-03 | 2026-03-31 | King City Fisher Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty active, tower = 64 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 12:28 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.52 mg/L 12:28 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.63/1.61/1.63 mg/L SL1000 Readings: MCL = 1.49 mg/L TNH3 = 0.35 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 7.1 C 12:35 - collected weekly regulatory micro. sample - W/O # W11705494 12:38 - adjusted total chlorine analyzer to 1.62 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0036552 | 0 | 0
2026-03 | 2026-03-16 | King City Dufferin Elevated Tank | WEST | -on site to respond to meter chamber flood alarm -ran sump pump in local -cleared alarm -pump back in auto | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | King City Dufferin Elevated Tank | WEST | -On-site to complete station check and collect samples -system duty not active, tower = 46 % -checked equipment -reviewed trends -replaced CL17 reagents -verified chlorine analyzers: 13:54 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.60 mg/L 13:54 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.66 mg/L MCL = 1.54 mg/L TNH3 = 0.36 mg/L FNH3 = 0.06 mg/L NO2 = 0.003 mg/L temp = 6.2 C 13:59 - collected weekly regulatory micro. sample - W/O # W11637334 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0031278 | 0 | 0
2026-03 | 2026-03-17 | King City Fisher Elevated Tank | WEST | On site to complete monthly work orders including: -portable generator test run -valve exercising -prv inspection -low temperature alarm -housekeeping -analyzer maintenance -health and safety inspection -heat trace system inspection Station operation normal, no issues on site. | FLAG | stage2_low_confidence | 0.011898 | ML: above threshold (no LLM available) — 0.012 | work order [maintenance_action]; alarm [control_system] | 0.011898 | 0 | 0
2026-03 | 2026-03-18 | King City Fisher Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 47 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 12:15 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.63 mg/L 12:15 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.51/1.49/1.52 mg/L SL1000 Readings: MCL = 1.43 mg/L TNH3 = 0.35 mg/L FNH3 = 0.07 mg/L NO2 = 0.004 mg/L temp = 5.4 C 12:22 - collected weekly regulatory micro. sample - W/O # W11672783 12:24 - adjusted total chlorine analyzer to 1.51 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no issues found -closed tower isolation valve to test in preparation for KCETDS isolation, no issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0037033 | 0 | 0
2026-03 | 2026-03-04 | King City Fisher Elevated Tank | WEST | -On-site to complete station check and collect samples -system duty not active, tower = 44 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 13:21 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.58 mg/L 13:21 - Grabs: Free Chlorine = 0.01 mg/L Total Chlorine = 1.57 mg/L SL1000 Readings: MCL = 1.49 mg/L TNH3 = 0.36 mg/L FNH3 = 0.07 mg/L NO2 = 0.003 mg/L temp = 5.0 C 13:25 - collected weekly regulatory micro. sample - W/O # W11637334 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0033258 | 0 | 0
2026-03 | 2026-03-11 | King City Fisher Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty active, tower = 39 % -checked equipment -reviewed trends -replaced KI solution -verified chlorine analyzers: 11:46 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.40 mg/L 11:46 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.53/1.52/1.55 mg/L SL1000 Readings: MCL = 1.45 mg/L TNH3 = 0.36 mg/L FNH3 = 0.07 mg/L NO2 = 0.003 mg/L temp = 7.4 C 11:52 - collected weekly regulatory micro. sample - W/O # W11657053 11:55 - adjusted total chlorine analyzer to 1.53 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0036722 | 0 | 0
2026-03 | 2026-03-25 | King City Fisher Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 64 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 12:43 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.51 mg/L 12:43 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.49 mg/L SL1000 Readings: MCL = 1.48 mg/L TNH3 = 0.37 mg/L FNH3 = 0.08 mg/L NO2 = 0.004 mg/L 12:48 - collected weekly regulatory micro. sample - W/O # W11690322 -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0038316 | 0 | 0
2026-03 | 2026-03-25 | King City Fisher Elevated Tank | WEST | On site responding to power fail (Hydro one planned power shut down). Transferred power to portable generator. W11756686. 03:45 utility power restored, shut down generator and returned site to utility power. Freedom mobile on site inspecting equipment. | FLAG | stage2_low_confidence | 0.022419 | ML: above threshold (no LLM available) — 0.022 |  | 0.022419 | 0 | 0
2026-03 | 2026-03-31 | Kleinburg Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 76 % -checked equipment -reviewed trends 08:57 - collected grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 1.97 mg/L MCL = 1.88 mg/L TNH3 = 0.42 mg/L FNH3 = 0.05 mg/L NO2 = 0.003 mg/L temp = 7.4 C 09:01 - collected weekly regulatory micro. sample - W/O # W11705756 -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0032677 | 0 | 0
2026-03 | 2026-03-11 | Kleinburg Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 68 % -checked equipment -reviewed trends 08:02 - collected grab sample: Free Chlorine = 0.05 mg/L Total Chlorine = 1.88 mg/L MCL = 1.89 mg/L TNH3 = 0.46 mg/L FNH3 = 0.08 mg/L NO2 = 0.003 mg/L temp = 7.3 C 08:06 - collected weekly regulatory micro. sample - W/O # W11657170 -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0032677 | 0 | 0
2026-03 | 2026-03-04 | Kleinburg Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 73 % -checked equipment -reviewed trends 09:12 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.90 mg/L MCL = 1.86 mg/L TNH3 = 0.42 mg/L FNH3 = 0.05 mg/L NO2 = 0.004 mg/L temp = 6.6 C 09:17 - collected weekly regulatory micro. sample - W/O # W11637596 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0031525 | 0 | 0
2026-03 | 2026-03-10 | Kleinburg Elevated Tank | WEST | On site to complete monthly work orders. -low temp alarm -valve exercising -standby generator test run -health and safety inspection. | FLAG | stage2_low_confidence | 0.018664 | ML: above threshold (no LLM available) — 0.019 | work order [maintenance_action]; alarm [control_system] | 0.018664 | 0 | 0
2026-03 | 2026-03-25 | Kleinburg Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 79 % -checked equipment -reviewed trends 08:52 - collected grab sample: Free Chlorine = 0.05 mg/L Total Chlorine = 1.83 mg/L MCL = 1.92 mg/L TNH3 = 0.42 mg/L FNH3 = 0.04 mg/L NO2 = 0.004 mg/L 08:57 - collected weekly regulatory micro. sample - W/O # W11690439 -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0036444 | 0 | 0
2026-03 | 2026-03-02 | Kleinburg HWY 27 Booster Pumping Station | WEST | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -replaced KI reagent -pump #1 hours = 17888.5 -pump #2 hours = 17983.7 -pump #3 hours = 18646.2 -verified chlorine analyzers: 12:53 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.86 mg/L 12:53 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.97/1.96/1.95 mg/L 13:02 - adjusted total chlorine analyzer to 1.96 mg/L based on average of 3 grabs -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037716 | 0 | 0
2026-03 | 2026-03-04 | Kleinburg Elevated Tank | WEST | Under the direction of David Tarascio, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a Network panel. All three Booster Pumps were in manual off. There was a historian hrbt alarm due to OIT comm fail Provided 24 VDC power to new switch. There is a trend gap on SCADA between 12:16 PM to 12:47 PM due to this work. After the replacement, checked all the ports and reset the comm alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | Kleinburg Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 69 % -checked equipment -reviewed trends 08:41 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.85 mg/L MCL = 1.84 mg/L TNH3 = 0.42 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 5.7 C 08:45 - collected weekly regulatory micro. sample - W/O # W11672975 -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0032677 | 0 | 0
2026-03 | 2026-03-04 | Kleinburg HWY 27 Booster Pumping Station | WEST | Under the direction of David Tarascio, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a Network panel. All three Booster Pumps were in manual off. There was a historian hrbt alarm due to OIT comm fail Provided 24 VDC power to new switch. There is a trend gap on SCADA between 11:31 AM to 11:51 AM due to this work. After the replacement, checked all the ports and reset the comm alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-06 | Kleinburg HWY 27 Booster Pumping Station | WEST | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 11:15 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 2.00 mg/L 11:15 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 2.01 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041899 | 0 | 0
2026-03 | 2026-03-13 | Kleinburg HWY 27 Booster Pumping Station | WEST | Station Check (no issues found) Input data to PWQ 11:05 Verified Depolox (mg/l) Free: Grab 0.04, A 0.02 Total: Grab 1.88, A 1.91 (Acetate, & distilled/Ki top up) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049073 | 0 | 0
2026-03 | 2026-03-27 | Kleinburg HWY 27 Booster Pumping Station | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 11:50 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 2.06mg/l grab: 2.04mg/l -reagents all ok -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050908 | 0 | 0
2026-03 | 2026-03-16 | Kleinburg HWY 27 Booster Pumping Station | WEST | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 10:44 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.94 mg/L 10:44 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.89 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042691 | 0 | 0
2026-03 | 2026-03-23 | Kleinburg HWY 27 Booster Pumping Station | WEST | -on site to complete station check -system duty active, pumps 1 and 2 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 12:01 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 2.01 mg/L 12:01 - Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 2.02 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046699 | 0 | 0
2026-03 | 2026-03-20 | Kleinburg HWY 27 Booster Pumping Station | WEST | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 13:28 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 2.08 mg/L 13:28 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.04 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042691 | 0 | 0
2026-03 | 2026-03-10 | Kleinburg HWY 27 Booster Pumping Station | WEST | On site to complete monthly work orders. -pump and motor maintenance -chlorine analyzer maintenance -sump pit inspection -health and safety inspection -check valve inspection -prv inspection -low temp alarm | FLAG | stage2_low_confidence | 0.01503 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action]; alarm [control_system] | 0.01503 | 0 | 0
2026-03 | 2026-03-09 | Kleinburg HWY 27 Booster Pumping Station | WEST | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 13:24 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.93 mg/L 13:24 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.96 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042691 | 0 | 0
2026-03 | 2026-03-10 | Kleinburg Whisper Lane Booster Pumping Station | WEST | -on site to complete work orders -informed ROC of work -completed High/Low Temperature Alarm Test -completed Flood Alarm, Test -completed Pump and Motor, Inspection -completed Eye Wash, Solution Replacement -completed Pressure Relief Valve, Inspection -completed Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance -filled grit sand and electrolyte -flushed sample lines, checked flow rates -verified analyzers after maintenance: 13:26 - Analyzer readings: Free Chlorine = 0.10 mg/L Total Chlorine = 2.02 mg/L 13:26 - Grabs: Free Chlorine = 0.04/0.03/0.03 mg/L Total Chlorine = 2.00 mg/L 13:33 - adjusted free chlorine analyzer to 0.03 mg/L based on average of 3 grabs -site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-06 | Kleinburg Whisper Lane Booster Pumping Station | WEST | -on site to complete station check -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 11:34 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.93 mg/L 11:34 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.92 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045806 | 0 | 0
2026-03 | 2026-03-13 | Kleinburg Whisper Lane Booster Pumping Station | WEST | Station Check (no issues found) input data to PWQ 11:45 Verified Depolox (mg/l) Free: Grab 0.07, A 0.05 Total: Grab 1.76, A 1.78 (Acetate top up) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004565 | 0 | 0
2026-03 | 2026-03-27 | Kleinburg Whisper Lane Booster Pumping Station | WEST | -on site for station check -checked trend: all ok -entered readings in PWQ: all ok -verified analyzer 12:30 -analyzer free: 0.06mg/l grab: 0.04mg/l -analyzer total: 1.97mg/l grab: 1.95mg/l -reagents all ok -locally ran pump 1 &2: no issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054757 | 0 | 0
2026-03 | 2026-03-19 | Kleinburg Whisper Lane Booster Pumping Station | WEST | Check mechanical seal Seal leaking. Locating a replacement seal | FLAG | stage2_low_confidence | 0.019401 | ML: above threshold (no LLM available) — 0.019 | leak [infrastructure]; leaking [infrastructure] | 0.019401 | 0 | 0
2026-03 | 2026-03-23 | Kleinburg Whisper Lane Booster Pumping Station | WEST | -on site to complete station check -ran pump #3 in manual -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 11:35 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.84 mg/L 11:35 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.83 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042631 | 0 | 0
2026-03 | 2026-03-16 | Kleinburg Whisper Lane Booster Pumping Station | WEST | -on site to complete station check -checked equipment -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 11:03 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.87 mg/L 11:03 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.84 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050844 | 0 | 0
2026-03 | 2026-03-20 | Kleinburg Whisper Lane Booster Pumping Station | WEST | Station Check (no issues found) Input data to PWQ 10:00 Verified Depolox (mg/l) Free: Grab 0.05, A 0.06 Total: Grab 1.82, A 1.88 Depolox (new KI/distilled) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003974 | 0 | 0
2026-03 | 2026-03-09 | Kleinburg Whisper Lane Booster Pumping Station | WEST | -on site to complete station check -ran pump #4 in manual -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 12:56 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.83 mg/L 12:56 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.88 mg/L -small leak from pump #4 shaft seal, created work order for CMS -no other issues | FLAG | stage2_low_confidence | 0.014691 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action]; leak [infrastructure] | 0.014691 | 0 | 0
2026-03 | 2026-03-02 | Kleinburg Whisper Lane Booster Pumping Station | WEST | -on site to complete station check -ran pumps 1 and 2 in local -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -pump hours: #1 = 3976.0 #2 = 4499.2 #3 = 5566.7 #4 = 5449.4 -verified chlorine analyzers: 11:55 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.96 mg/L 11:55 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.93 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040788 | 0 | 0
2026-03 | 2026-03-11 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | Totalizer: 4906177 m3 Discharge pressure: 24.5 kPa Flow Rate: 10.6L/s Monitoring well: 219.4masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.4 masl Well 13 RPM: 2043 AMP: 4.9 %: 18 Level: 206.4 masl | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011648 | 0 | 0
2026-03 | 2026-02-19 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | Totalizer: 4888666m3 Discharge pressure: 27.18Kpa Flow Rate: 10.5 L/s Monitoring well: 219.2 masl Well 8 RPM: 2350 AMP: 5.3 %: 36 Level: 208.5 masl Well 13 RPM: 2043 AMP: 4.9 %: 17 Level: 206.6 masl | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011685 | 0 | 0
2026-03 | 2026-03-08 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | Attended site to top up generator fuel. Fuel level at 5/8 of a tank on arrival. Fuel level full Generator took approximately 100L of fuel. Complete. | FLAG | stage2_low_confidence | 0.00802 | ML: above threshold (no LLM available) — 0.008 |  | 0.00802 | 0 | 0
2026-03 | 2026-03-07 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | On site due to a power failure | FLAG | stage2_low_confidence | 0.0096245 | ML: above threshold (no LLM available) — 0.01 | failure [equipment_failure] | 0.0096245 | 0 | 0
2026-03 | 2026-03-07 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | On site due to power failure | FLAG | stage2_low_confidence | 0.021678 | ML: above threshold (no LLM available) — 0.022 | failure [equipment_failure] | 0.021678 | 0 | 0
2026-03 | 2026-02-13 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | Totalizer: 4883206m3 Discharge pressure: 25.11Kpa Flow Rate: 11.2 L/s Monitoring well: 219.1 masl Well 8 RPM: 2450 AMP: 5.5 %: 42 Level: 207.6 masl Well 13 RPM: 2112 AMP: 4.6 %: 21 Level: 205.6 masl On site adjusted the combined flow rate to 10.5L/s as per Tanya kampherns request. Changed the speed of well 8 to 37% speed and well 8 to 17%. New values below Totalizer: 4883212m3 Discharge pressure: 25.18Kpa Flow Rate: 10.5 L/s Monitoring well: 219.1 masl Well 8 RPM: 2365 AMP: 5.3 %: 37 Level: 208.2 masl Well 13 RPM: 2043 AMP: 4.9 %: 17 Level: 206.6 masl | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00020349 | 0 | 0
2026-03 | 2026-03-23 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | On site for weekly Station check. Also replaced malfunctioning unit heater. Totalizer: 4916973 m3 Discharge pressure: 30.24 kPa Flow Rate: 10.2 L/s Monitoring well: 219.4 masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.6 masl Well 13 RPM: 2060 AMP: 4.9 %: 18 Level: 206.4 masl | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00091847 | 0 | 0
2026-03 | 2026-03-13 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | On site to switch power from temporary generator back to Hydro power. Reset any alarms and started pumps 13 and eight in manual mode as normal. Totalizer: 4907870m3 Discharge pressure: 24.52Kpa Flow Rate: 10.5 L/s Monitoring well: 219.4 masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.4 masl Well 13 RPM: 2060 AMP: 4.9 %: 18 Level: 206.4 masl | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.00191 | 0 | 0
2026-03 | 2026-03-06 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | Totalizer: 4901980 m3 Discharge pressure: 27.81 kPa Flow Rate: 10.3 L/s Monitoring well: 219.2 masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.5 masl Well 13 RPM: 2043 AMP: 4.9 %: 17 Level: 206.6 masl | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011918 | 0 | 0
2026-03 | 2026-03-18 | Major MacKenzie and Newkirk Road Dewatering Wells | W-MAINT | Details: Totalizer: 4912364 m3 Discharge pressure: 30.15 kPa Flow Rate: 10.3 L/s Monitoring well: 219.3 masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.6 masl Well 13 RPM: 2060 AMP: 4.9 %: 18 Level: 206.4 masl | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010354 | 0 | 0
2026-03 | 2026-03-04 | Maple North Reservoir | WEST | -on site to collect weekly bacti W11637582 -checked trends: all ok -entered reading in PWQ: all ok -took sample and chlorine grab 09:35 -free cl: 0.08mg/l -total cl: 1.63mg/l -west cell grab 09:40 -free cl: 0.08mg/l -total cl: 1.62mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043 | 0 | 0
2026-03 | 2026-03-31 | Maple North Reservoir | WEST | On site for station check, operational sampling and weekly bacti W11705742 Checked trends: all ok 10:30-Took sample and chlorine grab from west cell Free cl: 0.05mg/l Total cl: 1.70 mg/l 10:35-East cell chlorine grab Free cl: 0.03mg/l Total cl: 1.60 mg/l Entered readings in PWQ: all ok equipment all okay Equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004906 | 0 | 0
2026-03 | 2026-03-19 | Maple North Reservoir | WEST | -on site to complete following station check -outside sump pit inspection: all ok | FLAG | stage2_low_confidence | 0.012531 | ML: above threshold (no LLM available) — 0.013 |  | 0.012531 | 0 | 0
2026-03 | 2026-03-18 | Maple North Reservoir | WEST | on site for station check and weekly bacti W -checked trends: all ok -entered readings in PWQ: all ok -took sample and chlorine grab east cell 09:52 -free cl: 0.07mg/l -total cl: 1.48mg/l -west cell chlorine grab 10:37 -free cl: 0.04 mg/l -total cl: 1.47mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045439 | 0 | 0
2026-03 | 2026-03-18 | Maple North Reservoir | WEST | On site for station check, operational sampling and weekly bacti W11672961 Checked trends: all ok 10:37-Took sample and chlorine grab from west cell Free cl: 0.04mg/l Total cl: 1.47 mg/l 09:52-East cell chlorine grab Free cl: 0.07mg/l Total cl: 1.48 mg/l Entered readings in PWQ: all ok Equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053916 | 0 | 0
2026-03 | 2026-03-25 | Maple North Reservoir | WEST | On site for station check and weekly bacti W11690336 Checked trends: all ok 10:25-Took sample and chlorine grab from East cell Free cl: 0.05mg/l Total cl: 1.64 mg/l 10:30-west cell chlorine grab Free cl: 0.03mg/l Total cl: 1.63 mg/l Entered readings in PWQ: all ok Equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048871 | 0 | 0
2026-03 | 2026-03-23 | Maple North Reservoir | WEST | Restarted the Operator Interface Terminal due to Windows OS memory. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006612 | 0 | 0
2026-03 | 2026-03-12 | Maple North Reservoir | WEST | -on site to complete following work orders -JHSC inspection: all ok -general housekeeping- notice water on floor - pushed water into sump pit -sump pit inspection: all ok -main cross over valve: all ok | FLAG | stage2_low_confidence | 0.02254 | ML: above threshold (no LLM available) — 0.023 | work order [maintenance_action] | 0.02254 | 0 | 0
2026-03 | 2026-03-11 | Maple North Reservoir | WEST | on site for station check and weekly bacti W11657067 -checked trends: all ok -entered readings in PWQ: all ok -took sample and chlorine grab east cell 09:10 -free cl: 0.03mg/l -total cl: 1.59mg/l -west cell chlorine grab 09:15 -free cl: 0.03mg/l -total cl: 1.62mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049222 | 0 | 0
2026-03 | 2026-03-30 | Maple Pumping Station | WEST | conducted station check checked trends: all ok verified PD7 analyzer 10:40 Grab free Cl2: 0.07mg/l; Analyzer: 0.02mg/l Grab total Cl2: 1.70mg/l Analyzer: 1.68mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054194 | 0 | 0
2026-03 | 2026-03-13 | Maple Pumping Station | WEST | Station Check (no issues found) Input data to PWQ 14:15 Verified Depolox (mg/l) Free: Grab 0.04, A 0.03 Total: Grab 1.77, A 1.78 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050566 | 0 | 0
2026-03 | 2026-03-05 | Maple Pumping Station | WEST | -on site to complete following work orders -JHSC inspection: no high voltage on PD8 MCC room -screen inspection: all ok - | FLAG | stage2_low_confidence | 0.014304 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action] | 0.014304 | 0 | 0
2026-03 | 2026-03-05 | Maple Pumping Station | WEST | -on site to complete following work orders -screen inspection: all ok -sump inspection: all ok -general housekeeping main floor: all ok -diesel run -diesel start: 484/497.7 -diesel stop: 485/498.8 -diesel level: 38436 - 371/508L -diesel ventilation inspection: all ok -tested containment alarm: all ok -diesel transfer pumps: all ok -chlorine analyzer maintenance -verified PD7 analyzer 13:40 -analyzer free: 0.02mg/l grab: 0.05mg/L -analyzer total: 1.90mg/l grab: 1.88mg/l -flow/electrolyte/pressure and sand all ok -PD8 analyzer offline | FLAG | stage2_low_confidence | 0.013251 | ML: above threshold (no LLM available) — 0.013 | work order [maintenance_action]; alarm [control_system]; containment [safety] | 0.013251 | 0 | 0
2026-03 | 2026-03-09 | Maple Pumping Station | WEST | conducted station check checked trends: all ok verified PD7 analyzer 10:04 Grab free: 0.04mg/l Analyzer: 0.03mg/l Grab total: 1.72mg/l Analyzer: 1.67mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051997 | 0 | 0
2026-03 | 2026-03-03 | Maple Pumping Station | WEST | -on site to troubleshoot pd8 p4 multilin and Vfd. Found that the multilin had a red issue that was not still present and operating fine. We reset the unit and cleared alarm. Test ran the pump to confirm operation with control panel. Placed pump back to auto under direction of oic. | FLAG | stage2_low_confidence | 0.031 | ML: above threshold (no LLM available) — 0.031 | alarm [control_system] | 0.031 | 0 | 0
2026-03 | 2026-03-02 | Maple Pumping Station | WEST | W11695012- Site access for fire system contractor and building inspector Assisted contractor and inspector. conducted station check checked trends: all ok verified PD7 analyzer 11:00 analyzer free: 0.03mg/l grab: 0.02mg/l analyzer total: 1.71mg/l grab: 1.68mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical] | fire [critical] |  | 1 | 0
2026-03 | 2026-03-19 | Maple Pumping Station | WEST | on site for the following work order. W11668087- Process sump pump and drain valve exercise Unable to enter the chamber due to the ongoing construction. sump pumps started manually, listened pumps starting and made sure its running. However, level did not go down in LIT. will investigate later. W11641379- MWPS comprehensive house keeping, pump room | FLAG | stage2_low_confidence | 0.029826 | ML: above threshold (no LLM available) — 0.03 | work order [maintenance_action] | 0.029826 | 0 | 0
2026-03 | 2026-03-23 | Maple Pumping Station | WEST | -on site to complete station check -checked equipment -reviewed trends -recorded readings in PWQ sheet -PD8 analyzer out of service due to PD8 suction line isolation Verified analyzers: 09:24 - PD7 Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.69 mg/L 09:24 - PD7 Grabs: Free Chlorine = 0.01 mg/L Total Chlorine = 1.69 mg/L -no issues found | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-20 | Maple Pumping Station | WEST | conducted station check checked trends: all ok verified PD7 analyzer 10:40 Grab free: 0.06mg/l Analyzer: 0.02mg/l Grab total: 1.69mg/l Analyzer: 1.69mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051997 | 0 | 0
2026-03 | 2026-03-06 | Maple Pumping Station | WEST | conducted station check checked trends: all ok verified PD7 analyzer 09:54 Grab free: 0.01mg/l Analyzer: 0.03mg/l Grab total: 1.60mg/l Analyzer: 1.67mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051997 | 0 | 0
2026-03 | 2026-03-05 | Maple Pumping Station | WEST | On site to complete hard wiring for PD8 VFD remote reset signal upgrade. Tested fault signals and resetting from the PLC panel. | FLAG | stage2_low_confidence | 0.022474 | ML: above threshold (no LLM available) — 0.022 | fault [equipment_failure] | 0.022474 | 0 | 0
2026-03 | 2026-03-27 | Maple Pumping Station | WEST | conducted station check checked trends: all ok verified PD7 analyzer 10:20 Grab free Cl2: 0.04mg/l; Analyzer: 0.02mg/l Grab total Cl2: 1.70mg/l Analyzer: 1.67mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054194 | 0 | 0
2026-03 | 2026-03-16 | Maple Pumping Station | WEST | conducted station check checked trends: all ok verified PD7 analyzer 09:35 Grab free: 0.04mg/l Analyzer: 0.03mg/l Grab total: 1.65mg/l Analyzer: 1.65mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051997 | 0 | 0
2026-03 | 2026-03-11 | Maple South Reservoir | WEST | -on site to complete station check, following work orders and weekly bacti W -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sampl north cell 08:30 -free cl: 0.08mg/l -total cl: 1.61mg/l -cleaned and verified metro analyzer 08:35 -analyzer free:0.02mg/l grab: 0.04mg/l -analyzer total: 1.66mg/l grab: 1.68mg/l -flow/pressure/electrolyte: all ok -cleaned and verified peel analyzer 08:45 -analyzer: 1.80mg/l grab: 1.76mg/l - adjusted -changed reagents -tested high and low level alarms: all ok -sump pump inspection: all ok -construction on going | FLAG | stage2_low_confidence | 0.014176 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.014176 | 0 | 0
2026-03 | 2026-03-31 | Maple South Reservoir | WEST | on site for station check, operational sampling and weekly bacti W11705742 checked trends: all ok 09:20-took sample and chlorine grab north cell Free Cl2: 0.03 mg/l Total Cl2: 1.67mg/l 09:30-verified peel analyzer Grab Total Cl2: 1.69mg/l Analyzer Total Cl2: 1.67 mg/L Reagents all ok 09:35-verified metro analyzer Grab Free CL2- 0.05 mg/L Analyzer free CL2- 0.02mg/L Grab Total CL2- 1.66 mg/L Analyzer Total CL2- 1.69 mg/L entered readings in PWQ Site under construction | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039174 | 0 | 0
2026-03 | 2026-03-18 | Maple South Reservoir | WEST | on site for station check, operational sampling and weekly bacti W11672961 checked trends: all ok 09:50-verified peel analyzer Grab Total Cl2: 1.63mg/l Analyzer Total Cl2: 1.67 mg/L Reagents all ok 09:55-verified metro analyzer Grab Free CL2- 0.02 mg/L Analyzer free CL2- 0.02mg/L Grab Total CL2- 1.60 mg/L Analyzer Total CL2- 1.63 mg/L 09:40-took sample and chlorine grab north cell Free Cl2: 0.02 mg/l Total Cl2: 1.65mg/l entered readings in PWQ Site under construction | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003917 | 0 | 0
2026-03 | 2026-03-31 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Elog was down this morning March 31, 2026 Jason Garnett onsite from 7:45 am - 8:15 am Completed station and equipment check and weekly BacT sample W11705420 Took sample and grabs @ 7:55 am Total: 2.70 mg/l Free: 0.02 mg/l Analyzer matched grabs, reagents ok All other readings on PD sheets shared online folder ET Filling @ 20 l/s ET ops normal | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-25 | Maple South Reservoir | WEST | on site for station check, operational sampling and weekly bacti W11690336 checked trends: all ok 09:40-verified peel analyzer Grab Total Cl2: 1.70mg/l Analyzer Total Cl2: 1.71 mg/L Reagents all ok 09:45-verified metro analyzer Grab Free CL2- 0.03 mg/L Analyzer free CL2- 0.02mg/L Grab Total CL2- 1.70 mg/L Analyzer Total CL2- 1.67 mg/L 09:38-took sample and chlorine grab north cell Free Cl2: 0.04 mg/l Total Cl2: 1.64mg/l entered readings in PWQ Site under construction | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003917 | 0 | 0
2026-03 | 2026-03-04 | Maple South Reservoir | WEST | -on site for station check and weekly bacti W11637582 -checked trends: all ok -entered readings in PWQ: -verified peel analyzer 08:25: 1.68mg/l grab: 1.67mg/l -reagents all ok -took sample and chlorine grab north cell 08:30 -free cl: 0.10mg/l -total cl: 1.65mg/l -verified metro analyzer 08:40 -analyzer free: 0.02mg/l grab: 0.05mg/l -analyzer total: 1.63mg/l grab: 1.67mg/l -site under construction | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058512 | 0 | 0
2026-03 | 2026-03-04 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 3:00 Verified Depolox (mg/L) Free: Grab 0.04, A 0.02 Total: Grab 2.52, A 2.56 Samples #11637661, #11637260 & operational | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042466 | 0 | 0
2026-03 | 2026-03-25 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 10:10 Verified Depolox (mg/l) Free: Grab 0.04, A 0.01 Total: Grab 2.48, A 2.52 10:20 #11690790 bact. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038857 | 0 | 0
2026-03 | 2026-03-11 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 13:30 Verfied Depolox (mg/l) Free: Grab 0.04, A 0.02 Total: Grab 2.62, A 2.41 (adjusted to match grabs) 13:40 Sample #11657622 Depolox (acetate topped up) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041441 | 0 | 0
2026-03 | 2026-03-24 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Onsite to complete monthly Maximo workorders Telecom crew onsite No alarms created ET ops normal | FLAG | stage2_low_confidence | 0.012122 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012122 | 0 | 0
2026-03 | 2026-03-18 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 14:35 Verified Depolox (mg/l) Free: Grab 0.05, A 0.02 Total: Grab 2.66, A 2.60 3:00 #11672723 bact. and operational samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051727 | 0 | 0
2026-03 | 2026-03-31 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | onsite to receive hypo delivery, aprox 380 L Also station check and take weekly BacT sample W1111705420 from sample tap Total: 1.70 mg/l Free: 0.04 mg/l All other readings on PD sheets Top up hypo day tanks 1 and 2 reagents ok Ops normal | FLAG | stage2_low_confidence | 0.0073822 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073822 | 0 | 0
2026-03 | 2026-03-13 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Reservoir filling at time of check Took grabs from Inlet @ 10:00 am (post) Total: 2.60 mg/l Free: 0.03 mg/l All other readings on PD sheets *adjusted offset for header total ammonia from -0.03 to - 0.08 Topped up both Hypo day tanks Changed CL17 reagent ?inlet free? Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055518 | 0 | 0
2026-03 | 2026-03-06 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Tank filling Took grabs @ 11:05 am from post (inlet) Total: 2.38 mg/l Free: 0.04 mg/l Also took grabs from Pre (header) @ 10:35 am, readings input to PD sheets *adjusted offset on header FA from 0.00 to -0.07 to match grabs Top up both Hypo day tanks Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00572 | 0 | 0
2026-03 | 2026-03-09 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 13:00 Pre (outlet): Free: Grab 0.04, A 0.01 Total: Grab 1.82, A 1.89 13:15 Post (header) Free: Grab 0.06, A 0.07 Total: Grab 3.10, A 3.15 Header Free CL17 (new reagents) #11649044 (hot water flush of chemscan sample lines (chemical pumps manual off during work)) Ammonia tank (transfer of #1 into #2) Hypo tank #2 top up | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033681 | 0 | 0
2026-03 | 2026-03-10 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Received hypo delivery and topped up tanks 1 and 2. W11652297 | FLAG | stage2_low_confidence | 0.011723 | ML: above threshold (no LLM available) — 0.012 |  | 0.011723 | 0 | 0
2026-03 | 2026-03-11 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 10:50 Pre (Inlet/Draining) Free: Grab 0.04, A 0.01 Total: Grab 1.80, A 1.80 10:55 Post (header/draining): Free: Grab 0.06, A 0.05 Total: Grab 3.20, A 3.25 11:00 Sample #11657622 Chemscan (distilled, distilled/muriatic top up) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030606 | 0 | 0
2026-03 | 2026-03-04 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no other issues found) Input data to PWQ Verified CL17s (mg/l) 12:35 PRE Free: Grab 0.03, A 0.01 Total: Grab 1.65, A 1.66 12:45 Post (header) Free: Grab 0.07, A 0.04 Total: Grab 3.16, A 3.20 13:00 Samples #11637260, #11637661 & operational Ammonia pump 1 in manual off due to "fail to start" alarms | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0043184 | 0 | 0
2026-03 | 2026-03-03 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Hypo Delivery Before: Tank 1 280L, Tank 2 234L, bulk tank 0L After: Tank 1 280L, Tank 2 283L , bulk tank 330L Total delivered 379L Ammonia pump 1 "fail to start" cleared and started in duty 1 Chemscan (new yellow reagent ) | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-03 | 2026-03-16 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ #11667608 Chemscan sample line hot flush (chemical pumps manual off, chemscan off-line durin flush) Verified CL17s (mg/L) 13:30 Pre (draining/ Outlet): Free: Grab 0.03, A 0.02 Total: Grab 1.80, A 1.77 12:40 Post (draining/ Header): Free: Grab 0.05, A 0.05 Total: Grab 3.20, A 3.20 Cl17 (Inlet total) reagents changed Chemscan (green & grey reagent top up) Hypo tank 2 top up Ammonia Tank 2 top up (transferred from tank 1 (ammonia pump 1 oos)) | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s(mg/l)(draining) 12:05 Pre (inlet/outlet) Free: Grab 0.03, A 0.02 Total: Grab 1.79, A 1.83 12:35 #11672723 bact. & operational samples 12:15 Post (header) Free: Grab 0.04, A 0.05 Total: Grab 3.12, A 3.20 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038412 | 0 | 0
2026-03 | 2026-03-27 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite for station check Contractors cutting lower door into VC1 wall, have tarpped off chemscan. Reset breaker 6 for chlorine room electrical plug. Changed header total cl17 reagent. Station ok | FLAG | stage2_low_confidence | 0.0098244 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098244 | 0 | 0
2026-03 | 2026-03-25 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/l) (Draining): 12:22 PRE (inlet/outlet): Free: Grab 0.04, A 0.02 Total: Grab 1.91, A 2.00 12:35 POST(Header): Free: Grab 0.05, A 0.05 Total: Grab 3.20, 3.22 12:45 #11690790 bact. sample Chemscan (top up distilled, KI sol'n) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029968 | 0 | 0
2026-03 | 2026-03-19 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to assist with the relocation of the chemscan unit, all chemical pumps placed in manual and off Tank 2 remained filling as work being completed PCS/Instrumentation also on site Received Hypo delivery aprox 520 L Batched ammonia tank 1 Instrumentation also investigating am P1 fault an startup, left manual OFF for now Will monitor system via scada | FLAG | stage2_low_confidence | 0.02808 | ML: above threshold (no LLM available) — 0.028 | fault [equipment_failure]; scada [control_system] | 0.02808 | 0 | 0
2026-03 | 2026-03-20 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Trained with Ben H. on operation of site. On site to complete station check. Verified analyzers: Header Free Chlorine @ 11:10 Grab: 0.03 mg/L Analyzer: 0.03 mg/L Header Total Chlorine @ 11:10 Grab: 1.78 mg/L Analyzer: 1.77 mg/L Inlet Free Chlorine @ 11:17 Grab: 0.06 mg/L Analyzer: 0.04 mg/L Inlet Total Chlorine @ 11:17 Grab: 2.00 mg/L Analyzer: 2.08 mg/L Adjusted chemscan header free ammonia reading from 0.05 to 0.18 mg/L based on grabs -Ended duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011604 | 0 | 0
2026-03 | 2026-03-23 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to top up ammonia tank 1. Deactivated chlorine boosting system while batch tank. Placed back in service at 14:32 No issues found | FLAG | stage2_low_confidence | 0.019885 | ML: above threshold (no LLM available) — 0.02 | oos [equipment_failure] | 0.019885 | 0 | 0
2026-03 | 2026-03-19 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to witness Lexsan relocate the Chem Scan coordinated Connor from ROC, only the power was turned off none of the wires were removed. Jason Garnett is onsite site to witness the relocation Instrumentation were also onsite to verify the Chem Scan after power was turned back on. Site left under normal condition | FLAG | stage2_low_confidence | 0.046603 | ML: above threshold (no LLM available) — 0.047 |  | 0.046603 | 0 | 0
2026-03 | 2026-03-20 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | On site to complete station check. Verified chemscan outlet readings. Entered data into PD sheets | FLAG | stage2_low_confidence | 0.016154 | ML: above threshold (no LLM available) — 0.016 |  | 0.016154 | 0 | 0
2026-03 | 2026-03-17 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Work orders: #11669068 CL17 maint. Verified(mg/L): 10:15 Pre (header/Fill) Free: Grab 0.03, A 0.03 Total: Grab 1.98, A 1.97 10:30 Post (inlet/fill) Free: Grab 0.03, A 0.03 Total: Grab 1.98, A 1.97 #11669663 flood Hypo pump draw down (no changes made): #11670012 , #11675940, #11676221 Ammonia pump 1 (oos) unable to perform draw down) | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; oos [equipment_failure]; work order [maintenance_action] | flood [critical]; oos [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-23 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station and equipment check Informed ROC (Carter D) will be completing Maximo workorder hot water flush of all analyzer supply lines 9:30-10:45 am All chemical systems placed off and analyzers in cal mode, reservoir filling Returned system to normal w/ no issues Took grabs @ 11:15 am Post (inlet) Total: 2.30 mg/l Free: 0.05 mg/l All other readings on PD sheets Topped up both hypo day tanks Am P1 OOS Ops normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-24 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Attending site to check ammonia pump#1 (W11707116). Found internal pump relay not functioning to provide running status back to SCADA. Replaced internal relay and tested to function correctly after repair. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.066037 | ML: above threshold (no LLM available) — 0.066 | repair [maintenance_action]; scada [control_system] | 0.066037 | 0 | 0
2026-03 | 2026-03-19 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to verify Chemscan analyzer after relocation. Informed ROC. Turned on the Chemscan analyzer after relocation. Took a multiple grab samples. All readings back to normal and matched SCADA. All the associated alarms were cleared. No issues. Troubleshoot ammonia pump #1. Replaced the start/stop relay. Alarms still intermittently present. Ammonia pump #1 in manual off for now. Informed ROC, armed the building and left the site. | FLAG | stage2_low_confidence | 0.023701 | ML: above threshold (no LLM available) — 0.024 | sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.023701 | 0 | 0
2026-03 | 2026-03-24 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Onsite to receive hypo delivery 330 L Ops normal Top up hypo day tanks to make room in bulk tank | FLAG | stage2_low_confidence | 0.007603 | ML: above threshold (no LLM available) — 0.008 |  | 0.007603 | 0 | 0
2026-03 | 2026-03-05 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | #11668904 Hypo pump maint (cleaned all hypo inj. pts. and draw down) #11668956 Ammonia (due to ammonia pump having alarm issues) -Transferred ammonia tank 1 into tank 2 -ammonia tank 1 (new batch) #11669036 Chemscan -header Free Ammonia offset adjusted from -0.06 to 0.00 to match grab #11668939 chem tanks | FLAG | stage2_low_confidence | 0.012809 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.012809 | 0 | 0
2026-03 | 2026-03-31 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site to perform station check No issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039431 | 0 | 0
2026-03 | 2026-03-02 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | CENTRAL | Station Check (no issues found) Input data to PWQ CL17/Chemscan sample line hot water flush (Hypo& Ammonia chemical pumps manual off during flush) Verified CL17s (mg/L)(Draining) 13:30 Pre (Inlet) Free: Grab 0.04, A 0.01 Total: Grab 1.69, A 1.74 13:40 Post (header) Free: Grab 0.03, A 0.05 Total: Grab 3.10, A 3.19 Hypo tank 2 top up Ammonia Pump #1 had a "fail to start" on Friday and went to Duty 2, No issues found with pump and returned to Duty 1, ran without issue Chemscan (Grey & Green top up, Muratic/distilled new batch) | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-03 | 2026-03-09 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site to complete station check. Site offline and secure. | FLAG | stage2_low_confidence | 0.013528 | ML: above threshold (no LLM available) — 0.014 |  | 0.013528 | 0 | 0
2026-03 | 2026-03-02 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | Station Check Responding to security issue (outer door not secure (can be manually pulled open) however the inner door is secure, no signs of tampering) (ROC notified) Site off-line | FLAG | stage2_low_confidence | 0.017174 | ML: above threshold (no LLM available) — 0.017 |  | 0.017174 | 0 | 0
2026-03 | 2026-03-16 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site to complete station check. Site offline and secure. | FLAG | stage2_low_confidence | 0.013528 | ML: above threshold (no LLM available) — 0.014 |  | 0.013528 | 0 | 0
2026-03 | 2026-03-19 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site for PMs. -Completed JHSC inspection. All good -Notified ROC that tower pressure sensor (PIT) would be reading inaccurately while drawing water from the line for replacing the eyewash solution. Replaced eyewash solution | FLAG | stage2_low_confidence | 0.016571 | ML: above threshold (no LLM available) — 0.017 |  | 0.016571 | 0 | 0
2026-03 | 2026-03-25 | Newmarket (London) Yonge Street Elevated Tank | CENTRAL | On site to complete station check. Site offline and secure. | FLAG | stage2_low_confidence | 0.013528 | ML: above threshold (no LLM available) — 0.014 |  | 0.013528 | 0 | 0
2026-03 | 2026-03-24 | Newmarket (Northeast) Davis Drive Elevated Tank | CENTRAL | Station and equipment check Complete maximo workorders Low temp alarm in "hut", turned portable heater back on Flushed w/m with dechlor in place starting @ 10:40 am - 11:20 am aprox. 14 l/s (22 m3) Fixed leaking hose bib in old well 14 building JHSC inspection complete no issues Ops normal | FLAG | stage2_low_confidence | 0.016167 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system]; leak [infrastructure]; leaking [infrastructure] | 0.016167 | 0 | 0
2026-03 | 2026-03-20 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Onsite to refuel portable gas generator. | FLAG | stage2_low_confidence | 0.013157 | ML: above threshold (no LLM available) — 0.013 |  | 0.013157 | 0 | 0
2026-03 | 2026-03-31 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station and equipment check Take weekly BacT sample W11705420 and grabs @ 8:55 am Total: 2.78 mg/l Free: 0.03 mg/l Analyzer matched, reagents ok Mono: 2.33 mg/l Free Ammonia: 0.06 mg/l Total Ammonia: 0.52 mg/l Nitrite: 0.003 mg/l ET in delivery mode ET ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039788 | 0 | 0
2026-03 | 2026-03-27 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Altitude valve inspection: all good -Heat trace system inspection: all good -Portable generator test: all good, coordinated with Donny M. to top up fuel -JHSC inspection: all good -Flood alarm test: all good | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | Newmarket (West) Bathurst Tank | CENTRAL | Station and equipment check Take weekly BacT sample W11705420 and grabs @ 10:20 am from outlet sample tap Total: 2.69 mg/l Free: 0.04 mg/l Analyzer matched and reagents ok all other readings on PD sheets Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065909 | 0 | 0
2026-03 | 2026-03-04 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 11:00 Verified Depolox (mg/L) Free: Grab 0.04, A 0.06 Total: Grab 2.88, A 3.08 (adjusted to match grabs) Samples #11637260, #11637661, & operational Depolox (new KI/distilled) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045572 | 0 | 0
2026-03 | 2026-03-11 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 9:55 Verified Depolox (mg/l) Free: Grab 0.04, A 0.04 Total: Grab 2.92, A 2.91 10:00 Sample #11657622 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038842 | 0 | 0
2026-03 | 2026-03-25 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 11:00 Verified Depolox (mg/L) Free: Grab 0.03, A 0.05 Total: Grab 2.62, A 2.67 Depolox (topped up electrolyte) 11:18 #11690790 bact. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037452 | 0 | 0
2026-03 | 2026-03-27 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Onsite to perform monthly chlorine analyzer maintenance. | FLAG | stage2_low_confidence | 0.014151 | ML: above threshold (no LLM available) — 0.014 |  | 0.014151 | 0 | 0
2026-03 | 2026-03-18 | Newmarket (Southeast) Ivsbridge Elevated Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 9:55 Verified Depolox (mg/l) Free: Grab 0.06, A 0.04 Total: Grab 3.14, A 3.10 (topped up Acetate & KI/distilled) 9:05 #11672723 bact. & operational samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041694 | 0 | 0
2026-03 | 2026-03-25 | Newmarket (West) Bathurst Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 8:50 Verified Depolox (mg/L) Free: Grab 0.05, A 0.05 Total: Grab 2.60, A 2.62 Depolox (topped up electrolyte) 9:15 #11690790 bact. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037139 | 0 | 0
2026-03 | 2026-03-18 | Newmarket (West) Bathurst Tank | CENTRAL | :Station Check (no issues found) Input data to PWQ 10:00 Verified Depolox (mg/l) Free: Grab 0.05, A 0.05 Total: Grab 2.86. A 2.78 10:15 #11672723 bact. & operational samples | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043108 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Kirby Pumping Station | CENTRAL | On site to complete station check Entered data into PD sheet No issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071249 | 0 | 0
2026-03 | 2026-03-11 | Newmarket (West) Bathurst Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 8:36 Verified Depolox (mg/l) Free: Grab 0.08, A 0.05 Total: Grab 2.76, A 2.76 Depolox (acetate, distilled/KI , electrolyte top up) 8:45 Sample #11657622 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041057 | 0 | 0
2026-03 | 2026-03-04 | Newmarket (West) Bathurst Tank | CENTRAL | Station Check (no issues found) Input data to PWQ 9:20 Verified Depolox (mg/L) Free: Grab 0.04, A 0.05 Total: Grab 2.70, A2.72 9:50 Samples #11637260, 11637661, operational Depolox (topped up acetate & electrolyte | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043069 | 0 | 0
2026-03 | 2026-03-17 | Newmarket (West) Bathurst Tank | CENTRAL | Workorders: #11674409 Depolox Maint.: electrolyte top up 13:40 Verified (mg/l) Free: Grab 0.06, A 0.05 Total: Grab 2.70, A 2.76 #1167504 jhs #11675382 hi/lo test #11675664 dechlor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030807 | 0 | 0
2026-03 | 2026-03-06 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check FCV: 0% Flow: 0 l/s suction pressure: 47 kPa discharge pressure: 340 kPa All pumps available Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061416 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Kirby Pumping Station | CENTRAL | Station Check (no issues found) Input data to PWQ | FLAG | stage2_low_confidence | 0.011449 | ML: above threshold (no LLM available) — 0.011 |  | 0.011449 | 0 | 0
2026-03 | 2026-03-09 | Newmarket Kirby Pumping Station | CENTRAL | Station Check (no issues found) Input data to PWQ | FLAG | stage2_low_confidence | 0.011449 | ML: above threshold (no LLM available) — 0.011 |  | 0.011449 | 0 | 0
2026-03 | 2026-03-13 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check Ops normal | FLAG | stage2_low_confidence | 0.010753 | ML: above threshold (no LLM available) — 0.011 |  | 0.010753 | 0 | 0
2026-03 | 2026-03-23 | Newmarket Kirby Pumping Station | CENTRAL | Station and equipment check All ok Ops normal | FLAG | stage2_low_confidence | 0.0093001 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093001 | 0 | 0
2026-03 | 2026-03-27 | Newmarket Kirby Pumping Station | CENTRAL | Onsite for station check Recordings in PD sheet station ok | FLAG | stage2_low_confidence | 0.009895 | ML: above threshold (no LLM available) — 0.01 |  | 0.009895 | 0 | 0
2026-03 | 2026-03-16 | Newmarket Kirby Pumping Station | CENTRAL | Station Check (no issues found) Input data to PWQ Jhs inspection | FLAG | stage2_low_confidence | 0.010229 | ML: above threshold (no LLM available) — 0.01 |  | 0.010229 | 0 | 0
2026-03 | 2026-03-20 | Newmarket Kirby Pumping Station | CENTRAL | On site to complete station check. Station off. No issues found. Completed PD sheet | FLAG | stage2_low_confidence | 0.015107 | ML: above threshold (no LLM available) — 0.015 |  | 0.015107 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check and weekly bacti sample W11706327 Ben put wells 1 and 2 into manual on for duration of station check -Verified analyzers: Influent Free Chlorine @ 10:06 Grab: 2.68mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 10:13 Grab: 2.60 mg/L Analyzer: 2.55mg/L Treated Free Chlorine @ 10:16 Grab: 0.09 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 10:19 Grab: 2.84 mg/L Analyzer: 2.88 mg/L - Changed treated free and effluent free reagents - Entered data into PD Sheet - Checked trends - Filled ammonia tank 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00039209 | 0 | 0
2026-03 | 2026-03-26 | Newmarket Kirby Pumping Station | CENTRAL | Onsite to complete monthly Maximo workorders Informed ROC (Angelica) of ongoings Found no issues Ops normal | FLAG | stage2_low_confidence | 0.010341 | ML: above threshold (no LLM available) — 0.01 |  | 0.010341 | 0 | 0
2026-03 | 2026-03-13 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 10:18 Grab: 2.68 mg/L Analyzer: 2.68 mg/L Effluent Free Chlorine @ 10:14 Grab: 2.56 mg/L Analyzer: 2.57 mg/L Treated Free Chlorine @ 10:10 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:10 Grab: 2.90 mg/L Analyzer: 2.94 mg/L -Based on SL1000 grabs taken for ammonia pump 1 and 2, adjusted chlorine:ammonia ratio from 3.8 to 3.9 -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00104 | 0 | 0
2026-03 | 2026-03-10 | Newmarket Well 1 & 2 | CENTRAL | Silicate top up 686 L -1089 L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067216 | 0 | 0
2026-03 | 2026-03-09 | Newmarket Well 1 & 2 | CENTRAL | On site with Alex B to complete station check and operator samples -Verified analyzers: Influent Free Chlorine @ 10:20 Grab: 2.60 mg/L Analyzer: 2.63 mg/L Effluent Free Chlorine @ 10:24 Grab: 2.62 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 10:29 Grab: 0.09 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 10:32 Grab: 2.90 mg/L Analyzer: 2.95 mg/L - Entered data into PD Sheet - Checked trends - Topped up well 2 mineral oil - Alex put well 13 into manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00086616 | 0 | 0
2026-03 | 2026-03-03 | Newmarket Well 1 & 2 | CENTRAL | Silicate top up: Before 671L After 1069L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069919 | 0 | 0
2026-03 | 2026-03-20 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 14:42 Grab: 2.50 mg/L Analyzer: 2.53 mg/L Effluent Free Chlorine @ 14:39 Grab: 0.28 mg/L Analyzer: 0.32 mg/L Treated Free Chlorine @ 14:36 Grab: 0.12 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 14:36 Grab: 2.42 mg/L Analyzer: 2.52 mg/L -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00077506 | 0 | 0
2026-03 | 2026-03-27 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check -Verified analyzers: Influent Free Chlorine @ 12:12 Grab: 2.44 mg/L Analyzer: 2.42mg/L Effluent Free Chlorine @ 12:15 Grab: 0.15 mg/L Analyzer: 0.15 mg/L Treated Free Chlorine @ 12:18 Grab: 0.09 mg/L Analyzer: 0.8mg/L Treated Total Chlorine @ 12:21 Grab: 2.56 mg/L Analyzer: 2.48 mg/L - Entered data into PD Sheet - Checked trends - performed PM on silicate pumps: all good | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00078462 | 0 | 0
2026-03 | 2026-03-11 | Newmarket Well 1 & 2 | CENTRAL | On site with Alex B to complete station check and bacti samples (W11656837). -Verified analyzers: Influent Free Chlorine @ 10:12 Grab: 2.70 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 10:15 Grab: 2.30 mg/L Analyzer: 2.31 mg/L Treated Free Chlorine @ 10:18 Grab: 0.11 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:21 Grab: 2.70 mg/L Analyzer: 2.81 mg/L - Changed Influent free analyzer reagents - Entered data into PD Sheet - Checked trends - Alex returned well 1 and 2 to auto - Alex put well 15 to manual on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00099578 | 0 | 0
2026-03 | 2026-03-04 | Newmarket Well 1 & 2 | CENTRAL | NMW12 On site with Alex B to complete station check and weekly bacti samples W11638302 Alex B put wells into manual off -Verified analyzers: Influent Free Chlorine @ 9:47 Grab: 2.54 mg/L Analyzer: 2.60 mg/L Effluent Free Chlorine @ 9:50 Grab: 2.48 mg/L Analyzer: 2.56 mg/L Treated Free Chlorine @ 10:02 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9.57 Grab: 2.90 mg/L Analyzer: 2.94 mg/L - Entered data into PD Sheet - Checked trends - Alex put wells 1 and 2 back into auto - Alex put well 15 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00059851 | 0 | 0
2026-03 | 2026-03-04 | Newmarket Well 1 & 2 | CENTRAL | On site to complete PMs Informed ROC of relevant alarms Did chlorine leak detector test: all good Alex cleared alarms Calibrated and performed maintenance on turbidimeter: all good, reading 0.032 NTU Performed cleaning of chlorine analyzers: all good Verified analyzers: Influent free chlorine @ 14:34 Grab: 2.60 mg/L Analyzer: 2.52mg/L Effluent Free Chlorine @ 14:37 Grab: 0.15 mg/L Analyzer: 0.12 mg/L Treated Free Chlorine @ 14:40 Grab: 0.03 mg/L Analyzer: 0.06 mg/L Treated Total Chlorine @ 14:46 Grab: 2.08 mg/L Analyzer: 2.08 mg/L -Alex returned Newmarket wells 1 and 2 to auto | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; leak [infrastructure] | alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-06 | Newmarket Well 1 & 2 | CENTRAL | On site with Alex B to complete station check -Verified analyzers: Influent Free Chlorine @ 11:09 Grab: 2.70 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 11:12 Grab: 2.52 mg/L Analyzer: 2.56 mg/L Treated Free Chlorine @ 11:15 Grab: 0.13 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:18 Grab: 2.82 mg/L Analyzer: 2.94mg/L - Entered data into PD Sheet - Checked trends - Filled ammonia tank 2 - Alex put Newmarket Well 15 into manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00078565 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check and collect operational samples. -Changed reagents for treated total analyzer -Verified analyzers: Influent Free Chlorine @ 10:30 Grab: 2.56 mg/L Analyzer: 2.64 mg/L Effluent Free Chlorine @ 10:27 Grab: 2.58 mg/L Analyzer: 2.62 mg/L Treated Free Chlorine @ 10:24 Grab: 0.16 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:24 Grab: 2.94 mg/L Analyzer: 3.01 mg/L -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00091334 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Well 1 & 2 | CENTRAL | Changed chlorine cylinder bank B with Joe Williams. | FLAG | stage2_low_confidence | 0.01389 | ML: above threshold (no LLM available) — 0.014 |  | 0.01389 | 0 | 0
2026-03 | 2026-03-03 | Newmarket Well 1 & 2 | CENTRAL | Attending site to repair Influent Free chlorine analyzer push buttons (W11688098). ROC shut off well near end of cycle so that work could proceed. Calibration mode was used to reduce alarms from this equipment. Replaced all switches on analyzer circuit board. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.083259 | ML: above threshold (no LLM available) — 0.083 | repair [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.083259 | 0 | 0
2026-03 | 2026-03-24 | Newmarket Well 1 & 2 | CENTRAL | Silicate top up: (76.3 to 114.3cm) | FLAG | stage2_low_confidence | 0.0097828 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097828 | 0 | 0
2026-03 | 2026-03-12 | Newmarket Well 1 & 2 | CENTRAL | Received 9 full and gave 9 empty for chlorine delivery. | FLAG | stage2_low_confidence | 0.010803 | ML: above threshold (no LLM available) — 0.011 |  | 0.010803 | 0 | 0
2026-03 | 2026-03-23 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check and collect operational samples. -Placed wells in manual-on for duration of station check -Verified analyzers: Influent Free Chlorine @ 10:43 Grab: 2.80 mg/L Analyzer: 2.76 mg/L Effluent Free Chlorine @ 10:36 Grab: 2.56 mg/L Analyzer: 2.46 mg/L Treated Free Chlorine @ 10:33 Grab: 0.11 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:33 Grab: 2.80 mg/L Analyzer: 2.80 mg/L -Topped up ammonia tank 2 -Topped up well 2 mineral oil -Returned wells 1&2 to auto -Placed well 13 in manual-on -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0007967 | 0 | 0
2026-03 | 2026-03-18 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check and collect weekly bacti samples (W11673490). -Verified analyzers: Influent Free Chlorine @ 9:48 Grab: 2.56 mg/L Analyzer: 2.56 mg/L Effluent Free Chlorine @ 9:44 Grab: 2.56 mg/L Analyzer: 2.48 mg/L Treated Free Chlorine @ 9:41 Grab: 0.10 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:41 Grab: 2.82 mg/L Analyzer: 2.86 mg/L -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00098111 | 0 | 0
2026-03 | 2026-03-05 | Newmarket Well 1 & 2 | CENTRAL | On site to complete PMs with Alex B Informed ROC of relevant alarms Performed deep well exhaust valve maintenance for both wells: all good Performed PM for silicate system: - Put wells and chlorine boosters into manual off - Put dechlor in waste chamber - Hot flushed silicate pumping system - Hot flushed silicate injection points - Isolated raw main from contact tank and depressurized raw main. Pulled injection points and performed maintenance - Ran to waste while priming silicate lines - Performed drawdowns on silicate system - Changed max flow scada silicate set points from 220ml/L to 230ml/L for both silicate pumps - Places chlorine boosters into auto - Placed wells in auto and started duty Performed PM for ammonia system - performed drawdowns on ammonia pump one and two: all good Performed JHSC Inspection: all good - Tested silicate dosing: all good for both pumps | FLAG | stage2_low_confidence | 0.013906 | ML: above threshold (no LLM available) — 0.014 | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.013906 | 0 | 0
2026-03 | 2026-03-25 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check and collect weekly bacti samples (W11690106) -Verified analyzers: Influent Free Chlorine @ 9:33 Grab: 2.54 mg/L Analyzer: 2.57 mg/L Effluent Free Chlorine @ 9:30 Grab: 2.62 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 9:27 Grab: 0.11 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:27 Grab: 2.84 mg/L Analyzer: 2.87 mg/L -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00097718 | 0 | 0
2026-03 | 2026-03-16 | Newmarket Well 1 & 2 | CENTRAL | On site to complete station check and collect operational samples. -Changed chlorine cylinder bank A with Joe W. -Topped up ammonia tank 1 -Verified analyzers: Influent Free Chlorine @ 9:42 Grab: 2.50 mg/L Analyzer: 2.51 mg/L Effluent Free Chlorine @ 9:38 Grab: 2.58 mg/L Analyzer: 2.58 mg/L Treated Free Chlorine @ 9:34 Grab: 0.16 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 9:34 Grab: 3.00 mg/L Analyzer: 2.92 mg/L -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00071576 | 0 | 0
2026-03 | 2026-03-27 | Newmarket Well 1 & 2 | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Completed chlorine inspection: added dechlor to waste chamber and started backflushing slightly while completing work. Closed waste valve when finished. All good -Completed bank B chlorine cylinder change with Ben H. | FLAG | stage2_low_confidence | 0.026464 | ML: above threshold (no LLM available) — 0.026 | alarm [control_system]; alarms [control_system] | 0.026464 | 0 | 0
2026-03 | 2026-03-09 | Newmarket Well 14 | CENTRAL | Station Check (no issues found) site off-line | FLAG | stage2_low_confidence | 0.011201 | ML: above threshold (no LLM available) — 0.011 |  | 0.011201 | 0 | 0
2026-03 | 2026-03-13 | Newmarket Well 14 | CENTRAL | Flush water main for 1 hour @ aprox 13 L/S Flow meter reading after 46 m3 Ops normal | FLAG | stage2_low_confidence | 0.008612 | ML: above threshold (no LLM available) — 0.009 |  | 0.008612 | 0 | 0
2026-03 | 2026-03-16 | Newmarket Well 14 | CENTRAL | Visual inspection | FLAG | stage2_low_confidence | 0.01193 | ML: above threshold (no LLM available) — 0.012 |  | 0.01193 | 0 | 0
2026-03 | 2026-03-21 | Newmarket Well 14 | CENTRAL | Onsite to respond to loss of power alarms at 12:24. Found power pole breaker tripped on phase C outside of site. No issues found in facility. Notified ROC an on call electrician Tyler Z. 14:54. Electrician and electrical company on route route for repair. Station is offline, only lost communication to EGmCDD. | FLAG | stage2_low_confidence | 0.047751 | ML: above threshold (no LLM available) — 0.048 | tripped [equipment_failure]; trip [equipment_failure]; repair [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.047751 | 0 | 0
2026-03 | 2026-03-27 | Newmarket Well No. 15 | CENTRAL | On site to complete station check -Verified analyzers: Influent Free Chlorine @ 13:43 Grab: 3.12mg/L Analyzer: 3.06 mg/L Effluent Free Chlorine @ 13:45 Grab: 0.19 mg/L Analyzer: 0.16 mg/L Treated Free Chlorine @ 13:48 Grab: 0.08 mg/L Analyzer: 0.8 mg/L Treated Total Chlorine @ 13:51 Grab: 2.98 mg/L Analyzer: 3.00 mg/L - Entered data into PD Sheet - Checked trends - Changed Influent free reagents - Completed work order W11633920 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.00059409 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Well 14 | CENTRAL | Station Check No issues found Station Offline | FLAG | stage2_low_confidence | 0.0093416 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093416 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Well No. 15 | CENTRAL | On site to complete station check and weekly bacti sample W11706327 Ben put well 15 in manual on for duration of station check -Verified analyzers: Influent Free Chlorine @ 12:18 Grab: 3.00 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 12:21 Grab: 2.88 mg/L Analyzer: 2.87 mg/L Treated Free Chlorine @ 12:24 Grab: 0.13 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:31 Grab: 3.38 mg/L Analyzer: 3.50 mg/L - Entered data into PD Sheet - Checked trends - Topped up well mineral oil | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00085515 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Well No. 15 | CENTRAL | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 11:21 Grab: 3.06 mg/L Analyzer: 3.00 mg/L Effluent Free Chlorine @ 11:15 Grab: 2.90 mg/L Analyzer: 2.80 mg/L Treated Free Chlorine @ 11:11 Grab: 0.17 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 11:11 Grab: 3.48 mg/L Analyzer: 3.41 mg/L -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00089333 | 0 | 0
2026-03 | 2026-03-12 | Newmarket Well No. 15 | CENTRAL | Received chlorine delivery. 6 full, gave 6 empty. | FLAG | stage2_low_confidence | 0.010493 | ML: above threshold (no LLM available) — 0.01 |  | 0.010493 | 0 | 0
2026-03 | 2026-03-13 | Newmarket Well No. 15 | CENTRAL | On site to complete station check. -Placed well in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 8:46 Grab: 2.82 mg/L Analyzer: 2.71 mg/L Effluent Free Chlorine @ 8:41 Grab: 0.11 mg/L Analyzer: 0.14 mg/L Treated Free Chlorine @ 8:38 Grab: 0.10 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 8:38 Grab: 2.84 mg/L Analyzer: 2.85 mg/L -Topped up well 15 mineral oil. Noticed debris in reservoir, created WO W11732814 for maintenance to address it -Entered data into PD Sheet -Checked trends -Returned well to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00092524 | 0 | 0
2026-03 | 2026-03-11 | Newmarket Well No. 15 | CENTRAL | On site with Alex B to complete station check and weekly bacti samples W11656837 -Verified analyzers: Influent Free Chlorine @ 12:21 Grab: 2.94 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 12:24 Grab: 2.84 mg/L Analyzer: 2.84 mg/L Treated Free Chlorine @ 12:27 Grab: 0.13 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:38 Grab: 3.30 mg/L Analyzer: 3.38 mg/L - Entered data into PD Sheet - Checked trends - Alex put well 15 back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010125 | 0 | 0
2026-03 | 2026-03-03 | Newmarket Well No. 15 | CENTRAL | Silicate top up: Before 275.6L After 378L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070212 | 0 | 0
2026-03 | 2026-03-06 | Newmarket Well No. 15 | CENTRAL | NMW15 On site with Alex B to complete station check -Verified analyzers: Influent Free Chlorine @ 12:40 Grab: 2.98 mg/L Analyzer: 2.93 mg/L Effluent Free Chlorine @ 12:44 Grab: 2.88 mg/L Analyzer: 2.84 mg/L Treated Free Chlorine @ 12:47 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 12:51 Grab: 3.34 mg/L Analyzer: 3.43 mg/L - Entered data into PD Sheet - Checked trends - Alex B and Jay G changed chlorine cylinder bank B - Created W11714356 to quick report assessment of ammonia pump 1 dosing - Changed max flow set point from 98 to 102 for ammonia pump one: all good | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00094566 | 0 | 0
2026-03 | 2026-03-09 | Newmarket Well No. 15 | CENTRAL | On site with Alex B to complete station check and operator samples - Alex put well 13 back into auto - Alex put well 15 into manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 13:33 Grab: 2.86 mg/L Analyzer: 2.84 mg/L Effluent Free Chlorine @ 13:36 Grab: 2.76 mg/L Analyzer: 2.79mg/L Treated Free Chlorine @ 13:39 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 13:45 Grab: 3.26 mg/L Analyzer: 3.37 mg/L - Entered data into PD Sheet - Checked trends - Mixed and filled ammonia tank one - Alex returned well 15 to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00081158 | 0 | 0
2026-03 | 2026-03-04 | Newmarket Well No. 15 | CENTRAL | NMW15 On site with Alex B to complete station check and weekly bacti samples W11638302 -Verified analyzers: Influent Free Chlorine @ 11:04 Grab: 2.80 mg/L Analyzer: 2.79 mg/L Effluent Free Chlorine @ 11:07 Grab: 2.80 mg/L Analyzer: 2.84 mg/L Treated Free Chlorine @ 11:10 Grab: 0.15 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:14 Grab: 3.26 mg/L Analyzer: 3.36 mg/L - Entered data into PD Sheet - Checked trends - Alex returned well 15 to auto - Performed drawdown on ammonia pump one - Alex placed ammonia pump one in manual - Exercised ammonia valve one locally, Alex returned to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00081053 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Well No. 15 | CENTRAL | Discussed with Ben H, returned well to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059008 | 0 | 0
2026-03 | 2026-03-24 | Newmarket Well No. 15 | CENTRAL | 08:20 Notified roc of work. Locked out well 15. Emptied and Cleaned silicate tank with Alex Bell. Cleaned silicate foot valves. Replace silicate pump 1 pump tube. Joe Williams topped up silicate tank from empty to 376.6 L. Changed left chlorine cylinder. Primed both silicate pumps. Adjusted p1 max pump rate from 205 to 244 ml/min. Adjusted silicate concentration SCADA setpoint from 27 to 38%. 13:50 Placed silicate pumps and well 15 back to auto. | FLAG | stage2_low_confidence | 0.019438 | ML: above threshold (no LLM available) — 0.019 | scada [control_system] | 0.019438 | 0 | 0
2026-03 | 2026-03-23 | Newmarket Well No. 15 | CENTRAL | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 13:45 Grab: 2.98 mg/L Analyzer: 2.96 mg/L Effluent Free Chlorine @ 13:38 Grab: 2.84 mg/L Analyzer: 2.81 mg/L Treated Free Chlorine @ 13:34 Grab: 0.13 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 13:34 Grab: 3.48 mg/L Analyzer: 3.42 mg/L -Entered data into PD Sheet -Checked trends -Returned well to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00082958 | 0 | 0
2026-03 | 2026-03-19 | Newmarket Well No. 15 | CENTRAL | Returned well 15 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041227 | 0 | 0
2026-03 | 2026-03-25 | Newmarket Well No. 15 | CENTRAL | On site to complete station check, collect weekly bacti samples (W11690106), and reinstall silicate injection point 2. -Notified ROC of relevant alarms. Added dechlor to waste chamber. Isolated raw main via valve on influent side of contact tank and depressurized raw main via waste valve. Reinstalled silicate injection point 2. Primed line while backflushing well slightly. -Placed well in manual-on -Verified analyzers: Influent Free Chlorine @ 12:37 Grab: 3.02 mg/L Analyzer: 2.93 mg/L Effluent Free Chlorine @ 12:42 Grab: 2.98 mg/L Analyzer: 2.91 mg/L Treated Free Chlorine @ 12:46 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 12:46 Grab: 3.52 mg/L Analyzer: 3.50 mg/L -Confirmed both injection points functional. Left silicate injection point 2 in use -Returned well to auto -Entered data into PD Sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0030372 | 0 | 0
2026-03 | 2026-03-26 | Newmarket Well No. 15 | CENTRAL | Attending site to check 'motor error' on Total chlorine analyzer (W11761894). Replaced motor and verified reading. Analyzer reading 2.83mg/L, and average of 3 dpd grabs was 2.81mg/L. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.025969 | ML: above threshold (no LLM available) — 0.026 |  | 0.025969 | 0 | 0
2026-03 | 2026-03-19 | Newmarket Well No. 15 | CENTRAL | On site to complete PMs. Notified ROC. -Completed JHSC inspection, all good -Performed maintenance on and calibrated turbidimeter, analyzer read 0.060 NTU afterwards | FLAG | stage2_low_confidence | 0.0094816 | ML: above threshold (no LLM available) — 0.009 |  | 0.0094816 | 0 | 0
2026-03 | 2026-03-20 | Newmarket Well No. 15 | CENTRAL | Returned well to auto once maintenance finished with the mineral oil pot. Added ammonia to and mixed ammonia tank 2, returned ammonia valve 2 to auto. | FLAG | stage2_low_confidence | 0.016778 | ML: above threshold (no LLM available) — 0.017 |  | 0.016778 | 0 | 0
2026-03 | 2026-03-20 | Newmarket Well No. 15 | CENTRAL | Clean drip oiler and refill with new mineral oil | FLAG | stage2_low_confidence | 0.021833 | ML: above threshold (no LLM available) — 0.022 | drip [infrastructure] | 0.021833 | 0 | 0
2026-03 | 2026-03-03 | Newmarket Well No. 15 | CENTRAL | On site to troubleshoot treated free hi and hihi alarm and ammonia pumps with Donny M. Notified ROC of relevant alarms. Added dechlor to drain chamber and began backflushing. Verified analyzer: Treated Free Chlorine @ 9:32 Grab: 2.40 mg/L Analyzer: 1.20 mg/L Analyzer read 2.40 mg/L after adjustment. 9:43 Combined lolo alarm came in while backflushing. There was a free chlorine analyzer reading of 1.68 mg/L. Replaced diaphragm in ammonia pump 2. Cleaned foot valves for both pumps. Performed drawdowns. Placed well in manual-on. Placed chlorine dosing in manual for ammonia dosage tuning. Treated Free Chlorine @ 14:12 Grab: 0.13 mg/L Analyzer: 0.25 mg/L Analyzer read 0.13 mg/L after adjustment. Returned well to auto, returned chlorine dosing to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.002429 | 0 | 0
2026-03 | 2026-03-18 | Newmarket Well No. 15 | CENTRAL | On site to complete station check and collect weekly bacti samples (W11673490). -Placed well in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 11:25 Grab: 3.04 mg/L Analyzer: 2.93 mg/L Effluent Free Chlorine @ 11:16 Grab: 2.90 mg/L Analyzer: 2.89 mg/L Treated Free Chlorine @ 11:10 Grab: 0.12 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:10 Grab: 3.40 mg/L Analyzer: 3.46 mg/L -Entered data into PD Sheet -Checked trends -Returned well to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00082435 | 0 | 0
2026-03 | 2026-03-26 | Newmarket Well No. 15 | CENTRAL | On site to complete PMs. Notified ROC. -Completed ammonia inspection: all good Ammonia pump 1 max flow setpoint changed from 102 to 99 mL/min based on drawdowns Ammonia pump 2 max flow setpoint changed from 98 to 102 mL/min based on drawdowns -Completed deep well exhaust valve maintenance -Completed maintenance on CL17 chlorine analyzers, verified afterwards: Influent Free Chlorine @ 12:34 Grab: 3.16 mg/L Analyzer: 3.23 mg/L Effluent Free Chlorine @ 12:42 Grab: 0.18 mg/L Analyzer: 0.20 mg/L Treated Free Chlorine @ 12:31 Grab: 0.10 mg/L Analyzer: 0.10 mg/L Motor error issue persistent with treated total analyzer. Analyzer offline for now. Leaving well in manual-off, contacted Eric S. to come replace the motor and had ROC create CMU. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051767 | 0 | 0
2026-03 | 2026-03-18 | Newmarket Well No. 15 | CENTRAL | On site to complete PMs. Notified ROC. -Completed chlorine leak detection test: all good -Replaced reagents for treated total and free chlorine analyzers | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-20 | Newmarket Well No. 15 | CENTRAL | On site to complete station check. -Placed well in manual-off for duration of station check -Verified analyzers: Influent Free Chlorine @ 7:48 Grab: 2.72 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 7:45 Grab: 0.09 mg/L Analyzer: 0.12 mg/L Treated Free Chlorine @ 7:42 Grab: 0.08 mg/L Analyzer: 0.06 mg/L Treated Total Chlorine @ 7:42 Grab: 2.56 mg/L Analyzer: 2.51 mg/L -Filled ammonia tank 2 with water; did not add ammonia yet, placed valve 2 into manual-closed -Performed silicate pump drawdowns. Changed pump 1 max flow SCADA setpoint from 280 to 240 mL/min. Changed pump 2 SCADA max flow setpoint from 270 to 250 mL/min. Adjusted PSV and PRV on chemical board to higher settings. -Pump 1 appears to be pumping a small amount of air which may have caused previous dosing issues. Will address next week during silicate work; for now, silicate pump 1 remains manual-off but may be used with partial efficacy if needed. -Entered data into PD Sheet -Checked trends -Kept well in manual off for maintenance to perform work on mineral oil pot | FLAG | stage2_low_confidence | 0.0077475 | ML: above threshold (no LLM available) — 0.008 | scada [control_system] | 0.0077475 | 0 | 0
2026-03 | 2026-03-26 | Newmarket Well No. 15 | CENTRAL | On site to complete PMs. Notified ROC. -Completed chlorine inspection: all good. Added dechlor to waste chamber and backflushed slightly during work. Chlorinator 1 v-notch passes slightly under heavy vacuum; no corrective action currently needed -Eric S. on site to continue maintenance on treated total analyzer, well remains in manual-off | FLAG | stage2_low_confidence | 0.021547 | ML: above threshold (no LLM available) — 0.022 |  | 0.021547 | 0 | 0
2026-03 | 2026-03-16 | Newmarket Well No. 15 | CENTRAL | On site to complete station check and collect operational samples. -Placed well in manual-on for duration of station check -Verified analyzers: Influent Free Chlorine @ 13:12 Grab: 2.98 mg/L Analyzer: 2.86 mg/L Effluent Free Chlorine @ 13:09 Grab: 2.86 mg/L Analyzer: 2.73 mg/L Treated Free Chlorine @ 12:58 Grab: 0.11 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:58 Grab: 3.30 mg/L Analyzer: 3.34 mg/L -Change chlorine cylinder B with Joe W. -Entered data into PD Sheet -Checked trends -Returned well to auto -Cleaned foot valve for silicate pump 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00075424 | 0 | 0
2026-03 | 2026-03-10 | Newmarket Well No. 15 | CENTRAL | Silicate top up 211 L - 380 L | FLAG | stage2_low_confidence | 0.0080455 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080455 | 0 | 0
2026-03 | 2026-03-03 | Newmarket Well No. 15 | CENTRAL | Placed well 15 in manual-off after switching ammonia pumps did not remedy hihi free chlorine spike. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057579 | 0 | 0
2026-03 | 2026-03-20 | Newmarket Well No. 15 | CENTRAL | Onsite to troubleshoot silicate issues Silicate tank filling while well is off, water was passing through injection point, into the calibration column and back feeding into the silicate tank. Using C1V1/V2 = C2 I adjusted silicate concentration from 38% to 27%. Pulled injection points, both had silicate in chunks in check valves, disassembled and cleaned with hot water. Able to get injection point 1 back into service, injection point 2 check valve failed (leaving OOS) when discharge header was recharged. Hand pump had to be disassembled and cleaned as it was seized, causing power failure to chlorine room tripping the breaker. Silicate tank needed to be mixed, used hand pump onsite to mix the tank. Silicate P1 pulling in air, cut suction line and added new parker fitting, cleared air bubbles out of line Performed drawdowns on silicate P1 and P2 adjusted silicate P1 from 240 ml/min to 205 ml/min. Put everything back to auto. Facility ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; failure [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; seized [equipment_failure]; valve failed [infrastructure] | failed [equipment_failure]; failure [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; seized [equipment_failure]; valve failed [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | Newmarket Wells 13-16 | CENTRAL | On site with Ben H to complete PMs. Alex on site to complete silicate PM. - Performed chlorine inspection: all good - Performed chlorine analyzer maintenance: all good - Performed pressure relief valve test on well 13: all good - Performed terbidimeter cleaning: all good - Performed H&S inspection: all good Alex verified analyzers: Influent Free Chlorine @ 14:52 Grab: 2.34 mg/L Analyzer: 2.37 mg/L Effluent Free Chlorine @ 14:59 Grab: 0.53 mg/L Analyzer: 0.53 mg/L Treated Free Chlorine @ 14:56 Grab: 0.07 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 14:53 Grab: 2.18 mg/L Analyzer: 2.25 mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0015821 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Wells 13-16 | CENTRAL | NMW136 On site to complete station check and weekly bacti sample W11706327 Ben H. put well 13 in manual on for duration of station check -Verified analyzers: Influent Free Chlorine @ 8:05 Grab: 2.90 mg/L Analyzer: 2.92 mg/L Effluent Free Chlorine @ 8:08 Grab: 2.48mg/L Analyzer: 2.60 mg/L Treated Free Chlorine @ 8:11 Grab: 0.15 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 8:18 Grab: 3.14 mg/L Analyzer: 3.01 mg/L - Entered data into PD Sheet - Checked trends - Changed treated total reagents | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00027108 | 0 | 0
2026-03 | 2026-03-11 | Newmarket Wells 13-16 | CENTRAL | On site with Alex B to complete station check and weekly bacti samples (W11656837). Alex put well 13 into manual on for duration of the station check -Verified analyzers: Influent Free Chlorine @ 8:53 Grab: 2.60 mg/L Analyzer: 2.68 mg/L Effluent Free Chlorine @ 8:56 Grab: 2.38 mg/L Analyzer: 2.30 mg/L Treated Free Chlorine @ 9:00 Grab: 0.08 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:03 Grab: 2.72 mg/L Analyzer: 2.76 mg/L - Entered data into PD Sheet - Checked trends - -Topped up well 13 mineral oil - Alex put well 13 back in auto - Alex put well 1 and 2 into manual-on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00096031 | 0 | 0
2026-03 | 2026-03-03 | Newmarket Wells 13-16 | CENTRAL | Silicate top up: Before 2044L After 2352L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070212 | 0 | 0
2026-03 | 2026-03-10 | Newmarket Wells 13-16 | CENTRAL | Onsite to respond to treated free high alarm- informed by ROC: Took grab to verify analyzer (09:58): Treated free grab: 0.10 Treated free analyzer: 0.12 Treated free analyzer onsite not matching up with treated free scada reading- informed Ben H, and Eric S. Work order has been created. Instrumentation team will respond to site to further investigate. | FLAG | stage2_low_confidence | 0.016627 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action]; scada [control_system]; alarm [control_system] | 0.016627 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Wells 13-16 | CENTRAL | Received 8 full chlorine cylinders in delivery exchange for 8 empties. | FLAG | stage2_low_confidence | 0.011523 | ML: above threshold (no LLM available) — 0.012 |  | 0.011523 | 0 | 0
2026-03 | 2026-03-10 | Newmarket Wells 13-16 | CENTRAL | Silicate top up 1929 L - 3481 L Also exhaust fan in well 13 building very loud, turned off Will create workorder for maintenance to service or replace Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.007167 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Wells 13-16 | CENTRAL | Returned well 13 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041227 | 0 | 0
2026-03 | 2026-03-06 | Newmarket Wells 13-16 | CENTRAL | NMW136 On site with Alex B to complete station check -Verified analyzers: Influent Free Chlorine @ 9:56 Grab: 2.64 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 10:01 Grab: 2.52 mg/L Analyzer: 2.43 mg/L Treated Free Chlorine @ 10:04 Grab: 0.15 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 10:07 Grab: 2.82 mg/L Analyzer: 2.80 mg/L - Entered data into PD Sheet - Checked trends - Alex B. and Jay G. changed chlorine cylinder bank B | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00064825 | 0 | 0
2026-03 | 2026-03-10 | Newmarket Wells 13-16 | CENTRAL | Wel_AIT3 R1S13:Ch0 reading inaccurate based on Eric's testing. Move to R1S13:Ch02 temporarily until card is either replaced or drawings and literature updated. Eric will create a WO to initiate. | FLAG | stage2_low_confidence | 0.0075395 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075395 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 9:41 Grab: 2.70 mg/L Analyzer: 2.76 mg/L Effluent Free Chlorine @ 9:30 Grab: 2.32 mg/L Analyzer: 2.36 mg/L Treated Free Chlorine @ 9:26 Grab: 0.10 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 9:26 Grab: 2.82 mg/L Analyzer: 2.72 mg/L -Placed well 13 in manual-on to draw down chlorine cylinder bank B -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00099997 | 0 | 0
2026-03 | 2026-03-09 | Newmarket Wells 13-16 | CENTRAL | On site with Alex B to complete station check and operational samples -Verified analyzers: Influent Free Chlorine @ 11:51 Grab: 2.70 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 11:54 Grab: 2.48 mg/L Analyzer: 2.40mg/L Treated Free Chlorine @ 11:57 Grab: 0.15 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 12:00 Grab: 2.78 mg/L Analyzer: 2.74 mg/L - Entered data into PD Sheet - Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00091646 | 0 | 0
2026-03 | 2026-03-27 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check -Verified analyzers: Influent Free Chlorine @ 9:14 Grab: 2.88 mg/L Analyzer: 2.98 mg/L Effluent Free Chlorine @ 9:17 Grab: 2.62 mg/L Analyzer: 2.63 mg/L Treated Free Chlorine @ 9:20 Grab: 0.09mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:34 Grab: 2.94 mg/L Analyzer: 3.06 mg/L - Entered data into PD Sheet - Checked trends - Changed treated free reagents | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00074017 | 0 | 0
2026-03 | 2026-03-20 | Newmarket Wells 13-16 | CENTRAL | Onsite for station check recordings in PD sheet adjust effluent free chlorine analyzer adjust silicate p2 max flow from 225 ml/min to 255 ml/min based on drawdowns adjusted well 13 drip oiler to ~4-5 drips/min station ok | FLAG | stage2_low_confidence | 0.014477 | ML: above threshold (no LLM available) — 0.014 | drip [infrastructure] | 0.014477 | 0 | 0
2026-03 | 2026-03-16 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check and collect operational samples. -Topped up ammonia tank 2 -Verified analyzers: Influent Free Chlorine @ 11:00 Grab: 2.86 mg/L Analyzer: 2.84 mg/L Effluent Free Chlorine @ 10:55 Grab: 2.50 mg/L Analyzer: 2.50 mg/L Treated Free Chlorine @ 10:47 Grab: 0.07 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 10:47 Grab: 2.84 mg/L Analyzer: 2.86 mg/L -Adjusted mineral oil pot on well 13 to 1-2 drops per minute from <1 drops per minute -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00087979 | 0 | 0
2026-03 | 2026-03-19 | Newmarket Wells 13-16 | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Performed silicate hot flush: added dechlor to well 13 waste chamber. Flushed silicate chemical boards with hot water. Performed drawdowns. Pump 2 max flow setpoint changed from 225 to 240 mL/min. Backflushed for a short period via well 13 PRV to get rid of any excess silicate from work. -Worked with Joe D. to tighten pigtail on bank B chlorine cylinder with halogen 2B. | FLAG | stage2_low_confidence | 0.041358 | ML: above threshold (no LLM available) — 0.041 | alarm [control_system]; alarms [control_system] | 0.041358 | 0 | 0
2026-03 | 2026-03-27 | Newmarket Wells 13-16 | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Performed ammonia inspection: Adjusted pump 2 max flow setpoint from 220 to 230 mL/min based on drawdowns.Otherwise all good. | FLAG | stage2_low_confidence | 0.015859 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system]; alarms [control_system] | 0.015859 | 0 | 0
2026-03 | 2026-03-24 | Newmarket Wells 13-16 | CENTRAL | Silicate top up (57.5 to 65.3 cm) | FLAG | stage2_low_confidence | 0.0097649 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097649 | 0 | 0
2026-03 | 2026-03-23 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 11:49 Grab: 2.74 mg/L Analyzer: 2.83 mg/L Effluent Free Chlorine @ 11:46 Grab: 2.54 mg/L Analyzer: 2.57 mg/L Treated Free Chlorine @ 11:40 Grab: 0.09 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 11:40 Grab: 2.94 mg/L Analyzer: 3.06 mg/L -Entered data into PD sheet -Checked trends -Returned well 13 to auto -Placed well 15 in manual-on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00080356 | 0 | 0
2026-03 | 2026-03-18 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check and collect weekly bacti samples (W11673490). -Verified analyzers: Influent Free Chlorine @ 8:18 Grab: 2.90 mg/L Analyzer: 2.97 mg/L Effluent Free Chlorine @ 8:22 Grab: 2.30 mg/L Analyzer: 2.41 mg/L Treated Free Chlorine @ 8:08 Grab: 0.13 mg/L Analyzer: 0.09 mg/L Treated Total Chlorine @ 8:08 Grab: 2.48 mg/L Analyzer: 2.57 mg/L -Adjusted mineral oil pot on well 13 to 2-3 drops per minute from <1 drops per minute. Will continue to monitor -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013778 | 0 | 0
2026-03 | 2026-03-13 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check. -Placed well 13 in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 12:55 Grab: 2.68 mg/L Analyzer: 2.66 mg/L Effluent Free Chlorine @ 12:44 Grab: 2.42 mg/L Analyzer: 2.19 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.42 mg/L afterwards. Treated Free Chlorine @ 12:34 Grab: 0.12 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 12:51 Grab: 2.74 mg/L Analyzer: 2.53 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.74 mg/L afterwards. -Placed well in manual-off -Performed maintenance on well 13 deep well exhaust valve -Calibrated turbidimeter; analyzer read 0.043 NTU afterwards -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011891 | 0 | 0
2026-03 | 2026-03-10 | Newmarket Wells 13-16 | CENTRAL | Onsite to troubleshoot treated free reading discrepancy between analyzer and SCADA reading. Informed ROC and asked them to put well in manual off. Based on the troubleshooting we found issues with the analog input. Reached out to oncall PCS person (Kyle Carlen). He informed us to move the input from I11300 to I11302. Verified the analyzer reading. No issues. Treated Free chlorine reading spiked few times during the troubleshooting, well was in manual off during that period. Informed ROC, armed the building and no issues. | FLAG | stage2_low_confidence | 0.019559 | ML: above threshold (no LLM available) — 0.02 | scada [control_system] | 0.019559 | 0 | 0
2026-03 | 2026-03-12 | Newmarket Wells 13-16 | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Placed well 13 in manual-off then local -Added dechlor to waste chamber, isolated contact tank on influent side in order to depressurize raw main. Depressurized via well 13 PRV. Pulled injection points, opened influent side valve slightly (STILL MOSTLY CLOSED) to repressurize in order to run hot water through chemical boards and injection points. -Leaving site early to receive chlorine deliveries at other Newmarket well sites. Well 13 left in local, silicate pumps in manual-off. Injection points still removed from system and influent side valve still mostly closed. Notified ROC site would remain in local. | FLAG | stage2_low_confidence | 0.086212 | ML: above threshold (no LLM available) — 0.086 | alarm [control_system]; alarms [control_system] | 0.086212 | 0 | 0
2026-03 | 2026-03-04 | Newmarket Wells 13-16 | CENTRAL | NMW136 On site with Alex B to complete station check and weekly bacti samples W11638302 -Verified analyzers: Influent Free Chlorine @ 8:38 Grab: 2.74 mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 8:41 Grab: 2.58 mg/L Analyzer: 2.52 mg/L Treated Free Chlorine @ 8:44 Grab: 0.11mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 8:47 Grab: 2.86mg/L Analyzer: 2.92mg/L - Entered data into PD Sheet - Checked trends - topped up ammonia tank one - Topped up well 13 mineral oil | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00066509 | 0 | 0
2026-03 | 2026-03-12 | Newmarket Wells 13-16 | CENTRAL | Returned to site to continue work on silicate system. Christian B and Ben H on site to complete other PMs. -Cleaned injection points. Depressurized raw main via isolation on influent side of contact tank and opening well 13 PRV in order to put injection points back in place. Repressurized system and fully opened isolation valve. Primed silicate lines while backflushing slightly through well 13 PRV. Performed drawdowns on both silicate pumps. Changed max flow SCADA setpoint from 265mL/min to 225mL/min for silicate pump 2. -Replaced eyewash solution in silicate room -Returned well 13 to auto once PMs completed | FLAG | stage2_low_confidence | 0.068625 | ML: above threshold (no LLM available) — 0.069 | scada [control_system] | 0.068625 | 0 | 0
2026-03 | 2026-03-18 | Newmarket Wells 13-16 | CENTRAL | On site to complete PMs. Notified ROC of relevant alarms. -Completed chlorine leak detection test: all good -Created CMU W11744100 to replace pigtail on bank B cylinder 2nd from right (with halogen 2B) -Cleaned influent free chlorine analyzer to try and reduce trend ?jaggedness?. Verified analyzer afterward: Influent Free Chlorine @ 13:51 Grab: 2.42 mg/L Analyzer: 2.40 mg/L | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; leak [infrastructure] | alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-04 | Newmarket Wells 13-16 | CENTRAL | Change oil well 13 motor and drain drip oiler and clean Fill with new mineral oil Placed back in auto | FLAG | stage2_low_confidence | 0.014834 | ML: above threshold (no LLM available) — 0.015 | drip [infrastructure] | 0.014834 | 0 | 0
2026-03 | 2026-03-25 | Newmarket Wells 13-16 | CENTRAL | On site to complete station check and collect weekly bacti samples (W11690106) -Placed well 15 in manual-off. Started area duty 1 -Changed reagents for effluent free chlorine analyzer -Verified analyzers: Influent Free Chlorine @ 8:10 Grab: 2.86 mg/L Analyzer: 2.87 mg/L Effluent Free Chlorine @ 8:20 Grab: 2.22 mg/L Analyzer: 2.18 mg/L Treated Free Chlorine @ 8:24 Grab: 0.12 mg/L Analyzer: 0.10 mg/L Treated Total Chlorine @ 8:24 Grab: 2.60 mg/L Analyzer: 2.68 mg/L -Topped up well 13 mineral oil -Entered data into PD sheet -Checked trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0008844 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Booster Pumping Station | WEST | Onsite for station check Pump running Chamber secure and dry No issues observed | FLAG | stage2_low_confidence | 0.0076194 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076194 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Booster Pumping Station | WEST | Onsite for station check Pump running Chamber secure and dry No issues observed | FLAG | stage2_low_confidence | 0.0076194 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076194 | 0 | 0
2026-03 | 2026-03-16 | Nobleton Booster Pumping Station | WEST | Onsite for station check Pump on Site secure Chamber dry | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064696 | 0 | 0
2026-03 | 2026-03-23 | Nobleton Booster Pumping Station | WEST | Onsite for station check Pump appears to be running | FLAG | stage2_low_confidence | 0.0096542 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096542 | 0 | 0
2026-03 | 2026-03-20 | Nobleton Booster Pumping Station | WEST | Onsite for station check Pump on Site secure Chamber dry | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064696 | 0 | 0
2026-03 | 2026-03-04 | Nobleton North Elevated Tank | WEST | Onsite for station check and to collect weekly micro sample W11637120 Tower draining Checked residuals mg/l @0921 Free analyzer 1.07 grab 1.52 Total analyzer 1.54 grab 1.69 Adjusted both analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034757 | 0 | 0
2026-03 | 2026-03-27 | Nobleton Booster Pumping Station | WEST | Onsite for station check Pump on Site secure Chamber dry | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064696 | 0 | 0
2026-03 | 2026-03-25 | Nobleton North Elevated Tank | WEST | On site for station check and to collect weekly micro sample W11690158 Tower draining Check residuals mg/l @0914 Free analyzer 1.52 grab 1.33 Total analyzer 1.62 grab 1.64 Adjusted free analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032452 | 0 | 0
2026-03 | 2026-03-18 | Nobleton North Elevated Tank | WEST | On site for station check and to collect weekly micro sample W11672653 Tower draining Check residuals mg/l @0907 Free analyzer 1.62 grab 1.59 Total analyzer 2.32 grab 1.87 Adjusted total analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032619 | 0 | 0
2026-03 | 2026-03-17 | Nobleton North Elevated Tank | WEST | On site to complete work orders Completed maintenance on chlorine analyzer Reduced flow, resulting in a lower free chlorine residual Added grit Added electrolyte Grabs after Free analyzer 1.62 grab 1.42 Total analyzer 1.71 grab 1.71 Adjusted free analyzer Ran portable generator with no issues Completed jhsc | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.0044479 | 0 | 0
2026-03 | 2026-03-11 | Nobleton North Elevated Tank | WEST | Onsite for station check and to collect weekly micro sample W1165889 Tower draining Checked residuals mg/l @0905 Free analyzer 1.53 grab 1.42 Total analyzer 1.45 grab 1.65 Adjusted both analyzers based on average of multiple grabs Reagents ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029886 | 0 | 0
2026-03 | 2026-03-05 | Nobleton South Elevated Tank | WEST | Onsite to complete work orders Tower draining Completed maintenance on depolox analyzer Reagents ok Grit ok Added electrolyte to both free and total analyzers Grabs before @1229 Free analyzer 1.50 grab 1.52 Total analyzer 1.78 grab 1.74 Grabs after @1247 Free analyzer 1.49 grab 1.47 Total analyzer 1.72 grab 1.71 Completed monthly portable run , no issues Exercised manual valves Completed jhsc | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.00076465 | 0 | 0
2026-03 | 2026-03-31 | Nobleton South Elevated Tank | WEST | Onsite for station check and to collect weekly micro sample W11705252 Checked residuals mg/l @1020 Free analyzer 1.33 grab 1.54 Total analyzer 1.66 grab 1.70 Adjusted free analyzer Reagents ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00341 | 0 | 0
2026-03 | 2026-03-11 | Nobleton South Elevated Tank | WEST | Onsite for station check and to collect weekly micro sample W11656889 Checked residuals mg/l @1000 Free analyzer 1.52 grab 1.53 Total analyzer 1.69 grab 1.80 Reagents ok Adjusted total analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004112 | 0 | 0
2026-03 | 2026-03-25 | Nobleton South Elevated Tank | WEST | On site for station check and to collect weekly micro sample W11690158 Tower draining Check residuals mg/l @0958 Free analyzer 1.40 grab 1.44 Total analyzer 1.65 grab 1.70 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035069 | 0 | 0
2026-03 | 2026-03-18 | Nobleton South Elevated Tank | WEST | On site for station check and to collect weekly micro sample W11672653 Tower draining Check residuals mg/l @1015 Free analyzer 1.74 grab 1.59 Total analyzer 1.75 grab 1.71 Adjusted free analyzer Reagents ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0028583 | 0 | 0
2026-03 | 2026-03-04 | Nobleton South Elevated Tank | WEST | Onsite for station check and to collect weekly micro sample W11637120 Tower draining Checked residuals mg/l @1004 Free analyzer 1.24 grab 1.53 Total analyzer 1.82 grab 1.78 Adjusted free analyzer Reagents ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025405 | 0 | 0
2026-03 | 2026-03-30 | Nobleton Well 2 | WEST | Silicate top up (-0.33 to 41.91cm) | FLAG | stage2_low_confidence | 0.0097828 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097828 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Well 2 | WEST | Onsite for station check and to collect weekly micro sample W11705252 Well running Checked residuals mg/l Influent @1103 Free analyzer 1,98 grab 1.96 Total grab 2.74 Effluent @1108 Free analyzer 1.65 grab 1.66 Total grab 1.91 Reagents ok Nasi P1 39% Chlorinator 2 , 23ppd, 86% DF | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00070732 | 0 | 0
2026-03 | 2026-03-30 | Nobleton Well 2 | WEST | Onsite to assist GFL contractor with cleaning silicate tank Placed well and silicate pumps in local to prevent start up Disinfected with hypo solution before putting back to service Placed everything back to remote Started well in manual and had NTU spike due to chemical board valving issues , adjusted and turbidity dropped. | FLAG | stage2_low_confidence | 0.011543 | ML: above threshold (no LLM available) — 0.012 |  | 0.011543 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Well 2 | WEST | Silicate top up: ( 40.6 to 82.05cm) | FLAG | stage2_low_confidence | 0.0098468 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098468 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Well 2 | WEST | Onsite for station check and to collect weekly micro sample W11656889 Well running in manual Checked residuals mg/l Influent @1318 Free analyzer 1.92 grab 1.95 Total grab 2.60 Effluent @1322 Free analyzer 1.70 grab 1.72 Total grab 2.20 Placed well back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011042 | 0 | 0
2026-03 | 2026-03-03 | Nobleton Well 2 | WEST | On site to complete work orders Stopped well in manual Completed jhsc, no issues observed Cleaned cl17 analyzers Grabs Before Effluent free Analyzer 1.73 grab 1.68 Influent free Analyzer 1.81 grab 1.76 After Effluent free Analyzer 1.71 grab 1.70 Influent free Analyzer 1.72 grab 1.71 Calibrated ntu analyzer with 20 ntu vial Exercised prv Tested cl2 leak detection, no issues Changed cl2 cylinder with T Hudson Cl2 weight 35 to 103 kg Worked on silicate injection points Broke lance in infection point for p2 left in local Tested cl2 system Started well in manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; leak [infrastructure] | 0.00032707 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Well 2 | WEST | Onsite for station check Well running in auto Historian heartbeat shut down well restarted after Checked residuals mg/l Effluent @1403 Free analyzer 1.71 grab 1.80 Total grab 2.10 Influent @1408 Free analyzer 1.86 grab 1.92 Total grab 2.30 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00094855 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Well 2 | WEST | Onsite for station check Well running in manual Checked residuals mg/l Influent @1353 Free analyzer 1.96 grab 1.90 Total grab 2.44 Effluent @1348 Free analyzer 1.64 grab 1.65 Total grab 2.08 Put silicate p2 back in duty and primed Historian heartbeat alarm stopped well | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0010081 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Well 2 | WEST | Repair injection line Re and re silicates line injection shut off valve | FLAG | stage2_low_confidence | 0.022735 | ML: above threshold (no LLM available) — 0.023 | repair [maintenance_action] | 0.022735 | 0 | 0
2026-03 | 2026-03-02 | Nobleton Well 2 | WEST | Onsite for station check Remotely started well Checked residuals mg/l Influent @1217 Free analyzer 1.88 grab 1.87 Total grab 2.90 Effluent @1210 Free analyzer 1.63 grab 1.66 Total grab 1.86 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012958 | 0 | 0
2026-03 | 2026-03-13 | Nobleton Well 2 | WEST | Onsite for station check Well running in manual Checked residuals mg/l Influent @1303 Free analyzer 1.88 grab 2.00 Total grab 2.36 Effluent @1309 Free analyzer 1.66 grab 1.79 Total grab 2.07 Primed silicate p2 Changed reagents on both cl17 analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00083005 | 0 | 0
2026-03 | 2026-03-23 | Nobleton Well 2 | WEST | On site to meet GFL contractor for quote to clean out silicate tank. Temporary day tank does not fit in site facility doors. Will have silicate tank topped up prior to clean so facility can be used in auto. | FLAG | stage2_low_confidence | 0.022511 | ML: above threshold (no LLM available) — 0.023 |  | 0.022511 | 0 | 0
2026-03 | 2026-03-24 | Nobleton Well 2 | WEST | Onsite to monitor silicate system Added flushing connector to bottom of chemical board To get rid of air in suction side of p1 Replaced o rings in ball valve Disconnected and reinstalled fitting to go from pvc to pump suction ball valve De pressurized main Cleaned injection point of silicate p2 Due to high discharge pressure Repressurized main Completed drawdown of p1 117 ml/min Started well P1 suction appeared to stay charged Swapped duties to check p2 pressure, appeared normal but started to increase as runtime increased Rotated duties back to p1 Deactivated all stop rotate Flushed ntu analyzer Ran silicate p1 in manual speed setpoint | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029929 | 0 | 0
2026-03 | 2026-03-18 | Nobleton Well 2 | WEST | Onsite for station check and to collect weekly micro sample Well running Checked residuals mg/l Influent @1230 Free analyzer 1.87 grab 1.83 Effluent @1221 Free analyzer 1.80 grab 1.79 Total grab 2.19 Flushed ntu analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012444 | 0 | 0
2026-03 | 2026-03-19 | Nobleton Well 2 | WEST | Onsite to investigate silicate issues Changed ball valves on silicate chemical board Re plumbed connections for pump tube element Changed tube element in p2 Drawdown to system 117 ml/ min Left well in man off available in emergency Silicate tank lit not showing correct level Due to build up | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-03 | 2026-03-19 | Nobleton Well 2 | WEST | Onsite to check on silicate LIT and chlorinator #1 Informed ROC ROC placed well manual off Viewed silicate trends. Found LIT signal to be a little noisy. Removed LIT transducer and flange to inspect. Transducer is clean but a lot of solids build up below it. Opened tank lid and found a massive amount of solids build up. Tank needs to be cleaned out. Uneven solids surface interfering with ultrasonic signal. Found chlorinator #1 showing 1% open when closed. Adjusted zero position very slightly and exercised actuator. Zero is good now. Ops onsite for silicate work Informed ROC. Ops and ROC to coordinate well back to AUTO Left site | FLAG | stage2_low_confidence | 0.043936 | ML: above threshold (no LLM available) — 0.044 |  | 0.043936 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Well 2 | WEST | Onsite to complete station check and collect weekly micro sample Well running Checked residuals mg/l Influent @1320 Free analyzer 1.86 grab 1.89 Total grab 2.80 Effluent @1317 Free analyzer 1.79 grab 1.78 Total grab 2.06 Stopped well in manual To continue troubleshooting silicate pump two issues Depressurized the main and put in new injection point Started well and manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012257 | 0 | 0
2026-03 | 2026-03-20 | Nobleton Well 2 | WEST | Onsite for station check Well in manual off Checked residuals mg/l Effluent @1305 Free analyzer 1.47 grab 1.52 Total grab 1.70 Influent @1308 Free analyzer 1.60 grab 1.66 Total grab 1.81 Earlier in day changed cl2 cylinder with J.Williams Replumbed the fittings on the tube element on p1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00099548 | 0 | 0
2026-03 | 2026-03-19 | Nobleton Well 2 | WEST | In to work on silicate system. Removed silicate tank mixer from tank lid. Requested quote from contractor, will have tank cleaned out (solids buildup in tank, overdue for clean. Interfering with LIT). Replaced all asahi ball valves on silicate board. Replaced tubing element and compression fittings on Si P2. Changed to PE tubing, Parker fittings, asahi ball valves for fpt unions to tube element. Changed cal column vent line to 1:2 PE tubing and ran back to silicate tank. Will change Si P1 lines on another date. Performed drawdowns on Si P2 to system. W2 manual off, available as backup well (until tank is cleaned or temporary day tank is set up). | FLAG | stage1_keyword | 0.95 | Critical keyword match: backup [infrastructure] | backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-27 | Nobleton Well 2 | WEST | Onsite for station check Started well in manual Checked residuals mg/l Effluent @1014 Free analyzer 1.71 grab 1.75 Total grab 1.97 Influent @1022 Free analyzer 1.87 grab 1.87 Total grab 2.20 Nasi P2 38% Chlorinator 1 22.5 ppd, 84%df | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0009284 | 0 | 0
2026-03 | 2026-03-23 | Nobleton Well 2 | WEST | Onsite for station check Checked residuals mg/l Influent @1217 Free analyzer 1.62 grab 1.61 Total grab 1.73 Effluent @1220 Free analyzer 1.91 grab 1.92 Total grab 2.13 Topped up silicate tank to 77cm Primed sillicate pumps Draw down to system p1 105ml/min Started well in manual with silicate p1 in duty, ntu climbed Rotated duty and ntu came down | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00064397 | 0 | 0
2026-03 | 2026-03-04 | Nobleton Well 2 | WEST | Onsite for station check and to collect weekly micro sample W11637120 Well duty active Checked residuals mg/l Influent @1403 Free analyzer 1.95 grab 1.94 Total grab 2.42 Effluent @1355 Free analyzer 1.74 grab 1.71 Total grab 2.18 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013691 | 0 | 0
2026-03 | 2026-03-30 | Nobleton Wells 3 & 7 | WEST | Silicate top up (42.11 to 75.98cm) | FLAG | stage2_low_confidence | 0.0097828 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097828 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Wells 3 & 7 | WEST | Onsite to respond to well locking out due to low influent cl2 and to complete station check and collect weekly micro sample W11705252 Checked residuals Influent @1145 Free analyzer 0.62 grab 0.85 Started back flush @1146 Influent @1152 Free analyzer 1.50 grab 1.45 Stopped backflush @1153 Restarted well Influent @1226 Free analyzer 2.17 grab 2.13 Effluent @1232 Free analyzer 1.78 grab 1.75 Total grab 1.92 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00051105 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Wells 3 & 7 | WEST | Tried to prime hypo p2 Interlocked the well Ack reset and restarted well | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035559 | 0 | 0
2026-03 | 2026-03-05 | Nobleton Wells 3 & 7 | WEST | @1300 activated duty remotely Well interlocked due to influent lolo alarm @1313 ack reset alarm, when value came back up and well restarted | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0037298 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Wells 3 & 7 | WEST | Onsite for station check well running Checked residuals mg/ Influent @0914 Free analyzer 2.19 grab 2.18 Total grab 2.88 Effluent @0918 Free analyzer 1.75 grab 1.73 Total grab 1.99 Reagents ok Stopped well Noticed leak on silicate p2 Cleaned and tried to solace pump head New pump head did not appear to work Cleaned old one and put back on Primed pump Primed both hypo pumps Topped up hypo tanks | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | leak [infrastructure] | 0.00061005 | 0 | 0
2026-03 | 2026-03-12 | Nobleton Wells 3 & 7 | WEST | Onsite to complete work orders Generator run Start 372.3 hrs Fuel 80.3 cm 842 L Stop 373.4 hrs Fuel Completed jhsc Exercised prv Cleaned injection points Sillicate to sight glass P1 120 ml/min P2 125 ml/min Hypo P1 355 ml/min P2 350 ml/min P2 making noise when off left in manual off Cleaned pump suction check valves | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | noise [equipment_failure]; work order [maintenance_action] | 0.00078142 | 0 | 0
2026-03 | 2026-03-04 | Nobleton Wells 3 & 7 | WEST | Onsite for station check and to collect weekly micro sample w11637120 Well running Checked residuals mg/l Influent @1253 Free analyzer 2.16 grab 2.15 Total grab 2.70 Effluent @1257 Free analyzer 1.57 grab 1.54 Total grab 1.80 Topped up hypo tanks Primed hypo p2 and put into duty Lolo influent caused well to lock out Ack reset and restarted well | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00080664 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Wells 3 & 7 | WEST | Onsite for station check and to collect weekly micro sample W11656889 Well running Checked residuals mg/l Influent @1244 Free analyzer 2.34 grab 2.32 Total grab 3.80 Effluent @1247 Free analyzer 1.74 grab 1.73 Total grab 2.02 Rotated hypo pump duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012471 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Wells 3 & 7 | WEST | Onsite for station check Well duty active Checked residuals mg/l Effluent @1106 Free analyzer 1.79 grab 1.62 Total grab 1.88 Influent @1114 Free analyzer 2.15 grab 2.20 Total grab 3.40 Silicate p2 63% Hypo p1 26% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00084893 | 0 | 0
2026-03 | 2026-03-16 | Nobleton Wells 3 & 7 | WEST | Onsite for station check Duty active Checked residuals mg/l Influent @0945 Free analyzer 2.22 grab 2.19 Total grab 3.44 Effluent @0943 Free analyzer 1.76 grab 1.66 Total grab 1.95 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012416 | 0 | 0
2026-03 | 2026-03-20 | Nobleton Wells 3 & 7 | WEST | Onsite for station check Well running in manual Checked residuals mg/l Effluent @0944 Free analyzer 1.58 grab 1.57 Total grab 1.73 Influent @0956 Free analyzer 2.05 grab 2.02 Total grab 3.40 Sillicate p1 85% , 81.32 ml/min Hypo p1 25%, 61.55 ml/min , 56.5%df Deactivated well Noticed leak on fittings of inlet to effluent cl17 Closed valve resulting in no flow to analyzer an low residual readings Changed tubing and fittings Opened valve to regain flow Primed hypo 2 and place back to auto Primed both silicate pumps @1040 Influent grab Free analyzer 1.36 grab 1.51 Adjusted analyzer Some how analyzer went to 3.25 and then read 0.00 mg.l Tried brief prime cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | leak [infrastructure] | 0.00029595 | 0 | 0
2026-03 | 2026-03-18 | Nobleton Wells 3 & 7 | WEST | Onsite for station check and to collect weekly micro sample W11672653 Well running Checked residuals mg/l Influent @1353 Free analyzer 2.28 grab 2.24 Effluent @1350 Free analyzer 1.80 grab 1.76 Total 2.06 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0017455 | 0 | 0
2026-03 | 2026-03-19 | Nobleton Wells 3 & 7 | WEST | Checked/troubleshoot hypo pump #2 and power receptacle, did not find any problems. | FLAG | stage2_low_confidence | 0.012246 | ML: above threshold (no LLM available) — 0.012 |  | 0.012246 | 0 | 0
2026-03 | 2026-03-17 | Nobleton Wells 3 & 7 | WEST | Onsite to complete work orders Cleaned ntu analzyer and calibrated with 20 ntu vial Cleaned cl17 analyzers Grabs after Effluent Free analyzer 1.57 grab 1.58 Influent Free analyzer 1.46 grab 1.49 Started well hypo p1 fail to start alarm interlocked well Restarted well | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; alarm [control_system] | 0.0042703 | 0 | 0
2026-03 | 2026-03-02 | Nobleton Wells 3 & 7 | WEST | Onsite for station check Well running in. Schedule mode, placed in manual to keep it on Effluent @1343 Free analyzer 1.61 grab 1.63 Total grab 1.87 Influent @1345 Free analyzer 2.10 grab 2.05 Total 2.90 Tried troubleshooting hypo p1 Caused well to interlocking by having both hypo pumps in manual Low influent interlock came in Checked residuals mg/l Influent @1421 Free analyzer 0.37 grab 0.39 Started to backlash Influent @1433 Free analyzer 1.53 grab 1.54 Stopped back flush approximately 10m3 Restarted well | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00010994 | 0 | 0
2026-03 | 2026-03-27 | Nobleton Wells 3 & 7 | WEST | Onsite for station check Checked residuals Influent @1255 Free analyzer 1.55 grab 1.32 Total grab 1.57 Adjusted free analyzer Effluent @1303 Free analyzer 1.48 grab 1.42 Total 1.68 Changed reagents in cl17 analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00084627 | 0 | 0
2026-03 | 2026-03-10 | Nobleton Wells 3 & 7 | WEST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-13 | Nobleton Wells 3 & 7 | WEST | Onsite for station check Well running in manual Checked residuals mg/l Influent @1359 Free analyzer 2.12 grab 2.05 Total grab 3.40 Effluent @1354 Free analyzer 1.74 grab 1.73 Total grab 1.93 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013062 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Wells 3 & 7 | WEST | On site for station check and to collect weekly micro sample W11690158 Well running Checked residuals mg/l Influent @1136 Free analyzer 2.22 grab 2.16 Effluent @1115 Free analyzer 1.57 grab 1.44 Total grab 1.72 Adjusted effluent analyzer Hypo p1 25%, 60.58ml/min, 55.25%df Nasi p1 68%, 81.68ml/min | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00084949 | 0 | 0
2026-03 | 2026-03-23 | Nobleton Wells 3 & 7 | WEST | Onsite for station check Well duty active Checked residuals mg/l Effluent @1005 Free analyzer 1.46 grab 1.40 Total grab 1.65 Influent @1008 Free analyzer 2.13 grab 2.06 Primed hypo p2 Hypo p1 24%, 59.52 ml/min, 54,75%df Nasi p1 67% , 80.94 ml/min | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0006955 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Wells 5 & 6 | WEST | Silicate top up (45.53 to 76.73cm) | FLAG | stage2_low_confidence | 0.0097828 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097828 | 0 | 0
2026-03 | 2026-03-30 | Nobleton Wells 5 & 6 | WEST | -on site to complete chlorinator rebuilds -rebuilt and calibrated both chlorinators -backflushed during calibrations -started well and tested both chlorinators in auto -no issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049918 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Wells 5 & 6 | WEST | Onsite for station check Well running in manual Checked residuals mg/l Influent @1227 Free analyzer 2.74 grab 2.70 Total grab 3.72 Effluent @1230 Free analyzer 2.01 grab 1.92 Total grab 2.38 Primed silicate p1 Reduced p2 max flow from 90 to 85 ml/min | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010125 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Wells 5 & 6 | WEST | Onsite to complete station check and collect weekly micro sample Well running Checked residuals mg/L Influent @1344 Free analyzer 2.90 grab 2.84 Effluent @1348 Free analyzer 1.84 grab 1.88 Total grab 2.48 Nasi P1 30%,47,1 ml/min Chlrntr 2 59%,154%DF | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0011857 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Wells 5 & 6 | WEST | Flushed ntu analyzer Ran silatze pumps to sight glass P1 160 ml/min/ P2 200 ml/,min Started well Uncommanded stop, shut well down T.Hudson onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031713 | 0 | 0
2026-03 | 2026-03-12 | Nobleton Wells 5 & 6 | WEST | -man/start well to test silicate system -primed silicate pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053306 | 0 | 0
2026-03 | 2026-03-12 | Nobleton Wells 5 & 6 | WEST | -remotely monitor station NTU -pump 1 was able to bring down station NTU to 0.08 NTU - at max flow 50ml/min (96%) dosage still low on with pump 1 running -pump 2 speed set to 75 (73%) - will monitor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064771 | 0 | 0
2026-03 | 2026-03-04 | Nobleton Wells 5 & 6 | WEST | Onsite to complete station check and to collect weekly micro sample Well running Checked residuals mg/l Influent @1132 Free analyzer 2.77 grab 2.88 Total grab 3.84 Effluent @1135 Free analyzer 2.02 grab 1.94 Total grab 2.30 Flushed ntu analyzer sample line causing spike Primed silicate pumps 1&2, noticed air in lines Uncommanded stop came in shutting down well Ack reset and it came in again Ack reset and started well Adjusted well flow from 25 to 28 L/s Changed reagents in both cl17 analyzers Cl2 appeared to be dosing ineffective reduced flow back to 25l/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00084042 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Wells 5 & 6 | WEST | -on site to replace chlorine ejector #1 -replaced ejector and vacuum tested chlorine system - ok -started well in manual and tested chlorinator #1 in auto, adjusted dosage factor down due to high influent residual -will monitor -primed silicate pump 2 | FLAG | stage2_low_confidence | 0.012073 | ML: above threshold (no LLM available) — 0.012 |  | 0.012073 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Wells 5 & 6 | WEST | Onsite for station check Well duty active Checked residuals mg/l Influent @1228 Free analyzer 2.79 grab 2.88 Total grab 2.72 Effluent @1230 Free analyzer 2.02 grab 2.01 Total grab 2.58 Stopped well to clean ntu analyzer Primed both dislocated pumps and restarted well | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010805 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Wells 5 & 6 | WEST | Attending site to check issues with silicate pump speed feedback not matching speed setpoint (W11726510). Reset parameters so that pump displays are in set to show RPM, and performed drawdown testing on both pumps with Jacob and Tim. Operations will monitor and advise is any other issues arise. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.043729 | ML: above threshold (no LLM available) — 0.044 |  | 0.043729 | 0 | 0
2026-03 | 2026-03-05 | Nobleton Wells 5 & 6 | WEST | Onsite to investigate Lo influent Checked residual mg/l @0935 Free analyzer 0.98 grab 0.92 @0936 started backflush @1000 Influent free analyzer 1.10 grab 1.11 @1002 stopped backflush Approximately 19m3 Restarted well in manual at 23l/s Influent hihi alarm came in Reduced dosage factor until residual stabilized Checked residuals mg/l Influent free @1111 Analyzer 2.79 grab 2.88 Effluent free @1115 Analyzer 2.26 grab 2.15 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00046911 | 0 | 0
2026-03 | 2026-03-02 | Nobleton Wells 5 & 6 | WEST | Onsite for station check Well running in manual @1117 Influent analyzer 2.83 grab 3.12 Total grab 3.76 @1124 Effluent free analyzer 2.26 grab 2.42 Total grab 2.94 Adjusted both cl17 analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0015716 | 0 | 0
2026-03 | 2026-03-20 | Nobleton Wells 5 & 6 | WEST | Onsite for station check Well running in manual Checked residuals mg/l Effluent @1142 Free analyzer 1.62 grab 1.72 Total 2.13 Influent @1147 Free analyzer 2.71 grab 2.62 Total grab 4.13 Sillicate p2 29% , 47.4 ml/min Chlorinator 1 54%, 140% df, 30 ppd Earlier in day changed cl2 cylinder with J.Williams | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00062781 | 0 | 0
2026-03 | 2026-03-16 | Nobleton Wells 5 & 6 | WEST | Onsite for station check Well running in manual Checked residuals mg/l Influent @1015 Free analyzer 2.87 grab 2.90 Total grab 3.46 Effluent @1018 Free analyzer 1.69 grab 1.77 Total grab 2.03 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0013062 | 0 | 0
2026-03 | 2026-03-18 | Nobleton Wells 5 & 6 | WEST | Onsite to complete station check and to collect weekly micro sample W11672653 Well duty active Checked residuals Influent @1124 Free analyzer 2.86 grab 3.28 Effluent @1130 Free analyzer 2.33 grab 2.34 Total grab 2.64 Adjusted influent analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0014512 | 0 | 0
2026-03 | 2026-03-27 | Nobleton Wells 5 & 6 | WEST | Onsite for station check Well running in manual Checked residuals mg/l Influent @1220 Free analyzer 2.80 grab 2.94 Effluent @1228 Free analyzer 1.86 grab 1.85 Total grab 2.14 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0012122 | 0 | 0
2026-03 | 2026-03-23 | Nobleton Wells 5 & 6 | WEST | Onsite for station check Well running Checked residuals mg/l Effluent @1055 Free analyzer 2.09 grab 2.17 Total grab 2.64 Influent @1058 Free analyzer 2.77 grab 2.88 Total grab 3.72 Chlorinator 1 59%, 154%df , 32 ppd Nasi p2 30%, 48 ml/mib | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00080243 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Wells 5 & 6 | WEST | Onsite for station check and to collect weekly micro sample W11690158 Well running Checked residuals mg/l Influent @1247 Free analyzer 2.74 grab 3.10 Total grab 3.80 Adjusted free analyzer Effluent @1249 Free analyzer 2.09 grab 2.06 Total grab 2.42 Chlorinator 1 32ppd, 58% Nasi p2 30%, 47.3 ml/min | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010912 | 0 | 0
2026-03 | 2026-03-12 | Nobleton Wells 5 & 6 | WEST | On site to investigate silicate issues Ran draw down on pump one When checking silicate injection point lines for air in advertently bumped into chlorine injection point line and broke the lance Shut down well Isolated the pipe Took out broken injection point and isolated corps stop Placed chlorinator one in booster pump, one in manual and out of service | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; oos [equipment_failure] | out of service [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-11 | Nobleton Wells 5 & 6 | WEST | -on site to troubleshoot silicate pumps -notice issue with pump speed on chemical pumps - informed Erik S - will attend -man/started well 5 with both silicate pull at 100% -verified analyzer -influent 13:05: 2.80mg/l grab: 2.58mg/l - adjusted -effluent 13:10: 1.91mg/l grab -treated total grab: -reagents all ok | FLAG | stage2_low_confidence | 0.0076886 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076886 | 0 | 0
2026-03 | 2026-03-10 | Nobleton Wells 5 & 6 | WEST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-17 | Nobleton Wells 5 & 6 | WEST | On site to complete work orders Completed jhsc Back on site to investigate diesel spill sump Emergency shower was left dripping, resulting in filling the sump pit Pumped pit out until the alarm cleared Well started an auto Noticed chlorinator 2 did not appear to be dosing tried to open chlorinator further , interlocked the well due to chlorinator being in local Restarted well with chlorinator 1 duty But well shut down due to low influent residual Took influent grab Analyzer 0.06 grab 2.20 Next reading residual recovered and alarm was reset Restart restarted well with chlorinator 2 Appeared to be dosing fine | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; emergency [critical]; work order [maintenance_action]; alarm [control_system]; drip [infrastructure] | spill [critical]; emergency [critical]; work order [maintenance_action]; alarm [control_system]; drip [infrastructure] |  | 1 | 0
2026-03 | 2026-03-16 | Nobleton Wells 5 & 6 | WEST | In to troubleshoot silicate system. Replace tube element and roller on Si P1 (roller changed from ?super? to regular roller with 2 active/ 2 passive rollers. -poor performance at lower speeds. Replaced suction / discharge tubing and fittings to PE tubing and Parker fittings 1/2 from 3/8 and tested. Replaced calibration column blow off line with 1/2 connection and ran to drain conduit. Tested Si P2 to system pressure: -drawdowns and 25 and 40% speeds = 168ml/min -changed Si P1 max pump capacity SP to 160ml/min and rotated into duty. Install replacement injector lance and 3/4 corp stop for chlorinator 1 discharge line and tested. Replaced turbidimeter sample line back to 1/4 and ran to sample sink. Run W5 in auto with chlorinator 1 and silicate P1 to test dosing and performance after maintenance. | FLAG | stage2_low_confidence | 0.046919 | ML: above threshold (no LLM available) — 0.047 |  | 0.046919 | 0 | 0
2026-03 | 2026-03-16 | Nobleton Wells 5 & 6 | WEST | -on site to troubleshoot silicate system -replaced silicate pump 2 element -returned silicate pump 2 to pvc suction line -started well and performed drawdowns into system, pump 2 max flow = 175 ml/min -set pump 2 scada max flow setpoint to 160 ml/min, will monitor dosage calculation | FLAG | stage2_low_confidence | 0.017953 | ML: above threshold (no LLM available) — 0.018 | scada [control_system] | 0.017953 | 0 | 0
2026-03 | 2026-03-31 | Queensville Elevated Tank | CENTRAL | Onsite for station check and weekly Bacti sample Recordings in PWQ sheet Residuals (mg/L) Inlet Grab @ 15:00 Free: 0.03 Total: 2.96 Inlet Analyzer @ 15:00 Free: 0.03 Total: 2.84 Outlet Grabs @ 14:55 Free: 0.03 Total: 2.4 Mono: 1.98 FA: 0.09 TA: 0.48 NO2: 0.005 Temp: 10.8 Outlet Analyzer @ 14:55 Analyzer Free: 0.10 Analyzer Total: 2.17 adjusted to 2.40 Station ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00034401 | 0 | 0
2026-03 | 2026-03-10 | Nobleton Wells 5 & 6 | WEST | Onsite to complete work orders Diesel Start 85.1/82.9 cm 880/ 856 L 261:10 hrs Stop 84.0 / 81.9 cm 868/ 845 L 262:29 hrs Tested cl2 leak detection Completed subsection of silicate system Cleaned injection points Ran hot water through lines Adjusted fittings Primed both pumps Exercised manual valves Exercised prv Cleaned cl17 analyzers Grabs before Influent Free analyzer 2.04 grab 1.93 Effluent Free analyzer 2.00 grab 2.05 Calibrated ntu analyzer with 20 ntu vial and flushed sample lines out Grabs after Influent Free analyzer 2.00 grab 1.99 Effluent Free analyzer 2.01 grab 1.96 Completed cl2 system inspection No issues observed Started well in manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; leak [infrastructure] | 0.00013923 | 0 | 0
2026-03 | 2026-03-04 | Queensville Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Weekly bacti and operational samples taken Verified analyzers, readings and grabs entered into PWQ sheet Inlet Free@1440 G:0.05 A:0.01mg/L Inlet Total@1444 G:2.70 A:2.67mg/L Outlet Free@1445 G:0.06 A0.08mg/L Outlet Total@1448 G:2.46 A:2.41mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061448 | 0 | 0
2026-03 | 2026-03-25 | Queensville Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Weekly bacti and operational samples taken Verified analyzers and entered all readings and grabs into PWQ sheet Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1103 G:0.07 A:0.10mg/L Inlet Total@1105 G:2.78 A:2.85mg/L Outlet Free@1107 G:0.07 A:0.11mg/L Outlet Total@1110 G:2.20 A:2.23mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061224 | 0 | 0
2026-03 | 2026-03-09 | Queensville Elevated Tank | CENTRAL | On-site due to an inlet free hi hi alarm. Inlet analyzer reading 0,33mg/L on arrival. Average of three grabs, 0.09, 0.11, 0.15mg/L. Adjusted inlet free to 0.11mg/L Will continue to monitor remotely | FLAG | stage2_low_confidence | 0.017956 | ML: above threshold (no LLM available) — 0.018 | alarm [control_system] | 0.017956 | 0 | 0
2026-03 | 2026-03-05 | Queensville Elevated Tank | CENTRAL | On-site for various work orders: Dechlor puck dispenser inspected, cleaned and filled JHSC inspection completed Manual valve exercised Generator test completed Inlet/Outlet heat trace system inspection general housekeeping Analyzer maintenance and verification | FLAG | stage2_low_confidence | 0.014124 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action] | 0.014124 | 0 | 0
2026-03 | 2026-03-11 | Queensville Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Weekly bacti sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1110 G:0.06 A:0.10mg/L Inlet Total@1112 G:2.18 A:2.13mg/L Outlet Free@1118 G:0.10 A: 0.09mg/L Outlet Total@1120 G:2.10 A:2.14mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048909 | 0 | 0
2026-03 | 2026-03-18 | Queensville Elevated Tank | CENTRAL | On-site for a station and equipment check No issues found Changed inlet reagents (both) Adjusted inlet total to 2.78mg/L based on avg of three grabs, from 2.62mg/L Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1036 G:0.05 A:0.07mg/L Inlet Total@038 G:2.78 A:2.78mg/L Outlet Free@1052 G:0.07 A:0.08mg/L Outlet Total@1045 G:2.28 A:2.23mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005883 | 0 | 0
2026-03 | 2026-03-31 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for station check, weekly BACTI and iron monitoring samples Recordings in PD sheet Influent @ 09:29 Free Grab: 3.04 mg/L Analyzer Free: 2.92 mg/L adjusted to grab Effluent @ 09:32 Free Grab: 2.80mg/L Analyzer Free 2.58 mg/L adjusted to grab Treated @ 09:45 Free Grab: 0.12 mg/L Total Grab: 3.44 mg/L Analyzer Free: 0.21 mg/L Analyzer Total: 3.55 mg/L adjusted to grab SL1000 grabs FA; 0.05 TA; 0.62 Mono; 2.88 Nitrite; Temp; 9.7 Adjusted chlorine to ammonia ratio from 4.0 to 4.1 because of higher effluent free chlorine analyzer readings after adjustment. Station ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0006882 | 0 | 0
2026-03 | 2026-03-06 | Queensville Wells No. 1 and 2 | CENTRAL | 16:04. Onsite to respond to wells interlocked due to low influent. Well 1 started 3 times starting at 14:41 but shortly intlerocked on low influent residual. The contact tank has not been cleared (at 79 m3). Treated water total chlorine reading 2.74 mg/l. 16:22 verified analyzers: Influent free grab: 0.03. Analyzer: 0.03. Treated total grab: 2.74. Analyzer: 2.73. Treated free grab: 0.19. Analyzer: 0.14. 16:27 placed dechlorination pucks at outfall and initiated a backflush of contact chamber. 16:30 Tested chlorine dosing system. Found booster pump 2 fully air locked, likely occured ealier during isolation and repair work on the waste valve. Purged booster pumps of air. No issues remaining with chlorine system. 17:42 Influent free grab: 0.53. Analyzer: 0.50 mg/l. Completed backflush and reset CT timer on SCADA. 17:45 placed wells back in auto. 17:50 Found chlorine system again not functioning and shut off well. Booster pump 1 air locked again. Backflushed well briefly to remove any water in contact chamber that was not dosed. Bleeded off air from both booster pumps again and started well again at 18:11. 18:55 Verfied treated free grab: 0.10. Analyzer: 0.10. Total grab: 1.30 . Analzyer: 1.24. No issues remain. Notifed ROC work complete and to place well 1 back to auto | FLAG | stage2_low_confidence | 0.15528 | ML: above threshold (no LLM available) — 0.155 | oos [equipment_failure]; repair [maintenance_action]; scada [control_system] | 0.15528 | 0 | 0
2026-03 | 2026-03-03 | Queensville Wells No. 1 and 2 | CENTRAL | Onsite for chlorinator rebuilds and calibration. Informed ROC. ROC placed wells manual off Informed OIC Purged chlorine system and isolated. Rebuilt chlorinators and performed vacuum test. All good, no leaks. Put chlorine gas back in service and performed 11pt calibration. Verified calibration using scada. All ok Maximum gas flow is 70 (#1) and 75% (#2) Informed operations. Operations will come to site and back flush the system Informed ROC. Left site | FLAG | stage2_low_confidence | 0.0557 | ML: above threshold (no LLM available) — 0.056 | scada [control_system]; leak [infrastructure] | 0.0557 | 0 | 0
2026-03 | 2026-03-10 | Queensville Wells No. 1 and 2 | CENTRAL | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-09 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check CL2 2 booster pump locked out. Unable to reset and return to service Work order created. Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Operational sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1111 G:2.78 A:2.68mg/L Effluent Free@1117 G:0.13 A:0.10mg/L Treated Free@1121 G:0.10 A:0.09mg/L Treated Total@1122 G:2.76 A:2.71mg/L | FLAG | stage2_low_confidence | 0.029311 | ML: above threshold (no LLM available) — 0.029 | oos [equipment_failure]; work order [maintenance_action]; work order created [maintenance_action] | 0.029311 | 0 | 0
2026-03 | 2026-03-02 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Topped mineral oil well 1 Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Operational sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1030 G:3.12 A:3.03mg/L Effluent Free@1032 G;0.25 A:0.20mg/L Treated Free@1034 G:3.32 A:3.25mg/L Treated Total@1040 G:3.32 A:3,25mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057043 | 0 | 0
2026-03 | 2026-03-06 | Queensville Wells No. 1 and 2 | CENTRAL | Rebuild queensville well 1 wasting valve installed rubber repair kit | FLAG | stage2_low_confidence | 0.020383 | ML: above threshold (no LLM available) — 0.02 | repair [maintenance_action] | 0.020383 | 0 | 0
2026-03 | 2026-03-04 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Topped up ammonia day tank 2 Topped up both NaSi day tanks. Took weekly bacti samples Chemical levels and systems ok 15 cylinders and 4 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@1104 G:3.02 A:2.99mg/L Effluent Free@1106 G:2.68 A:2.73mg/L Treated Free@1107 G:0.16 A:0.21mg/L Treated Total@1111 G:3.38 A:3.38 Mono-2.81 FA-0.06 TA-0.56 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035216 | 0 | 0
2026-03 | 2026-03-10 | Queensville Wells No. 1 and 2 | CENTRAL | On-site to perform a number of PM's -CL2 gas detector test completed -Cylinder change with JZ, bank B -Deep well exhaust inspection and maintenance, both wells completed -JHSC inspection completed -Dechlor puck dispenser inspected -General Housekeeping -Cleaned and inspected flow control valve well 2 | FLAG | stage2_low_confidence | 0.0088734 | ML: above threshold (no LLM available) — 0.009 |  | 0.0088734 | 0 | 0
2026-03 | 2026-03-11 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 9 cylinders and 8 bags of ammonia in inventory Took weekly bacti samples Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1253 G:3.06 A: 2.91mg/L Effluent Free@1300 G:2.46 A:2.51mg/L Treated Free@1303 G:0.20 A:0.21mg/L Treated Total@1307 G:3.48 A:3.40mg¦L Mono-2.72 FA-0.02 TA-0.56mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033721 | 0 | 0
2026-03 | 2026-03-27 | Queensville Wells No. 1 and 2 | CENTRAL | Onsite with Cole W to respond to CL2 leak alarm- station interlocked, informed by ROC Upon arrival, found leak coming from one of the empty chlorine cylinders- cylinder not fully closed. Fully closed cylinder- no leak outstanding. Re-opened all chlorine cylinders and ack/reset all alarms via scada- informed ROC. Station placed back into auto. Station/equipment- Ok | FLAG | stage2_low_confidence | 0.026964 | ML: above threshold (no LLM available) — 0.027 | scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.026964 | 0 | 0
2026-03 | 2026-03-20 | Queensville Wells No. 1 and 2 | CENTRAL | Station and equipment check Took grabs @ 10:00 am (duty not active) Treated Total: 2.60 mg/l Treated Free: 0.05 mg/l Chemicals/reagents ok Receive and return 12 chlorine cylinders Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005558 | 0 | 0
2026-03 | 2026-03-12 | Queensville Wells No. 1 and 2 | CENTRAL | On site with Total Power for annual load test | FLAG | stage2_low_confidence | 0.012727 | ML: above threshold (no LLM available) — 0.013 |  | 0.012727 | 0 | 0
2026-03 | 2026-03-25 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check NaSi pump 2 OOS Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Weekly bacti and operational samples taken Adjusted ammonia pump 1 max to 205mL/min from 218mL/min. First FA grab was 0.01, after adjusting FA grab 0.03mg/L Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0906 G:2.64 A:2.59mg/L Effluent Free@0909 G:2.44 A:2.54mg/L Treated Free@0905 G:0.20 A:0.23mg/L Treated Total@0914 G:3.48 A:3.54mg/L | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-27 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found NaSi pump 2 back in service. New check valve installed at injector Cylinder change with JZ bank 1 Topped up ammonia day tank 2 Topped up NaSi day tanks Changed Influent reagents Verified analyzers and entered all readings and grabs into PWQ sheet Influent free@0850 G:2.96 A:2.9mg/L Effluent free@0855 G:0.19 A:0.17mg/L Treated free@0858 G:0.18 A:0.13mg/L Treated Total@0900 G:2.86 A;2.94mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059113 | 0 | 0
2026-03 | 2026-03-23 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check. No issues found. Chemical levels and systems ok NaSi pump 2 still OOS 15 cylinders and 2 bags of ammonia in inventory New rebuild kit left in ammonia room for pumps. Topped ammonia day tank 1 Topped up NaSi day tanks. Topped up mineral oil pot well 1 Changed cylinders with A Bell bank 2 Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0918 G:2.74 A:2.81mg/L Effluent Free@0923 G:0.12 A:0.11mg/L Treated Free@0924 G:0.07 A:0.08mg/L Treated Total@0927 G:2.78 A:2.84mg/L | FLAG | stage2_low_confidence | 0.011517 | ML: above threshold (no LLM available) — 0.012 | oos [equipment_failure] | 0.011517 | 0 | 0
2026-03 | 2026-03-17 | Queensville Wells No. 1 and 2 | CENTRAL | On site to help Kyle Rae with control wiring | FLAG | stage2_low_confidence | 0.012707 | ML: above threshold (no LLM available) — 0.013 |  | 0.012707 | 0 | 0
2026-03 | 2026-03-24 | Queensville Wells No. 1 and 2 | CENTRAL | Find treated total chlorine hi alarm triggered at 15:24 during SCADA review. Placed chlorine dosing system to automatic mode. Dosage factor should drop until target influence is reached. | FLAG | stage2_low_confidence | 0.008029 | ML: above threshold (no LLM available) — 0.008 | scada [control_system]; alarm [control_system] | 0.008029 | 0 | 0
2026-03 | 2026-03-17 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for chemical systems testing. Drawdowns completed on ammonia Hot flushed and primed both NaSi lines. NaSi 2 is OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-03 | Queensville Wells No. 1 and 2 | CENTRAL | On site to change well one manual speed potentiometer. Dan and I replaced and tested to confirmed operation. Cleared alarms and left well one in manual off. Under direction of oic | FLAG | stage2_low_confidence | 0.029077 | ML: above threshold (no LLM available) — 0.029 | alarm [control_system]; alarms [control_system] | 0.029077 | 0 | 0
2026-03 | 2026-03-03 | Queensville Wells No. 1 and 2 | CENTRAL | Onsite with Donny M to replace chlorine lines and regulators. Purged chlorine system. replaced the chlorine parts tested vacuum-ok tested for leaks-ok back flushed, added dechlor to outfall ran well 1 and tested both chlorinators. adjusted dosing factors for both chlorinators. site ok | FLAG | stage2_low_confidence | 0.013123 | ML: above threshold (no LLM available) — 0.013 | leak [infrastructure] | 0.013123 | 0 | 0
2026-03 | 2026-03-07 | Queensville Wells No. 1 and 2 | CENTRAL | 16:00 Onsite to respond to wells interlocked due to low influent on start up. Found localized flooding up to due to recent rain and snowmelt in storm ditch on east side of building. Notified ROC. Tested chlorine booster pump 2. Found it air locked. Bleed off air. Retested and booster pump will not start. Placed oos. Booster pump 1 ran ok with no air lock issues. 16:15 began back flushing contact chamber after placing declination pucks at outfall. 16:54 completed back flush. Reset contact tank calculations on SCADA with backflush completed. Verified influent free gab: 1.54. Analyzer: 1.62 mg/l. 17:00 started well 1 in manual. Waste valve is open at start up but found well not wasting. Found waste line isolation valve closed. Opened valve and shut down well 1. Briefly backflushed again. 17:28 started well 1 in manual with no further issues. Chlorine booster pump 2 remains oos. Notified roc system back in operation. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; oos [equipment_failure]; scada [control_system] | flood [critical]; oos [equipment_failure]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | Queensville Wells No. 1 and 2 | CENTRAL | On site to replace pilot illumination and contacts on well pump 2 starter. With assistance from Will Mather and ROC, well placed in manual, taken out of service and de-energized. Work completed. ROC notified, well placed in remote and returned to operation. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-27 | Queensville Wells No. 1 and 2 | CENTRAL | On-site due to a call from ROC about a potential CL2 leak. Upon arrival sensor reading 0.0. Reset halogen system, tightened up valves. Cleared interlock on OIT panel. Will continue to monitor remotely | FLAG | stage2_low_confidence | 0.03112 | ML: above threshold (no LLM available) — 0.031 | leak [infrastructure] | 0.03112 | 0 | 0
2026-03 | 2026-03-16 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 9 cylinders and 6 bags of ammonia in inventory Changed effluent free analyzer reagents Topped up mineral pots Operational sample taken Adjust ammonia dosage on pump 2 to increase FA. First grab was 0.01mg/L after adjustment to 203mL/min from 207mL/min grab was 0.04mg/L Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1221 G:2.76 A:2.88mg/L Effluent Free@1229 G:2.56 A:2.52mg/L Treated Free@1231 G:0.26 A:0.23mg/L Treated Total@1233 G:3.30 A:3.42mg/L Mono-2.74 FA-0.04 TA-0.57mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0072081 | 0 | 0
2026-03 | 2026-03-06 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 4 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Adjusted effluent free based on an average of 3 grabs. 2.54 from 2.77mg/L Influent Free@1230 G:2.66 A:2.7mg/L Effluent Free@1234 G:2.54 A:2.54mg/L Treated Free@1240 G:0.18 A:0.22mg/L Treated Total@1243 G:3.44 A:3.47mg/L Mono-2.79 FA-0.04 TA-0.59mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042011 | 0 | 0
2026-03 | 2026-03-30 | Queensville Wells No. 3 and 4 | CENTRAL | See photos/paper log book | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-17 | Queensville Wells No. 1 and 2 | CENTRAL | On site to investigate chlorine booster pump #2 and work on well pump #2. Well pump #2 de-energized. ROC notified. Found chlorine booster pump 2 to have opened fuse feeding starter. Confirmed motor in good condition with megger. Replaced fuse, tested operation with operator Will Mather and returned to service. Well pump 2 control illumination and terminals replaced. With assistance from Ben Hess and ROC, well pump 2 placed in auto and returned to normal operation. | FLAG | stage2_low_confidence | 0.019614 | ML: above threshold (no LLM available) — 0.02 | oos [equipment_failure] | 0.019614 | 0 | 0
2026-03 | 2026-03-18 | Queensville Wells No. 1 and 2 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok NaSi pump 2 still OOS Topped up ammonia day tank 2 9 cylinders and 4 bags of ammonia in inventory Took weekly bacti samples Analyzer maintenance completed NTU verification completed Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0849 G:3.00 A:2.90mg/L Effluent Free@0854 G:2.68 A:2.67mg/L Treated Free@0856 G:0.19 A:0.23mg/L Treated Total@0900 G:3.42 A:3.53mg/L Mono-2.87 FA-0.04 TA-0.60mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure] | 0.0057713 | 0 | 0
2026-03 | 2026-03-31 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for station check, weekly BACTI and iron monitoring samples Recordings in PD sheet Influent @ 13:40 Free Grab: 3.02 mg/L Analyzer Free: 2.97 mg/L Effluent @ 13:42 Free Grab: 2.90 mg/L Analyzer Free: 2.90 mg/L Treated @ 13:48 Free Grab: 0.07 mg/L Total Grab: 3.50 mg/L Analyzer Free: 0.16 mg/L Analyzer Total: 3.56 mg/L SL1000 grabs FA; 0.06 TA; 0.63 Mono; 2.87 Nitrite: Temp; 9.4 Station ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00044874 | 0 | 0
2026-03 | 2026-03-09 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Placed well 3 back into auto and rotated duties Chemical systems and levels ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1315 G:1.93 A:2.02mg/L Effluent Free@1319 G:0.17 A:0.22mg/L Treated Free@1320 G:0.02 A:0.04mg/L Treated Total@1324 G:2.12 A:2.21mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067407 | 0 | 0
2026-03 | 2026-03-10 | Queensville Wells No. 3 and 4 | CENTRAL | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-02 | Queensville Wells No. 3 and 4 | CENTRAL | Attending site to continue investigating erratic readings from Total chlorine analyzer (W11685985). Replaced entire analyzer again. Well was in manual off during maintenance work. Well 3 was started in manual before leaving site, via ROC. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.033809 | ML: above threshold (no LLM available) — 0.034 |  | 0.033809 | 0 | 0
2026-03 | 2026-03-12 | Queensville Wells No. 3 and 4 | CENTRAL | Onsite with D Moses and A Morvin (OJT) performed various work orders including all chemical systems inspections and drawdowns and testing flow control inspection exercise and cleaning Cl2 system inspection and leak test completed | FLAG | stage2_low_confidence | 0.031204 | ML: above threshold (no LLM available) — 0.031 | work order [maintenance_action]; leak [infrastructure] | 0.031204 | 0 | 0
2026-03 | 2026-03-12 | Queensville Wells No. 3 and 4 | CENTRAL | Onsite to commission treated total AIT (CL17sc) Informed ROC Maintenance onsite Commissioned and configured new AIT. Took grabs G=2.19mg/l A=2.17mg/l Issue with LoLo switch alarm. Input on PAC changes but no change on SCADA. Will discuss with PCS Wells are LOCAL OFF Informed operations and ROC. Wells are available to run Armed building and leftsbite | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system] | scada [control_system]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check CMP work order created for well 4 motor oil Topped up oil pot well 4 Weekly bacti samples taken Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@0831 G:2.54 A:2.65mg/L Effluent Free@0834 G:2.56 A:2.64mg/L Treated Free@0835 G:0.09 A:0.14mg/L Treated Total@0840 G:3.08 A:3.16mg/L Mono-2.53 FA-0.07 TA-0.57mg/L | FLAG | stage2_low_confidence | 0.0078808 | ML: above threshold (no LLM available) — 0.008 | work order [maintenance_action]; work order created [maintenance_action] | 0.0078808 | 0 | 0
2026-03 | 2026-03-02 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Operational sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0845 G:2.60 A:2.6g/L Effluent Free@0850 G:2.58 A:2.64mg/L Treated Free@0851 G:0.09 A:.13mg/L Treated Total@0907 G:3.18 A:3.19mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059871 | 0 | 0
2026-03 | 2026-03-11 | Queensville Wells No. 3 and 4 | CENTRAL | QVW34- CT Not Achieved Alarm. Notified Will M. He is running to waste. Directed to disregard. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058039 | 0 | 0
2026-03 | 2026-03-12 | Queensville Wells No. 3 and 4 | CENTRAL | Changed/replaced chlorine analyzer with new model. | FLAG | stage2_low_confidence | 0.013802 | ML: above threshold (no LLM available) — 0.014 |  | 0.013802 | 0 | 0
2026-03 | 2026-03-13 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check Well 3 in manual on after backlash of contact tank. Started back flush with dechlor at 0800 completed at 0819 with two Influent total grabs of 2.90 mg/L and 3.16mg/L Reset QV duties Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Took treated bacti sample. Changed Influent and effluent reagents Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1110 G:2.48 A:2.58mg/L Effluent Free@1112 G:2.64 A:2.54mg/L Treated Free@1114 G:0.11 A:0.14mg/L Treated Total@1117 G3.02 A:3.07mg/L | FLAG | stage2_low_confidence | 0.011097 | ML: above threshold (no LLM available) — 0.011 |  | 0.011097 | 0 | 0
2026-03 | 2026-03-18 | Queensville Wells No. 3 and 4 | CENTRAL | -Collected weekly BacT sample YD #W11672737 Grab: Influent free=2.62mg/L effluent free=2.08mg/L treated free=0.18mg/L total=2.52mg/L@16:10 Analyzer: Influent free=2.63mg/L effluent free=2.15mg/L treated free=0.13mg/L total=2.57mg/L | FLAG | stage2_low_confidence | 0.010782 | ML: above threshold (no LLM available) — 0.011 |  | 0.010782 | 0 | 0
2026-03 | 2026-03-23 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok. 15 cylinders and 6 bags of ammonia in inventory Topped up mineral oil pot well 4 Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1116 G:2.76 A: 2.70mg/L Effluent Free@1118 G:2.62 A:2.74mg/L Treated Free@1119 G:0.10 A:0.14mg/L Treated Total@1122 G:3.18 A:3.18mg/L Mono-2.61 FA-0.08 TA-0.60mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042147 | 0 | 0
2026-03 | 2026-03-25 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found. Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Weekly bacti and operational samples taken Verified all analyzers and entered all readings and grabs into PWQ sheet Influent Free@1221 G:2.30 A:2.38mg/L Effluent Free@1224 G:2.72 A:2.73mg/L Treated Free@1226 G:0.14 A:0.14mg/L Treated Total@1218 G:3.12 A:3.15mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067801 | 0 | 0
2026-03 | 2026-03-16 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found Chemical levels and systems ok. 15 cylinders and 6 bags of ammonia in inventory Topped up both mineral pots Run generator while under load of well 3 Generator hours start: 714h 34min End: 715h33m Fuel start 1759L. End 1724L 60Hz 601v coolant temp 160?f Oil Temp 169?F Oil pressure 89psi Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1001 G:2.74 A:2.80mg/L Effluent Free@1004 G:2.58 A:2.69mg/L Treated Free@1009 G:0.10 A:0.14mg/L Treated Total@1013 G:3.08 A:3.12mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039528 | 0 | 0
2026-03 | 2026-03-18 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check Wells locked out due to low Influent free Not dosing due to closed valve. Back flushed with dechlor. Restarted wells. Chemical systems and levels ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers JZ will take bacti samples | FLAG | stage2_low_confidence | 0.0097275 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097275 | 0 | 0
2026-03 | 2026-03-25 | Queensville Wells No. 3 and 4 | CENTRAL | On site with Dan Boate to finish cleanup work on Well #4 vfd cabinet and complete Well 3 and 4 PM?s. | FLAG | stage2_low_confidence | 0.012562 | ML: above threshold (no LLM available) — 0.013 |  | 0.012562 | 0 | 0
2026-03 | 2026-03-27 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check Installed new check valve on NaSi 2 injection point verified function Chemical levels and systems ok Topped up mineral pot well 3 Verified analyzers and entered all readings and grabs into PWQ sheet Influent free@1141 G:2.78 A:2.74mg/L Effluent free@1143 G:0.13 A:0.12mg/L Treated Free@1138 G:0.03 A:0.06mg/L Treated Total@1138 G:2.46 A:2.41mg/L | FLAG | stage2_low_confidence | 0.0076637 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076637 | 0 | 0
2026-03 | 2026-03-02 | Queensville Wells No. 3 and 4 | CENTRAL | Changed treated free reagents | FLAG | stage2_low_confidence | 0.012507 | ML: above threshold (no LLM available) — 0.013 |  | 0.012507 | 0 | 0
2026-03 | 2026-03-19 | Queensville Wells No. 3 and 4 | CENTRAL | On site with operator Will Mather to investigate Well Pump #3 fail to start. Conducted test run of well 3 in remote without incident. Pump ran for approximately 60 mins. Well 3 then placed in manual and run to waste. Pump was started and stopped 4 times to test operation. Fail to start could not be replicated. Well pump 3 returned to normal operation. | FLAG | stage1_keyword | 0.95 | Critical keyword match: incident [safety] | incident [safety] |  | 1 | 0
2026-03 | 2026-03-24 | Queensville Wells No. 3 and 4 | CENTRAL | Attending site to check push button issues on Influent chlorine analyzer (W11744080). Replaced all push buttons and verified reading. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.020658 | ML: above threshold (no LLM available) — 0.021 |  | 0.020658 | 0 | 0
2026-03 | 2026-03-20 | Queensville Wells No. 3 and 4 | CENTRAL | Station and equipment check Well duty not active during check Took grabs @ 8:40 am Treated Total: 2.20 mg/l Treated Free: 0.05 mg/l Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049428 | 0 | 0
2026-03 | 2026-03-24 | Queensville Wells No. 3 and 4 | CENTRAL | on_site for various work orders -JHSC inspection completed -Comprehensive housekeeping -Deep well exhaust maintenance/inspection both wells -Dechlor puck dispenser inspected - | FLAG | stage2_low_confidence | 0.016488 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action] | 0.016488 | 0 | 0
2026-03 | 2026-03-11 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No new issues found Verified wells isolated from system Ran wells to waste, in hand, in order to get weekly raw bacteria samples. Contact time not met alarm came in as a result It can be disregarded because of previous actions. Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1007 G:1.80 A:1.74mg/L Effluent Free@1010 G:0.11 A:0.09mg/L Treated Free@1011 G:0.05 A:0.04mg/L Treated Total@1014 G:2.18 A2.20mg/L | FLAG | stage2_low_confidence | 0.012755 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.012755 | 0 | 0
2026-03 | 2026-03-06 | Queensville Wells No. 3 and 4 | CENTRAL | On-site for a station and equipment check No issues found. Chemical levels and systems ok Topped up ammonia day tank 1 15 cylinders and 4 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1002 G:2.78 A:2.70mg/L Effluent Free@1003 G:0.16 A:0.16mg/L Treated Free@1009 G:0.07 A:0.06mg/L Treated Total@1012 G:2.60 A:2.57mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061988 | 0 | 0
2026-03 | 2026-03-30 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site for station check Check trends All okay station duty off 12:15- Grabs taken Free CL2-0.04 mg/L Total CL2- 2.01 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039315 | 0 | 0
2026-03 | 2026-03-11 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site to complete station check and weekly bacti W11657067 Checked trends: all ok Took chlorine grab and sample East cell 13:10 Free CL2: 0.06mg/l Total CL2: 1.46mg/l West cell 13:14 Free CL2: 0.03mg/l Total CL2: 1.42mg/l Equipment all ok Entered reading PWQ: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046068 | 0 | 0
2026-03 | 2026-03-31 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site to complete station check, operational sample and weekly bacti W11705742 Checked trends: all ok Took chlorine grab and sample West cell 14:10 Free CL2: 0.06mg/l Total CL2: 1.56mg/l East cell 14:15 Free CL2: 0.04mg/l Total CL2: 1.60 mg/l Equipment all ok Entered reading PWQ: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005069 | 0 | 0
2026-03 | 2026-03-03 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | Onsite for the following pm work orders. Informed ROC about the works being done. W11640420 RHPSWA, JHSC Health and Safety Inspection W11640701 RHPSWA, Ventilation System Inspection W11640724 RHPSWA, PRV Valve Inspection W11640863 RHPSWA, Pump & Motor Inspection, W11642274 RHPSWA, Comprehensive Housekeeping W11640981 RHPSWA, Flood Alarm Test W11641081 RHPSWA, Discharge Valve & Actuator Exercise & Inspection Station check Check trends All okay station duty off 13:00- Grabs taken Free CL2-0.03 mg/L Total CL2- 1.90 mg/L W11640747 RHRSWA, High/Low Temperature Alarm Test W11639808 RHRSWA, Dehumidifier Inspection & Cleaning W11639629 RHRSWA, Actuated Valve Exercise & Inspection W11641140 RHRSWA, External Venting Screens Inspection W11639852 RHRSWA, Sump Pit System Inspection W11640737 RHRSWA, Flood Alarm Test, | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | - reset power alarms -all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0058628 | 0 | 0
2026-03 | 2026-03-06 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site for station check Check trends All okay station duty off 13:40- Grabs taken Free CL2-0.05 mg/L Total CL2- 1.91 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039315 | 0 | 0
2026-03 | 2026-03-04 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | -on site to complete station check and weekly bacti W11637582 -checked trends: all ok -entered reading PWQ: all ok -took chlorine grab and sample west cell 13:15 -free cl: 0.08mg/l -total cl: 1.38mg/l -east cell 13:25 -free cl: 0.08mg/l -total cl: 1.42mg/l -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047379 | 0 | 0
2026-03 | 2026-03-11 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | wrong log entry. this log belongs to JFRS. See JFRS | FLAG | stage2_low_confidence | 0.01401 | ML: above threshold (no LLM available) — 0.014 |  | 0.01401 | 0 | 0
2026-03 | 2026-03-23 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | Station Check (pumping station) (no issues found) Input data to PWQ 12:35 Chlorine residual grab: (Free 0.04mg/l, Total 1.97mg/l) | FLAG | stage2_low_confidence | 0.0072615 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072615 | 0 | 0
2026-03 | 2026-03-09 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site for station check Check trends All okay station duty off 14:15- Grabs taken Free CL2-0.02 mg/L Total CL2- 1.98 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039315 | 0 | 0
2026-03 | 2026-03-25 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site to complete station check and weekly bacti W11690336 Checked trends: all ok Took chlorine grab and sample East cell 14:00 Free CL2: 0.06mg/l Total CL2: 1.57mg/l West cell 14:05 Free CL2: 0.05mg/l Total CL2: 1.60 mg/l Equipment all ok Entered reading PWQ: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046368 | 0 | 0
2026-03 | 2026-03-16 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site for station check Check trends All okay station duty off 13:15- Grabs taken Free CL2-0.06 mg/L Total CL2- 1.78 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039315 | 0 | 0
2026-03 | 2026-03-27 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site for station check Check trends All okay station duty off 14:00- Grabs taken Free CL2-0.05 mg/L Total CL2- 2.023 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039474 | 0 | 0
2026-03 | 2026-03-18 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site to complete station check, operational sample and weekly bacti W11672961 Checked trends: all ok Took chlorine grab and sample West cell 14:10 Free CL2: 0.06mg/l Total CL2: 1.44mg/l East cell 14:05 Free CL2: 0.05mg/l Total CL2: 1.48 mg/l Equipment all ok Entered reading PWQ: all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005069 | 0 | 0
2026-03 | 2026-03-20 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | WEST | On site for station check Check trends All okay station duty off 13:54- Grabs taken Free CL2-0.00 mg/L Total CL2- 2.03 mg/L entered values in PWQ sheet Equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039315 | 0 | 0
2026-03 | 2026-03-31 | Richmond Hill Bloomington Elevated Tank | CENTRAL | On-site for station check and sampling. W11705550 14:16 Deactivated PD9 duty. Tower level 69% and draining at 12 l/s. 14:30 Verified inlet analyzer (mg/l): Free chlorine grab: 0.08 Total chlorine grab: 2.08 Analyzer: 2.06 14:35 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.03. Total chlorine grab: 1.83. analyzer: 1.88. Free ammonia: 0.11 Total ammonia: 0.44 Monochloramine: 1.66 Nitrite: 0.004. Recorded readings into PD sheets. Station and equipment: No issues identified. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038733 | 0 | 0
2026-03 | 2026-03-04 | Richmond Hill Bloomington Elevated Tank | CENTRAL | On-site for station check and sampling. W11637390. 13:26 Deactived PD9 duty. 13:30 Tower level 69% and draining at 10 l/s. 13:31 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.06. Total chlorine grab: 1.94. Analyzer: 2.01. 13:38 verified outlet analyzer and collected sample. free chlorine grab: 0.06. Total chlorine grab: 1.81. Analyzer: 1.85. Ph: 7.98. Free ammonia: 0.11 Total ammonia: 0.43 Monochloramine: 1.62. ?Nitrite: 0.000. Temperature: 4.9 celsius. Recorded data in process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029362 | 0 | 0
2026-03 | 2026-03-11 | Richmond Hill Bloomington Elevated Tank | CENTRAL | On-site for station check and sampling. MBHP - W11656917. 10:05 Tower level 67% and filling at 87 l/s. 10:08 Verified inlet analyzer (mg/l): Free chlorine grab: 0.11 Total chlorine grab: 1.96 Analyzer: 2.01. 10:16 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.02. Total chlorine grab: 1.80. analyzer: 1.85. Free ammonia: 0.11 Total ammonia: 0.43 Monochloramine: 1.61. Nitrite: 0.004. pH: 8.0. temperature: 6.4 celsius. Recorded readings into PD sheets. Station and equipment: No issues identified. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0020548 | 0 | 0
2026-03 | 2026-03-18 | Richmond Hill Bloomington Elevated Tank | CENTRAL | On-site for station check and sampling. MBDW - W11672825. 10:13 Deactivated PD9 duty. 10:16Tower level 66% and draining at 10 l/s. 10:37 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.02. Total chlorine grab: 1.81. analyzer: 1.83. Free ammonia: 0.11 Total ammonia: 0.44 Monochloramine: 1.68. Nitrite: 0.003. pH: 8.2. temperature: 6.4 celsius. 10:49 Verified inlet analyzer (mg/l): Free chlorine grab: 0.10 Total chlorine grab: 1.94 Analyzer: 1.97. Recorded readings into PD sheets. Station and equipment: No issues identified. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0019608 | 0 | 0
2026-03 | 2026-03-31 | Richmond Hill Coon's Elevated Tank | CENTRAL | On-site for station check and sampling. W11705550 08:16 Tower level 68% and draining at 93 l/s. 08:25 verified outlet analyzer and collected sample. free chlorine grab: 0.05. Total chlorine grab: 1.89. Analyzer: 1.85. Free ammonia: 0.11. Total ammonia: 0.45. Monochloramine: 1.71. ?Nitrite: 0.003. Temperature: 5.8 celsius. 08:40 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.08. Total chlorine grab: 1.87. Analyzer: 1.88. Recorded data in process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036012 | 0 | 0
2026-03 | 2026-03-02 | Richmond Hill Bloomington Elevated Tank | CENTRAL | Onsite to replace chlorine analyzer reagents. No issues found. | FLAG | stage2_low_confidence | 0.014489 | ML: above threshold (no LLM available) — 0.014 |  | 0.014489 | 0 | 0
2026-03 | 2026-03-25 | Richmond Hill Bloomington Elevated Tank | CENTRAL | On-site for station check and sampling. W11690186 09:29 Tower level 68% and draining at 88 l/s. 09:32 Verified inlet analyzer (mg/l): Free chlorine grab: 0.08 Total chlorine grab: 1.92Analyzer: 1.86. 09:47 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.04. Total chlorine grab: 1.85. analyzer: 1.85. Free ammonia: 0.10 Total ammonia: 0.44 Monochloramine: 1.70 Nitrite: 0.005. Temperature: 5.2 celsius. Recorded readings into PD sheets. Station and equipment: No issues identified. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033065 | 0 | 0
2026-03 | 2026-03-24 | Richmond Hill Bloomington Elevated Tank | CENTRAL | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp tests ET Hi/Low level test Heat trace inspection Ventilation inspection CL17 analyzer maintenance Recirculation pump test Actuated valve inspection Drain valve inspection PRV inspection Performed station housekeeping Station/equipment- Ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.004625 | 0 | 0
2026-03 | 2026-03-04 | Richmond Hill Coon's Elevated Tank | CENTRAL | On-site for station check and sampling. W11637390. 14:11 Tower level 67% and draining at 147 l/s. 14:14 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.95. Analyzer: 1.99. 14:18 verified outlat analyzer and collected sample. free chlorine grab: 0.04. Total chlorine grab: 1.76. Analyzer: 1.74 Ph: 8.03 Free ammonia: 0.06 Total ammonia: 0.38 Monochloramine: 1.65. ?Nitrite: 0.003. Temperature: 4.8 celsius. Recorded data in process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031023 | 0 | 0
2026-03 | 2026-03-02 | Richmond Hill Coon's Elevated Tank | CENTRAL | Onsite to replace chlorine analyzer reagents for both inlet and outlet. No issues found. | FLAG | stage2_low_confidence | 0.013677 | ML: above threshold (no LLM available) — 0.014 |  | 0.013677 | 0 | 0
2026-03 | 2026-03-27 | Richmond Hill Coon's Elevated Tank | CENTRAL | Check altitude valve Installed two new solenoid valves on altitude and had control put back in controlling towe | FLAG | stage2_low_confidence | 0.015363 | ML: above threshold (no LLM available) — 0.015 |  | 0.015363 | 0 | 0
2026-03 | 2026-03-25 | Richmond Hill Coon's Elevated Tank | CENTRAL | On-site for station check and sampling. W11690186 07:00 Tower level 68% and draining at 88 l/s. 07:00 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.90. Analyzer: 1.94. 07:20 verified outlet analyzer and collected sample. free chlorine grab: 0.05. Total chlorine grab: 1.85/1.86/1.84. Analyzer: 1.76. Adjusted analyzer to match grabs. Free ammonia: 0.10. Total ammonia: 0.44. Monochloramine: 1.62. ?Nitrite: 0.004. Temperature: 5.4 celsius. Recorded data in process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044879 | 0 | 0
2026-03 | 2026-03-19 | Richmond Hill Coon's Elevated Tank | CENTRAL | Onsiter to complete work orders: 10:34 notified ROC of work and placed chlorine analyzers in calibration mode. Chlorine analyzer maintenance - ok. 11:18 Verified analyzers: Inlet: 1.78. Analyzer: 1.75. outlet: 1.89. Analyzer: 1.89. Inlet/outlet heat trace inspection - ok. Circulation pump test - ok. chlorine scrubber check - ok. drain valve exercise- ok. JHSC inspection- ok. Actuated valve exercise and inspection: ok. PRV valve inspection: ok 11:27-11:38 triggered Low building temperature alarms of electrical, ammonia, chlorine and valve rooms. ok Ventillation system inspection:ok Site cleaning. No issues found. | FLAG | stage2_low_confidence | 0.014175 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.014175 | 0 | 0
2026-03 | 2026-03-11 | Richmond Hill Coon's Elevated Tank | CENTRAL | On-site for station check and sampling. W11656917. 08:48 Tower level 64% and draining at 83 l/s. 09:00 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.95. Analyzer: 1.99. 09:07 verified outlet analyzer and collected sample. free chlorine grab: 0.02. Total chlorine grab: 1.79. Analyzer: 1.73 Free ammonia: 0.09. Total ammonia: 0.42. Monochloramine: 1.67. ?Nitrite: 0.004. Temperature: 5.4 celsius. Recorded data in process sheets. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036012 | 0 | 0
2026-03 | 2026-03-18 | Richmond Hill Coon's Elevated Tank | CENTRAL | On-site for station check and sampling. W11672825 11:26 Tower level 60% and draining at 92 l/s. 11:33 verified outlet analyzer (mg/l) and collected sample. Free chlorine grab: 0.02. Total chlorine grab: 1.72. Analyzer: 1.73 Free ammonia: 0.13. Total ammonia: 0.45. Monochloramine: 1.62. ?Nitrite: 0.005. Temperature: 4.8 celsius. Ph: 8.01 11:43 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.06. Total chlorine grab: 1.87. Analyzer: 1.91. Work order previously created for Alltitude valve solenoide which is letting some water leak to drain. Recorded data in process sheets. No issues found. | FLAG | stage2_low_confidence | 0.010051 | ML: above threshold (no LLM available) — 0.01 | work order [maintenance_action]; leak [infrastructure] | 0.010051 | 0 | 0
2026-03 | 2026-03-12 | Richmond Hill Pugsley Pumping Station | EAST | Vibration readings | FLAG | stage2_low_confidence | 0.021831 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021831 | 0 | 0
2026-03 | 2026-03-30 | Richmond Hill Pugsley Pumping Station | EAST | On site to complete station check. Time: 12:45 Grab (mg/l) Free: 0.05 Total: 1.50 No outstanding alarms. No OOS equipment. Checked station and trends. | FLAG | stage2_low_confidence | 0.010525 | ML: above threshold (no LLM available) — 0.011 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.010525 | 0 | 0
2026-03 | 2026-03-09 | Richmond Hill Pugsley Pumping Station | EAST | On site for facility station check and equipment verifications Duty is active - 330 L/s, 740 kpa Pumps 2 and 3 running in duty Grab sample from discharge: @13:00 Free: 0.02 mg/L Total: 1.61 mg/L Pump #2 and #3 system inspection and maintenance Reviewed trends, equipment OOS: None Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-06 | Richmond Hill Pugsley Pumping Station | EAST | On site for facility station check and equipment verifications Recorded readings in PWQ sheets Duty is active - Pumps 2 and 3 running in D1, 320 L/s, discharge pressure - 740 kpa Chlorine residual grabs from discharge @14:33 Grab free: 0.03 mg/L Grab total: 1.48 mg/L Reviewed trends Equipment OOS: None Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-02 | Richmond Hill Pugsley Pumping Station | EAST | On site to check station and equipment. P1 and P4 are running in duty 1. 14:50 chlorine residuals grab in mg/l: Total: 1.55 Free: 0.04 Other station readings are in PWQ sheets. Reviewed trends, Station is under normal operation. Generator warning alarm was outstanding from last night. Checked generator, no alarms lit at the control board. Both heaters are on. Able to ack+reset the warning alarm. Equipment OOS: none. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-20 | Richmond Hill Pugsley Pumping Station | EAST | Station Check (no issues found) Input data to PWQ 13:50 Chlorine Grab Residual (mg/l) Free: 0.04, Total 1.58 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054905 | 0 | 0
2026-03 | 2026-03-17 | Richmond Hill Pugsley Pumping Station | EAST | On site for monthly PMs - Informed ROC of work to be completed - Diesel generator test run and hours log Start Hours: 378.9 Start Fuel: 6447 L Pre checks: - Oil Level: Ok - Coolant Level: Ok - Battery cell levels: Ok - Battery Terminals and cables: Ok - Coolant recirc pump: Ok - Fluid Leaks: N/A @10:50 - Started generator: Ran pumps 1 and 4 during test run, to test station under generator power @11:22 - Readings while generator running Current: 196 amps Voltage: 600 V Frequency: 60.0 hz Engine speed: 1798 RPMs Oil pressure: 64 psi Oil temp: 160 F Generator stopped @12:05 Stop hours: 380.2 Stop Fuel: 6507 L No issues with generator run or transfer test - Pump #1 system inspection - Pump #4 system inspection - Flood alarm test @13:45 - Sump pumps inspection / maintenance - Suction valves exercise (Hand valves) - Discharge valve exercise (Hand valve) - Surge valves test - Housekeeping Placed all pumps back to auto Station operation okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; leak [infrastructure] | flood [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-24 | Richmond Hill Pugsley Pumping Station | EAST | Onsite to replace PSL switch on pump #3. Informed ROC and they put the pump #3 in manual off. Replaced the PSL switch and verified calibration. Put it back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | FLAG | stage2_low_confidence | 0.0079491 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0079491 | 0 | 0
2026-03 | 2026-03-19 | Richmond Hill Pugsley Pumping Station | EAST | Assisted Dan B and Ernie H with the surge valve system. They were on site to address the discharge surge valves electrical panel not working. When they tested the surge valves on discharge, valve #1 got stuck open Got to site with Jack P and we adjusted the needle valve for the close speed, and serviced the valve, flushed the strainer. The valve opened and closed okay. Tested multiple times, surge system is back to normal. | FLAG | stage2_low_confidence | 0.070209 | ML: above threshold (no LLM available) — 0.07 | not working [equipment_failure] | 0.070209 | 0 | 0
2026-03 | 2026-03-18 | Richmond Hill Pugsley Pumping Station | EAST | On site to remove surge tank sump pumps as requested. | FLAG | stage2_low_confidence | 0.013285 | ML: above threshold (no LLM available) — 0.013 |  | 0.013285 | 0 | 0
2026-03 | 2026-03-16 | Richmond Hill Pugsley Pumping Station | EAST | On site for facility station check and equipment verifications Duty is active - RHRSWA Level -76% Flow: 390 L/s, Discharge pressure: 757 kpa Recorded station readings in PWQ sheets Grab sample from discharge (mg/L) Free: 0.02 Total: 1.58 Reviewed trends, equipment OOS: None Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-06 | Richmond Hill Pugsley Pumping Station | EAST | On site to investigate surge receiving tank pump system.Investigate and found pump shorted to ground. Also found incorrect system logic with drain line motorized actuator valve and PLC programming. Will write a report and see if we can get that changed. Will need to return to replace pump. | FLAG | stage2_low_confidence | 0.039619 | ML: above threshold (no LLM available) — 0.04 |  | 0.039619 | 0 | 0
2026-03 | 2026-03-19 | Richmond Hill Pugsley Pumping Station | EAST | On site to respond to work order reporting discharge header surge relief valve system not working during recent test. Found batteries needing replacement. Replaced batteries and tested. Found upper surge relief valve sticking open. Ops cleaned y strainer and adjusted close speed pilot. Valve working well now. | FLAG | stage2_low_confidence | 0.14022 | ML: above threshold (no LLM available) — 0.14 | not working [equipment_failure]; work order [maintenance_action] | 0.14022 | 0 | 0
2026-03 | 2026-03-23 | Richmond Hill Pugsley Pumping Station | EAST | On site for station check and equipment verifications Readings in PWQ sheets Grab residuals from discharge @14:50 Free: 0.07 Total: 1.50 Reviewed trends Station operation normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003398 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | - on site to finish station check and collect weekly bacti W11705704 - Jen Silva collected highlift sample at 11:20 - analyzer: 3.45mg/l grab: 3.50mg/l - free grab: 0.06mg/l - all other analyzer verification in PWQ -reagents all ok -topped up KMnO4 tank 1 16 -81cm -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070985 | 0 | 0
2026-03 | 2026-03-30 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | - on site to repsond to highlift ntu fault, filter 3 Ntu alarm and UV minor faults - UV minor faults caused by power blip 28/03/2026 at 06:56 - reset alarms - turned plant off and cleaned NTU analyzers and adjust flows -topped up KMnO4 tank 2 16cm - 81cm -received post filter low chlorine alarms - verified at 14:10: 1.75mg/l grab; 1.79mg/l -checked chlorine system: all ok - adjust chlorinator 1 dosage factor 144% to 148% - on call operator | FLAG | stage2_low_confidence | 0.043307 | ML: above threshold (no LLM available) — 0.043 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.043307 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | - on site for cylinder change 53kg - 121kg | FLAG | stage2_low_confidence | 0.0095244 | ML: above threshold (no LLM available) — 0.01 |  | 0.0095244 | 0 | 0
2026-03 | 2026-03-28 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Respond to UVT Transmittance Fault, OOR alarms. UVT sensor has low flow alarm active, started unit again to monitor. Triggered UVT sample flow warning again and interlocked filters on UVT Transmittance fault. Appears to be ample sample flow to analyzer (less flow / pressure on startup of plant). Sample flow warning on 30 second delay, but warning triggers SCADA fault alarm and interlocks plant. Changed UVT ?flow alarm output? setting from YES to NO temporarily to start up plant. Changed low flow warning delay from 30s to 0s - this disables flow warning and should prevent UVT fault on plant startup due to ?low sample flow? Monitored startup, no issues. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-28 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | UV interlocked due to power failure. System appears to have shutdown normally. UV dose less than 40mj/cm2 while filter discharge flow registered for approximately 1 minute. Within compliance. | FLAG | stage2_low_confidence | 0.021442 | ML: above threshold (no LLM available) — 0.021 | failure [equipment_failure]; compliance [regulatory] | 0.021442 | 0 | 0
2026-03 | 2026-03-11 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to collect weekly bact samples from raw and treated sample taps (W11657095). @09:30 tested treated chlorine residuals via hach field kit. Free: 0.04 mg/L Total: 3.66 mg/L Entered readings into PWQ sheet. Switched reservoir valving to north cell. | FLAG | stage2_low_confidence | 0.007417 | ML: above threshold (no LLM available) — 0.007 |  | 0.007417 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to collect weekly bact (W11705704) and iron (W11664712) samples. Completed in house lab and entered readings into PWQ sheet. Treated free grab: 0.06 mg/L Treated total grab: 3.50 mg/L | FLAG | stage2_low_confidence | 0.01151 | ML: above threshold (no LLM available) — 0.012 |  | 0.01151 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Respond to site to reset tripped OOS equipment due to power failure during storm event. Reset compressor 1, 2 (E0821 short circuit) Reset HLP1 (9 undervoltage) Reset HLP5 fire pump (phase reversal) UV system appears to have interlocked normally at 0224. Filter discharge flow registered for less than one minute during shutdown when UV dose below 40mj/cm2. Offsite 0347 during start up, responding to HLETYS comm, power failure | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; fire [critical]; failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; short circuit [equipment_failure] | sso [critical]; fire [critical]; failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; short circuit [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-04 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to collect weekly bact samples from raw and treated sample taps (w11637544). Collected MET samples (W11637705). Treated grab residual @ 08:53 Free: 0.04 mg/L Total: 3.71 mg/L Completed in house lab analyses and entered readings into PWQ sheet. | FLAG | stage2_low_confidence | 0.0073699 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073699 | 0 | 0
2026-03 | 2026-03-05 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | onsite to perfom the following WOs: - Filter turbidity analyzers - Finished water turbidity analyzer - Switched chlorinator duties, placed chlorinator 4 in lead duty and chlorinator 2 in off/ standby Reviewed Scada, duty active, deactivated duty ~ Dave T Notified ROC before and after completion of WOs - Did chlorine cylinder change with DT, tested for vacuum switch and tested leak no issues. Dave T activated duty after completion of WOs monitored station operation before leaving site no issues | FLAG | stage2_low_confidence | 0.018626 | ML: above threshold (no LLM available) — 0.019 | scada [control_system]; leak [infrastructure] | 0.018626 | 0 | 0
2026-03 | 2026-03-13 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site responding to turbidity fault. Cleaned turbidimeter all seems okay. Checked UVT analyzer all ok. No new issues on site | FLAG | stage2_low_confidence | 0.020289 | ML: above threshold (no LLM available) — 0.02 | fault [equipment_failure] | 0.020289 | 0 | 0
2026-03 | 2026-03-15 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to top up permangenate tanks 1 and 2 from 12/13-77/78cm | FLAG | stage2_low_confidence | 0.010523 | ML: above threshold (no LLM available) — 0.011 |  | 0.010523 | 0 | 0
2026-03 | 2026-03-12 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to complete monthly work orders including UV sensor check, well 2 valve exercising, prv inspection, compressor inspection and low temp alarm. | FLAG | stage2_low_confidence | 0.051731 | ML: above threshold (no LLM available) — 0.052 | sso [critical]; work order [maintenance_action]; alarm [control_system] | 0.051731 | 0 | 0
2026-03 | 2026-03-02 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to inspect facility and complete in house lab analysis. Entered readings into PWQ sheet - no issues on site. | FLAG | stage2_low_confidence | 0.01772 | ML: above threshold (no LLM available) — 0.018 |  | 0.01772 | 0 | 0
2026-03 | 2026-03-10 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -on site to reset high lift pump 4 fault -topped up kmno4 tank 1 16- 81cm | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-10 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -on site to meet Honeywell at SHW2 for hydro meter replacement -placed well in man/off and put SHW3 in auto -no issues - station back to normal | FLAG | stage2_low_confidence | 0.010554 | ML: above threshold (no LLM available) — 0.011 |  | 0.010554 | 0 | 0
2026-03 | 2026-02-23 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Review facility and trending for UV event occurring February 23 1533. Plant appears to have interlocked and shut down normally due to a power blip. UV dose registered below 40mj/cm2 for less than 30 seconds while filter discharge flow registered flow during shutdown. No issues. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054212 | 0 | 0
2026-03 | 2026-03-09 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | All trends checked and ok, all equipment checked and ok All measurements are in mg/l Highlights - 10:00 am Total grab 3.48 vs analyzer 3.52 Free grab 0.08 Monochloramine 2.98 Post filter - 10:20 am Total grab 2.09 vs 2.15 analyzer Free 0.04 Reservoir - 10:40 am Total grab 3.59 vs analyzer 3.69 Free grab 0.05 Monochloramine 3.26 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0017555 | 0 | 0
2026-03 | 2026-03-06 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to inspect facility. Completed in house lab analysis. Entered readings into PWA. Changed post filtration chlorine analyzer reagents. | FLAG | stage2_low_confidence | 0.019802 | ML: above threshold (no LLM available) — 0.02 |  | 0.019802 | 0 | 0
2026-03 | 2026-03-07 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -power blip caused UV minor fault alarms, plant was off at the time -reset alarms -no further issues | FLAG | stage2_low_confidence | 0.011216 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011216 | 0 | 0
2026-03 | 2026-03-24 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to work with operations, PCS and manufacturer's site technician to remove, replace and test new ultraviolet transmittance instrument panel. | FLAG | stage2_low_confidence | 0.020408 | ML: above threshold (no LLM available) — 0.02 |  | 0.020408 | 0 | 0
2026-03 | 2026-03-24 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to complete monthly work orders including: -Surve tank isolation valve exercise -transfer pumps inspection -PRV inspection -scrubber inspection -transfer pump air relief valve inspection No issues on site. | FLAG | stage2_low_confidence | 0.013643 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action] | 0.013643 | 0 | 0
2026-03 | 2026-03-18 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -on site to investigate filter 3 NTU trend -no issues with unit - cleaned -placed back into service | FLAG | stage2_low_confidence | 0.0086882 | ML: above threshold (no LLM available) — 0.009 |  | 0.0086882 | 0 | 0
2026-03 | 2026-03-19 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to complete monthly preventative maintenance work orders including: -health and safety inspection -high lift pumps inspection -high lift actuated valves inspection -changed chlorine cylinder bank 2 | FLAG | stage2_low_confidence | 0.017234 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action] | 0.017234 | 0 | 0
2026-03 | 2026-03-20 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to inspect facility. Completed in house lab analysis. Entered readings into PWQ sheet. Topped up KMNO4 tank 1. Tested chlorine residuals via hach field kit. High lift total analyzer: 3.61 mg/L High lift total chlorine grab: 3.69 mg/L Free grab: 0.04 mg/L | FLAG | stage2_low_confidence | 0.012664 | ML: above threshold (no LLM available) — 0.013 |  | 0.012664 | 0 | 0
2026-03 | 2026-03-23 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site responding to reservoir total chlorine lolo alarm. Replaced damaged tubing barb and primed unit. Completed station check and lab analyses. Entered readings into PWQ sheet. Changed post filter chlorine analyzer reagents - found unit leaking and created follow up work order. Station operation normal, no issues on site. | FLAG | stage2_low_confidence | 0.14659 | ML: above threshold (no LLM available) — 0.147 | work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] | 0.14659 | 0 | 0
2026-03 | 2026-03-18 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to collect weekly bact samples from raw and treated sample taps (W11672923). Tested chlorine residuals via hach field kit. Free: 0.06 mg/L Total: 3.60 mg/L Analyzer: 3.58 mg/L Entered readings into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062013 | 0 | 0
2026-03 | 2026-03-26 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to complete annual Chlorine system overhaul (regulators, ejectors, pigtails, manifold, tubing, fittings). Replaced / rebuilt all of the above. Switched vacuum gauges for chlorinators 1 and 2 to pull from chlorinator instead of ejector heads. Adjusted chlorinator 1 and 2 vacuum gauge low range alarms to match operating vacuum from chlorinators. Vacuum tested system and tested regulator switch over. Chlorinators all holding at or above -800mmHg. Placed SHTP back in service and monitored, no issues. SHETCS duty 1 start / stop returned to 15/45%. | FLAG | stage2_low_confidence | 0.036871 | ML: above threshold (no LLM available) — 0.037 | alarm [control_system]; alarms [control_system] | 0.036871 | 0 | 0
2026-03 | 2026-03-05 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -on site to respond to filter 3 repeatedly triggering post rinse ntu high alarm -initiated rinse, turbidity reading 0.38 -replaced turbidimeter vial, turbidity decreased to 0.287 -filter 3 back in service | FLAG | stage2_low_confidence | 0.012926 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.012926 | 0 | 0
2026-03 | 2026-03-10 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-10 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-05 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -on site to complete work orders -informed ROC of work -completed cylinder change -completed Check Valves Inspection, Schomberg WTP W3&4 -completed Pump and Motor Inspection, Schomberg WTP W3&4 -completed Exhaust Fan Inspection, Schomberg WTP W3&4 -completed Dehumidifier Inspection, Schomberg WTP W3&4 -completed Electric Actuated Valves Inspection, Schomberg WTP W3&4 -completed Fire Pumps and Motors, Inspection -completed Backwash Sump Tank System, Inspection -completed Low/High Temperature Alarm, Test -rotated chlorinator 4 duty into post UV dosing and tested | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; work order [maintenance_action]; alarm [control_system] | fire [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-25 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to complete monthly work orders including: -Surve tank isolation valve exercise -transfer pumps inspection - | FLAG | stage2_low_confidence | 0.018201 | ML: above threshold (no LLM available) — 0.018 | work order [maintenance_action] | 0.018201 | 0 | 0
2026-03 | 2026-03-16 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | -on site for station check, water quality lab -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -highlift 09:55: 3.70mg/l grab: 3.74mg/l -free cl grab: 0.05mg/l -post filter 10:05: 2.22mg/l grab: 2.20mg/l -reservoir 10:15: 3.05mg/l grab: 3.06mg/l -all reagents ok -switch to south cell - swapped sample lines -cleaned highlight NTU - flushed NTU sample line - caused highlift chlorine analyzer to spike to 4.15mg/l 09:50 - took total chlorine grab: 3.74mg/l - not adverse -reset UV minor faults -isolated reactor to investigate the failed sensor issue -sleeves all out but found water in sensor rod 2/3 -informed team lead -restarted plant: all ok -cleaned NTU analyzer filter 3 | FLAG | stage2_low_confidence | 0.01393 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; failed [equipment_failure] | 0.01393 | 0 | 0
2026-03 | 2026-03-16 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to replace halogen system battery, replace Rotork batteries, replace VFD air filters, and infrared scan electrical equipment. | FLAG | stage2_low_confidence | 0.019152 | ML: above threshold (no LLM available) — 0.019 |  | 0.019152 | 0 | 0
2026-03 | 2026-03-27 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to complete station check. Entered readings into PWQ sheet. Verified online chlorine analyzers. Completed in house lab. | FLAG | stage2_low_confidence | 0.018544 | ML: above threshold (no LLM available) — 0.019 |  | 0.018544 | 0 | 0
2026-03 | 2026-03-03 | Schomberg Water Treatment Plant & Wells 2-4 | WEST | On site to complete monthly preventative maintenance work orders. Changed tubing elements in both reservoir analyzer sample pumps. Completed chlorine chemical system check. Performed chlorine analyzer maintenance. Completed monthly diesel generator test run. Start hours: 543.1 Stop hours: 544.5 Fuel used: 8 L | FLAG | stage2_low_confidence | 0.033588 | ML: above threshold (no LLM available) — 0.034 | work order [maintenance_action] | 0.033588 | 0 | 0
2026-03 | 2026-03-31 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Rechlore building Attended Cl2 leak alarm No leak identified, reset halogen system and alarms, restarted cl2 gas dosing system, monitored site from scada for any gas buid up. everything look normal. Reservoir:- On site to complete station check, operational sample and collect weekly bacti W11705742 Checked trends: all ok 13:10-Took sample and chlorine grab from cell 1 (North) Free Cl2: 0.06mg/L Total Cl2: 2.07mg/L 13:15- cell 2 grab(East) Free Cl2: 0.08mg/L Total Cl2: 2.08mg/L 13:17-Cell 3 grab (West) Free Cl2: 0.04 mg/L Total Cl2: 2.13mg/L Entered reading in PWQ: all ok Equipment Okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-03 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to change cylinder | FLAG | stage2_low_confidence | 0.011689 | ML: above threshold (no LLM available) — 0.012 |  | 0.011689 | 0 | 0
2026-03 | 2026-03-30 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Station check Check Trends: All okay 13:30-Verified pre- injection Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.06 mg/L Grab Total Cl2- 1.55mg/L; Analyzer- 1.48 mg/L 13:50-Verified post- injection Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.54mg/L (Avg-2.52,2.54,2.58); Analyzer- 2.15 mg/L Adjusted analyzer up to 2.30 mg/L Reagents all good Verified Chem Scan- All okay Reagent all good entered values in PWQ sheet Topped up ammonia tank 1- 15.20 cm -to 75.46 cm equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056316 | 0 | 0
2026-03 | 2026-03-11 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Reservoir:- On site to complete station and collect weekly bacti W11657067 Checked trends: all ok Took sample and chlorine grab north cell 10:25 Free Cl2: 0.05mg/L Total Cl2: 2.05mg/L South cell grab - 10:29 Free Cl2: 0.03mg/L Total Cl2: 2.09mg/L West cell grab- 10:33 Free Cl2: 0.02mg/L Total Cl2: 2.12mg/L Entered reading in PWQ: all ok Equipment Okay Rechloramination:- On site for Station check Check Trends: All okay 11:05-Verified pre- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.55mg/L; Analyzer- 1.49 mg/L 11:12-Verified post- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.19mg/L; Analyzer- 2.21 mg/L Reagents all good Verified Chem Scan- All okay topped up grey and green Reagents Topped up Ammonia tank 1 :15.03 cm- 75.22 cm entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0017936 | 0 | 0
2026-03 | 2026-03-13 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Station check Check Trends: All okay 10:40-Verified pre- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.50mg/L; Analyzer- 1.46 mg/L 10:50-Verified post- injection Analyzer Grab Free CL2-0.08mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.24mg/L; Analyzer- 2.24 mg/L Reagents all good Verified Chem Scan- All okay topped up DI water entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005036 | 0 | 0
2026-03 | 2026-03-04 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to complete station and collect weekly bacti W11637582 -checked trends: all ok -entered reading in PWQ: all ok -took sample and chlorine grab north cell 10:15 -free cl: 0.06/l -total cl: 2.01mg/l -west cell grab 10:15 -free cl: 0.08mg/l -total cl: 2.13mg/l -south cell grab 10:20 -free cl: 0.07mg/l -total cl: 2.10mg/l -complete re chlorine building station check -checked trends: all ok -entered reading in PWQ: -verified pre analyzer 11:50 -analyzer free: 0.07mg/l grab: 0.10mg/l -analyzer total: 1.53mg/l grab: 1.52mg/l -reagents all ok -verified post analyzer 12:00 -analyzer free: 0.05mg/l grab: -analyzer total: 1.60mg/l grab: 1.67mg/l - adjusted -reagents all ok -chemscan verified -reagents all ok -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0018001 | 0 | 0
2026-03 | 2026-03-02 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Station check Check Trends: All okay 13:25-Verified pre- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.06 mg/L Grab Total Cl2- 1.55mg/L; Analyzer- 1.50 mg/L 13:30-Verified post- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.13mg/L; Analyzer- 2.15 mg/L Reagents all good Topped up Ammonia Tank 1- 15.04 cm to 75.31 cm entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060165 | 0 | 0
2026-03 | 2026-03-09 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Station check Check Trends: All okay 11:55-Verified pre- injection Analyzer Grab Free CL2-0.01mg/L; Analyzer- 0.06 mg/L Grab Total Cl2- 1.54mg/L; Analyzer- 1.51 mg/L 11:55-Verified post- injection Analyzer Grab Free CL2-0.03mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 2.24mg/L; Analyzer- 2.20 mg/L Reagents all good Verified Chem Scan- All okay topped up grey and green Reagents Topped up Ammonia tank 2 :15.04 cm- 75.52 cm entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055516 | 0 | 0
2026-03 | 2026-03-10 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Reset sump pump power failure trip for Rechlor building and sanitary sump pit at pumping station. Receive chlorine cylinder delivery. No issues. | FLAG | stage2_low_confidence | 0.023496 | ML: above threshold (no LLM available) — 0.023 | failure [equipment_failure]; trip [equipment_failure] | 0.023496 | 0 | 0
2026-03 | 2026-03-27 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Station check Check Trends: All okay 12:45-Verified pre- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.42mg/L; Analyzer- 1.46 mg/L 12:52-Verified post- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.08 mg/L Grab Total Cl2- 2.19mg/L; Analyzer- 2.16 mg/L Reagents all good Verified Chem Scan- All okay Reagent all good entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049998 | 0 | 0
2026-03 | 2026-03-23 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Station Check (no issues found) Input data to PWQ Verified Depoloxs (mg/L) 9:25 PRE: Free: Grab 0.04, A 0.07 Total: Grab 1.53, A 1.50 9:35 POST: Free: Grab 0.05, A 0.08 Total: Grab 2.32, A 2.27 Chemscan: (topped up distilled, distilled/muratic) Depolox: (topped up acetate for both) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0028742 | 0 | 0
2026-03 | 2026-03-16 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Station check Check Trends: All okay 11:05-Verified pre- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.48mg/L; Analyzer- 1.42 mg/L 11:13-Verified post- injection Analyzer Grab Free CL2-0.05mg/L; Analyzer- 0.08 mg/L Grab Total Cl2- 2.06mg/L; Analyzer- 2.04 mg/L Reagents all good Verified Chem Scan Post inj FNH3 Grab- 0.12 mg/L Post inj FNH3 Analyzer- 0.07 mg/L Adjusted Post Inj FNH3 slope from 0.04 to 0.06 New Post inj FNH3 analyzer reading- 0.09 mg/L Reagents all good. entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048151 | 0 | 0
2026-03 | 2026-03-20 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Station check Check Trends: All okay Topped up Ammonia Tank 1- 15.23 cm to 75.48 cm 11:20-Verified pre- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.08 mg/L Grab Total Cl2- 1.80mg/L; Analyzer- 1.88 mg/L 11:40-Verified post- injection Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.30mg/L; Analyzer- 2.34 mg/L Reagents all good Verified Chem Scan- All okay topped up grey Reagent entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053163 | 0 | 0
2026-03 | 2026-03-25 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Reservoir:- On site to complete station check and collect weekly bacti W11690336 Checked trends: all ok 11:38-Took sample and chlorine grab from cell 1 (North) Free Cl2: 0.04mg/L Total Cl2: 2.16mg/L 11:40- cell 2 grab(East) Free Cl2: 0.03mg/L Total Cl2: 2.14mg/L 11:45-Cell 3 grab (West) Free Cl2: 0.03 mg/L Total Cl2: 2.15mg/L Entered reading in PWQ: all ok Equipment Okay Rechloramination:- On site for Station check Check Trends: All okay 12:42-Verified pre- injection Analyzer Grab Free CL2-0.03mg/L; Analyzer- 0.08 mg/L Grab Total Cl2- 1.92 mg/L; Analyzer- 1.87 mg/L 13:10-Verified post- injection Analyzer Grab Free CL2-0.05mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 2.18mg/L; Analyzer- 2.16 mg/L Reagents all good Verified Chem Scan- All okay Reagents all good entered values in PWQ sheet Topped up ammonia tank 2- 15.07 cm to 75 cm equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.001824 | 0 | 0
2026-03 | 2026-03-31 | Woodbridge East Booster Pumping Station | WEST | -on site to complete following work orders -adjusted san marko van 54psi to 48psi -placed metro valve and pumps back into auto - tested flood alarm: all ok -tested sump pit: all ok -hoist inspection: all ok -heating inspection: all ok -check valve inspection: all ok -dehumidifier check: all ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Onsite responding to multiple alarms due to power blip CMU5 W11702361 Reset halogen system to get chloramination chemical system up and running reservoir at beginning of fill cycle Silenced diesel fuel tank outdoor alarm (very loud outdoors can hear from outside of the gate) Silenced generator diesel pump panel inside generator room Reset PD8 pump 2 soft starter fault -control volt low fault- ZC voltage lost- Had RO Connor turn BVPS pumps off until I was able to reset chlorine and ammonia systems. | FLAG | stage2_low_confidence | 0.051473 | ML: above threshold (no LLM available) — 0.051 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.051473 | 0 | 0
2026-03 | 2026-03-06 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Station check Check Trends: All okay 11:45-Verified pre- injection Analyzer Grab Free CL2-0.03mg/L; Analyzer- 0.06 mg/L Grab Total Cl2- 1.48mg/L; Analyzer- 1.44 mg/L 11:55-Verified post- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.30mg/L; Analyzer- 2.24 mg/L Reagents all good Verified Chem Scan- All okay Reagents all good entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050264 | 0 | 0
2026-03 | 2026-03-17 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | On site for Scheduled PM workorders, Informed ROC about the works being done. W11631734 RHRSTR, Separation Valve Exercise, South Richmond Hill RES (3M) W11631751 RHRSTR, West and East Hatch Clean Up, South Richmond Hill RES (3M) W11632526 RHRSTR, External Venting Screens Inspection, South Richmond Hill RES (6M) W11632026 RHRSTR, JHSC Health and Safety Inspection, East Vaughan BPS, South Richmond Hill RES | FLAG | stage2_low_confidence | 0.026625 | ML: above threshold (no LLM available) — 0.027 |  | 0.026625 | 0 | 0
2026-03 | 2026-03-18 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | Reservoir:- On site to complete station and collect weekly bacti W11672961 Checked trends: all ok 11:43-Took sample and chlorine grab north cell Free Cl2: 0.06mg/L Total Cl2: 1.98mg/L 11:45- cell 2 grab Free Cl2: 0.02mg/L Total Cl2: 2.15mg/L 11:50-Cell 3 grab Free Cl2: 0.04mg/L Total Cl2: 2.15mg/L Entered reading in PWQ: all ok Equipment Okay Rechloramination:- On site for Station check Check Trends: All okay 12:50-Verified pre- injection Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.56mg/L; Analyzer- 1.53 mg/L 13:09-Verified post- injection Analyzer Grab Free CL2-0.05mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.57mg/L; Analyzer- 2.53 mg/L Reagents all good Verified Chem Scan- All okay Reagents all good entered values in PWQ sheet equipment okay. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0015666 | 0 | 0
2026-03 | 2026-03-17 | South Richmond Hill Teston Reservoir & Rechlorination Facility | WEST | -on site to complete work orders -informed ROC of work -completed Chemscan Analyzer Maintenance -completed manual clean and manual zero 230 = 2571 248 = 3537 Min = -0.0016 Max = 0.0022 -completed Ammonia Peristaltic Pump Inspection 1200 hour service -replaced both pump elements -completed drawdowns on pumps: Pump #1 max flow = 433 ml/min Pump #2 max flow = 433 ml/min -completed Ammonia Feed and Storage Inspection -completed Chlorine Scrubber Inspection -completed Chlorine Leak Detector Test -completed Chlorine System Inspection -ran ejectors to waste and completed vacuum test -no issues -completed chlorine cylinder change -received ammonia delivery -completed Chlorine Analyzer Maintenance -checked electrolyte and grit sand -verified sample flows -verified analyzers after maintenance: 13:08 - pre-injection Analyzer readings: Free Chlorine = 0.08 mg/L Total Chlorine = 1.72 mg/L 13:08 - pre-injection Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.77 mg/L 13:18 - post-injection Analyzer readings: Free Chlorine = 0.09 mg/L Total Chlorine = 1.88 mg/L 13:18 - post-injection Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 1.85 mg/L -duty active, tested all chemical systems in auto -no issues, site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; leak [infrastructure] | work order [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-02 | Woodbridge East Booster Pumping Station | WEST | -on site to complete station check -system duty not active, activated duty for station check -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:01 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.47 mg/L 11:01 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.52 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054148 | 0 | 0
2026-03 | 2026-03-09 | Woodbridge East Booster Pumping Station | WEST | -on site to complete station check -system duty active, pump 1 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:29 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.55 mg/L 11:29 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.57 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048996 | 0 | 0
2026-03 | 2026-03-23 | Woodbridge East Booster Pumping Station | WEST | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 10:30 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.45 mg/L 10:30 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.50 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004633 | 0 | 0
2026-03 | 2026-03-13 | Woodbridge East Booster Pumping Station | WEST | Station Check (no issues found) Input data to PWQ 13:15 Verified Depolox (mg/L) Free: Grab 0.05, A 0.04 Total: Grab 1.65, A 1.60 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050566 | 0 | 0
2026-03 | 2026-03-20 | Woodbridge East Booster Pumping Station | WEST | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:49 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.57 mg/L 11:49 - Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 1.59 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045467 | 0 | 0
2026-03 | 2026-03-27 | Woodbridge East Booster Pumping Station | WEST | -on site for station check -checked trends: all ok -entered reading in PWQ: -verified analyzer 10:00 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 1.29mg/l grab: 1.37mg/l - adjusted -place station valve local close due to weekend isolation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069183 | 0 | 0
2026-03 | 2026-03-16 | Woodbridge East Booster Pumping Station | WEST | -on site to complete station check -system duty active, pump 1 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:54 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.55 mg/L 11:54 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.56 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048996 | 0 | 0
2026-03 | 2026-03-19 | Woodbridge East Booster Pumping Station | WEST | -on site to complete work orders -informed ROC of work -completed Manual Valve, Exercise -completed Low Temperature Alarm, Test -completed Sump Pit System, Inspection -completed Flood Alarm, Test -completed Siemens Depolox 5 Maintenance -checked electrolyte and grit sand -verified flow -verified analyzers after maintenance: 11:31 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.53 mg/L 11:31 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.52 mg/L -completed Motorized Valve Actuator Inspection & Exercise -completed JHSC Health and Safety Inspection -completed Pump & Motor, Inspection -no issues, site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | Woodbridge East Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 65 % -checked equipment -reviewed trends 11:25 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.71 mg/L 11:29 - collected weekly regulatory micro. sample - W/O # W11706785 SL1000 readings: MCL = 1.64 mg/L TNH3 = 0.39 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 7.1 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0030506 | 0 | 0
2026-03 | 2026-03-06 | Woodbridge East Booster Pumping Station | WEST | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 13:04 - Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.40 mg/L 13:04 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.49/1.49/1.49 mg/L 13:14 - adjusted total chlorine analyzer to 1.49 mg/L based on average of 3 grabs -no other issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059756 | 0 | 0
2026-03 | 2026-03-19 | Woodbridge East Elevated Tank | WEST | -on site to complete work orders -informed ROC of work -completed Manual Valve, Exercise -completed Actuated Valve, Exercise & Inspection -completed Portable Gasoline Generator, Test -transferred site to generator power, no issues -completed Sump Pit System, Inspection -tested flood alarm -completed Low Temperature Alarm, Test -completed Dehumidifier, Inspection & Cleaning -completed JHSC Health and Safety Inspection -no issues, site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-25 | Woodbridge East Elevated Tank | WEST | -adjust high level alarm 82-75% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0046796 | 0 | 0
2026-03 | 2026-03-25 | Woodbridge East Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower filling due to San Marco valve work, tower = 58 % -checked equipment -reviewed trends 11:27 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.89 mg/L 11:30 - collected weekly regulatory micro. sample - W/O # W11690893 SL1000 readings: MCL = 1.79 mg/L TNH3 = 0.41 mg/L FNH3 = 0.06 mg/L NO2 = 0.006 mg/L -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0040126 | 0 | 0
2026-03 | 2026-03-25 | Woodbridge East Elevated Tank | WEST | -adjusted PRV at chancellor and San Marko at 09:45 am -48- 55psi -tower began to fill at 60l/s at 52% 09:45 - tower filling at 10l/s at 66% at 15:15 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035901 | 0 | 0
2026-03 | 2026-03-04 | Woodbridge East Elevated Tank | WEST | -On-site to complete station check and collect samples -system duty not active, tower = 73 % -checked equipment -reviewed trends 11:59 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.67 mg/L 12:03 - collected weekly regulatory micro. sample - W/O # W11638725 SL1000 readings: MCL = 1.54 mg/L TNH3 = 0.36 mg/L FNH3 = 0.05 mg/L NO2 = 0.003 mg/L temp = 6.8 C -collected operational ATP and phosphorus samples -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.003051 | 0 | 0
2026-03 | 2026-03-11 | Woodbridge East Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 78 % -checked equipment -reviewed trends 10:27 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.69 mg/L 10:31 - collected weekly regulatory micro. sample - W/O # W11657772 SL1000 readings: MCL = 1.54 mg/L TNH3 = 0.36 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 6.9 C -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0029334 | 0 | 0
2026-03 | 2026-03-31 | Woodbridge West Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 80 % -checked equipment -reviewed trends 10:43 - collected grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 1.47 mg/L 10:47 - collected weekly regulatory micro. sample - W/O # W11706785 SL1000 readings: MCL = 1.29 mg/L TNH3 = 0.31 mg/L FNH3 = 0.06 mg/L NO2 = 0.003 mg/L temp = 7.5 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.003045 | 0 | 0
2026-03 | 2026-03-18 | Woodbridge East Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 77 % -checked equipment -reviewed trends 11:02 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.67 mg/L 11:07 - collected weekly regulatory micro. sample - W/O # W11673653 SL1000 readings: MCL = 1.55 mg/L TNH3 = 0.36 mg/L FNH3 = 0.05 mg/L NO2 = 0.004 mg/L temp = 6.0 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.003045 | 0 | 0
2026-03 | 2026-03-04 | Woodbridge West Elevated Tank | WEST | -On-site to complete station check and collect samples -deactivated system duty, tower = 64% -checked equipment -reviewed trends 11:05 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.48 mg/L 11:09 - collected weekly regulatory micro. sample - W/O # W11638725 SL1000 readings: MCL = 1.30 mg/L TNH3 = 0.30 mg/L FNH3 = 0.04 mg/L NO2 = 0.004 mg/L temp = 4.4 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0030303 | 0 | 0
2026-03 | 2026-03-11 | Woodbridge West Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 52% -checked equipment -reviewed trends 09:51 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.41 mg/L 09:55 - collected weekly regulatory micro. sample - W/O # W11657772 SL1000 readings: MCL = 1.21 mg/L TNH3 = 0.30 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 6.2 C -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0029135 | 0 | 0
2026-03 | 2026-03-24 | Woodbridge West Elevated Tank | WEST | -on site to complete work orders -informed ROC of work -completed Sensing Line Heat Trace System, Inspection -completed Low Temperature Alarm, Test -completed Sump Pit System Inspection -completed Flood Alarm Test -completed Air Valve Inspection -completed Manual Valve, Exercise -completed JHSC Health and Safety Inspection -completed High & Low Water Level Alarm, Test -completed Actuated Valve, Exercise -completed Portable Gasoline Generator, Test -transferred PAC power to portable generator -no issues -site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | Woodbridge West Elevated Tank | WEST | -On-site to complete station check and collect sample -system duty not active, tower = 74 % -checked equipment -reviewed trends 10:20 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.47 mg/L 10:24 - collected weekly regulatory micro. sample - W/O # W11673653 SL1000 readings: MCL = 1.29 mg/L TNH3 = 0.30 mg/L FNH3 = 0.05 mg/L NO2 = 0.003 mg/L temp = 5.6 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0030506 | 0 | 0
2026-03 | 2026-03-25 | Woodbridge West Elevated Tank | WEST | -On-site to complete station check and collect sample -deactivated system duty, tower = 58 % -checked equipment -reviewed trends 10:50 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.45 mg/L 10:54 - collected weekly regulatory micro. sample - W/O # W11690893 SL1000 readings: MCL = 1.28 mg/L TNH3 = 0.31 mg/L FNH3 = 0.05 mg/L NO2 = 0.005 mg/L -recorded readings in PWQ sheet -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0032735 | 0 | 0
2026-03 | 2026-03-29 | Nobleton Water Resource Recovery Facility | WW-WEST | Onsite to add soda ash to aeration tanks. added 2 bags of soda ash per train | FLAG | stage2_low_confidence | 0.0084642 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084642 | 0 | 0
2026-03 | 2026-03-30 | Nobleton Water Resource Recovery Facility | WW-WEST | Received call from ROC for Mech. bar screen OOS alarm. (ongoing issue) Arrived onsite at 3:15am, Inlet channel hi level alarm present due to channel backing up. Reset bar screen and cleared alarms. Bar screen running operationally with no issues found - will continue to monitor. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | Nobleton Water Resource Recovery Facility | WW-WEST | Received bar screen alarm. Upon inspection, the screen faulted in the lower position as it was pulling up rags. Small chunk of rags built up. Changed barscreen start level setpoint from 150 mm to 140 mm to clear rags before large buildup occurs. Will create a work order if the issue occurs again overnight. | FLAG | stage2_low_confidence | 0.058571 | ML: above threshold (no LLM available) — 0.059 | fault [equipment_failure]; faulted [equipment_failure]; work order [maintenance_action]; alarm [control_system] | 0.058571 | 0 | 0
2026-03 | 2026-03-30 | Nobleton Water Resource Recovery Facility | WW-WEST | - GFL on site to take a load of sludge. - Transferred sludge from the thickening tank to the holding tank - Enabled RAS batch wasting mode at 9:15. Wasted 18 m^3 from train 1 and 18 m^3 from train 2 then reset RAS batch wasting mode once done - Performed inhouse lab and recorded readings on SharePoint. No new issues - Added 1 bag of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint. No new issues - Prepared sampling bottles for the sampling day | FLAG | stage2_low_confidence | 0.022373 | ML: above threshold (no LLM available) — 0.022 |  | 0.022373 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Water Resource Recovery Facility | WW-WEST | Checked station and recorded readings on SharePoint. No new issues | FLAG | stage2_low_confidence | 0.014988 | ML: above threshold (no LLM available) — 0.015 |  | 0.014988 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Water Resource Recovery Facility | WW-WEST | - Collected weekly regulatory samples - Performed inhouse lab and recorded readings on SharePoint. No issues | FLAG | stage2_low_confidence | 0.023304 | ML: above threshold (no LLM available) — 0.023 | regulatory [regulatory] | 0.023304 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Water Resource Recovery Facility | WW-WEST | - Added 1 bag of soda ash each to aeration tank 1 and 2 - GFL on site to take a load of sludge. Transferred sludge from the thickening tank to the holding tank - Enabled RAS batch wasting mode at 8:03. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode once done - Inspected and cleaned DO probe. No new issues - No condensation in aeration air lines. all okay - Removed rags from aeration tank inlet sluice gate and surface | FLAG | stage2_low_confidence | 0.023374 | ML: above threshold (no LLM available) — 0.023 |  | 0.023374 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Water Resource Recovery Facility | WW-WEST | - Checked station and recorded readings on SharePoint - added 2 bags of soda ash each to aeration tank 1 and 2 - assisted maintenance with troubleshooting effluent pump pressure decrease - maintenance worked on RAS valve 4. Killed power to the rotork unit to be removed tomorrow to install a new RAS valve - performed partial lab due to attending contractor coordination at Janet SPS for sewer clean out - Performed JHSC inspection. Tested eyewash. Eyewash alarms received. No issues | FLAG | stage2_low_confidence | 0.040616 | ML: above threshold (no LLM available) — 0.041 | alarm [control_system]; alarms [control_system] | 0.040616 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Water Resource Recovery Facility | WW-WEST | Collected regulatory samples | FLAG | stage2_low_confidence | 0.01928 | ML: above threshold (no LLM available) — 0.019 | regulatory [regulatory] | 0.01928 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Water Resource Recovery Facility | WW-WEST | In to Monitor Station During High Flow Event. Placed Bar-screen in Continuous Cycle Mode. Found Filter Air Lift Clogged. Cleared Obstructions and Returned to Service. | FLAG | stage2_low_confidence | 0.025963 | ML: above threshold (no LLM available) — 0.026 | clog [infrastructure]; clogged [infrastructure] | 0.025963 | 0 | 0
2026-03 | 2026-03-07 | Nobleton Water Resource Recovery Facility | WW-WEST | On site to investigate reoccurring low DO alarms on Aeration Tank 2. Cleaned probe and removed rags from inlet stems on both sides. High flows from snow melting and rain all day. Instruct ROC to monitor and turn on second blower as required. Added 2x 25kg bags of soda ash to each aeration basin. | FLAG | stage2_low_confidence | 0.028161 | ML: above threshold (no LLM available) — 0.028 | alarm [control_system]; alarms [control_system] | 0.028161 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Water Resource Recovery Facility | WW-WEST | - Supernated sludge thickening tank. - Transferred sludge from the thickening tank to the sludge holding tank - Completed in-house lab and recorded readings on SharePoint. No issues. - Added 2 bags of soda ash each to aeration tank 1 and 2. - Checked station and recorded readings on SharePoint. - Enabled RAS batch wasting mode at 09:08. - Set auto wasting for 15 m^3 from train 1 and 15 m^3 from train 2 between 10:00 and 12:00. - Wasted another 5 m^3 from train 1. Then reset RAS batch wasting mode at 11:57. - Created W11714307 for alum pump 5. Pump works well in manual but displays error when analogue signal cable is plugged in. - Reduced air lift flow rates for both grit vortexes. Found the water was flowing too quickly over the weir. Flows slower and carries fewer solids over at the lower flow rate. | FLAG | stage1_keyword | 0.95 | Critical keyword match: plugged [infrastructure] | plugged [infrastructure] |  | 1 | 0
2026-03 | 2026-03-13 | Nobleton Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. Received Alum Delivery. Reviewed and Signed Documentation. Alum Tank Level: 0.57 ?> 3.10m. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 09:35. WAS Valves #2 and 3 Manual Open. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Wasting Complete, Reset Batch Wasting Set-point. Wasted 20 m3 from Clarifier #1 and 15 m3 from Clarifier #2. Returned WAS Valves #2 and 3 to Manual Closed. Inspected Bar-screen Influent and Effluent Sensors. Cleaned Sensor Heads and Adjusted Signal Pathway, Trends Restored. | FLAG | stage2_low_confidence | 0.014791 | ML: above threshold (no LLM available) — 0.015 |  | 0.014791 | 0 | 0
2026-03 | 2026-03-10 | Nobleton Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:55. WAS Valves #2 and 3 Manual Open. Maintenance (Mech.) On-site for RAS Valve Replacement. Placed RAS Pumps #1-3 in Manual Off and Isolated Manual Suction and Discharge Valves in Preparation. Lowered and Activated Decant Pump. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. Maintenance (Mech.) Unable to Complete Valve Replacement due to Isolation Issues. Returned RAS System to Service. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Adjusted Aer. Train #1 and 2 Alum Dosage Set-points Based on In-House Laboratory Results: 225.00 ?> 220.00 mg/L. Verified Sand Filter Air Lift Function and Performance. Flushed Reject Wash Boxes, Weirs and Air Lifts. Wasting Complete, Reset Batch Wasting Set-point. Wasted 15 m3 from Clarifier #1 and 10 m3 from Clarifier #2. Returned WAS Valves #2 and 3 to Manual Closed. Returned Sand Filter #2 to Service Based on High Influent Flows. Verified Air Lift Function and Performance. Completed Consolidated Headworks Building Inspections with No Issues. Returned to Service. Cleared Associated Alarms. | FLAG | stage2_low_confidence | 0.081028 | ML: above threshold (no LLM available) — 0.081 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.081028 | 0 | 0
2026-03 | 2026-03-04 | Nobleton Water Resource Recovery Facility | WW-WEST | - Collected regulatory samples - Performed in-house lab and recorded readings on SharePoint. No new issues | FLAG | stage2_low_confidence | 0.023119 | ML: above threshold (no LLM available) — 0.023 | regulatory [regulatory] | 0.023119 | 0 | 0
2026-03 | 2026-03-12 | Nobleton Water Resource Recovery Facility | WW-WEST | Remotely changed alum pumps 1, 3, 4 back to auto speex | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047456 | 0 | 0
2026-03 | 2026-03-05 | Nobleton Water Resource Recovery Facility | WW-WEST | - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint - Enabled RAS batch wasting mode at 10:08. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 13:47 - Plant water booster pump is cycling too much. This eventually causes pumps to fault on high and low pressure. This issue seems to have been going on for a while. Upon inspection, it seems RT1 and RT2 temperature protection relay faulted and is showing red. In addition, the discharge side fails to maintain adequate pressure while the plant water demand is low (vortex water scour not active at the time, no plant water usage from hydrant, etc). This is causing the pump to cycle on constantly to boost the pressure. The pressure tank seems to be okay with no leaks. Pressure switch differential settings seem okay. The check valve seems to be the culprit. I?ve tried to isolate the lead pump, pump 1, and the hissing sound stopped but the system still loses pressure fast. Therefore, it seems to be leaking on both sides. Created work order for maintenance and notified team - Received soda as delivery at 14:50. Received 250 bags. Signed all papers | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure]; leaking [infrastructure] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 1
2026-03 | 2026-03-11 | Nobleton Water Resource Recovery Facility | WW-WEST | Reduce alum from 215mg/L to 200mg/L on both post aeration dosing points. Reduce filter inlet alum from 19.5mg/L to 15mg/L due to high flows from rain and snow melt. | FLAG | stage2_low_confidence | 0.017977 | ML: above threshold (no LLM available) — 0.018 |  | 0.017977 | 0 | 0
2026-03 | 2026-03-10 | Nobleton Water Resource Recovery Facility | WW-WEST | Checked heat trace. digi span shows correct readings and confirmed heat production. No issues | FLAG | stage2_low_confidence | 0.016944 | ML: above threshold (no LLM available) — 0.017 |  | 0.016944 | 0 | 0
2026-03 | 2026-03-02 | Nobleton Water Resource Recovery Facility | WW-WEST | - Added 2 bags of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 8:55. Placed valves and was pumps to auto. Set automatic batch wasting mode to waste 19 m^3 from train 1 and 14 m^3 from train 2. Reset RAS batch wasting mode at 12:30. Placed valves and was pumps back to manual off. - performed in-house lab. No issues - Notified ROC of the work being performed - Inspected the generator and fuel level, all okay. Started the generator at 13:25. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 314 hrs to 315.06 hrs. Fuel level from 19.5 inch to inch 19.25 inch - Checked station and recorded readings on SharePoint - HVAC panel in generator room shows smoke detector tripped and HVAC tripped | FLAG | stage2_low_confidence | 0.15284 | ML: above threshold (no LLM available) — 0.153 | tripped [equipment_failure]; trip [equipment_failure]; smoke [equipment_failure] | 0.15284 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Water Resource Recovery Facility | WW-WEST | On site for ras pump valve 4 stiff. Electrical unwired will return to remove and install new plug valve. Also looked at effluent prv?s. Isolated pumps and prvs suspect leaking further down line as line pressure decreases. | FLAG | stage2_low_confidence | 0.034564 | ML: above threshold (no LLM available) — 0.035 | leak [infrastructure]; leaking [infrastructure] | 0.034564 | 0 | 0
2026-03 | 2026-03-12 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Young Jung(OIC). -Completed sand filter valve exercise -Completed scum pumps 1&2 inspections, no issues found -Completed filter inlet channel cleaning | FLAG | stage2_low_confidence | 0.010514 | ML: above threshold (no LLM available) — 0.011 |  | 0.010514 | 0 | 0
2026-03 | 2026-03-15 | Nobleton Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WO. Corporate IT Staff On-site Upon Arrival. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. Completed Filter Air Lift Inspection, Performance and Function OK. | FLAG | stage2_low_confidence | 0.0090664 | ML: above threshold (no LLM available) — 0.009 |  | 0.0090664 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Water Resource Recovery Facility | WW-WEST | On site to troubleshoot RAS VL V4. Disconnected power and outputs from PAC panel. Unwired power and control wires for actuator removal. Mechanics are replacing valve. | FLAG | stage2_low_confidence | 0.017005 | ML: above threshold (no LLM available) — 0.017 |  | 0.017005 | 0 | 0
2026-03 | 2026-03-12 | Nobleton Water Resource Recovery Facility | WW-WEST | - Cleaned filter inlet channel - Gave OJT on the plant hvac system controllers, rooftop hvac system and generator radiator. Changed two rooftop 24x24x2 sized filters. Ordered smaller 12x24x2 filters. | FLAG | stage2_low_confidence | 0.017603 | ML: above threshold (no LLM available) — 0.018 |  | 0.017603 | 0 | 0
2026-03 | 2026-03-04 | Nobleton Water Resource Recovery Facility | WW-WEST | - Transferred sludge from the thickening tank to the sludge holding tank - Enabled RAS batch wasting mode at 9:06. Wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode once done - Checked station and recorded readings on SharePoint. No new issues - Removed lots of rags from aeration tank 1 and 2 outlet - Inspected and cleaned DO probe. No issues - Checked airlines for condensation. None found | FLAG | stage2_low_confidence | 0.020824 | ML: above threshold (no LLM available) — 0.021 |  | 0.020824 | 0 | 0
2026-03 | 2026-03-12 | Nobleton Water Resource Recovery Facility | WW-WEST | Completed daily lab and added data into SharePoint. Completed station check - effluent pump still cycling on and off with high pressure, known issue with WO. Filter cell 4 plugged - unplugged and working normally. Other filter cells working well. Decanted sludge thickening tank. Placed WAS pumps and valves into auto and Enabled batch wasting at 830am and set auto waste for 30m3 from 10am to 12pm. Placed WAS pumps and valves back in manual upon wasting completion. Bled condensation from aeration condensation lines. Added 2 bags of soda ash to aeration tanks per train. Assisted Young and Harie with sludge pump PMs | FLAG | stage1_keyword | 0.95 | Critical keyword match: plugged [infrastructure] | plugged [infrastructure] |  | 1 | 0
2026-03 | 2026-03-20 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rahamithiran(OIT) working under the direction of Young Jung(OIC). -Completed lab analysis & station check , no issues found -Added 2 bags of soda ash per each aeration tank -Started batch wasting process at 09:40 , wasting from 11:00-13:00 for 19m^3 per train -Transferred STT to SHT without supernate process -Cleaned UV channel & banks -Turned WAS pumps 1&2 to manuel off | FLAG | stage2_low_confidence | 0.011526 | ML: above threshold (no LLM available) — 0.012 |  | 0.011526 | 0 | 0
2026-03 | 2026-03-19 | Nobleton Water Resource Recovery Facility | WW-WEST | - Performed in-house lab and recorded readings on SharePoint - Added 2 bags of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 9:30. Wasted 10 m^3 from train 1 and 10 m^3 from train 2 then reset RAS batch wasting mode once done - Assisted with sanitary sump pit high high float test. Alarm received - Flows still elevated due to snow melt and rain. Due to high alum usage (flow paced), changed alum pump manual speed from 37% down to 15% - Checked station and recorded readings on SharePoint. No new issues - Cleaned aeration inlet channel - Notified ROC of the work being performed. - Inspected aeration blower 1-3. Oil was good. Belt was good. Changed filter for aeration blower 2. Washed the used mesh filter with soap and placed it back on the shelf for future use | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-22 | Nobleton Water Resource Recovery Facility | WW-WEST | High flows caused bad readings on bar screen differential level. This caused bar screen to fault. Inlet channel back-fed sludge thickening tank and filled it with raw sewage. Can be pumped out tomorrow. Reset screen. Adjusted differential level from 200mm to 150mm. Monitored. Looks okay for now. | FLAG | stage2_low_confidence | 0.017614 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure] | 0.017614 | 0 | 0
2026-03 | 2026-03-18 | Nobleton Water Resource Recovery Facility | WW-WEST | - Checked station and recorded readings on SharePoint. No new issues - Added 2 bags of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 8:08. Wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode at 11:10 - Removed rags at aeration outlet - No condensation at airlines - Inspected DO probe. No issues - Inspected WAS pumps 1 and 2. Checked belt, motor and oil. No issues - Inspected RAS pumps 1~3. Checked coupling, oil and motor. No issues - Reset RAS and WAS alarms - Received a call from ROC about mechanical screen fault. Local panel shows overtorque. Upon examination, there was a huge ball of rags stuck to the screen and was not able to remove it. Placed the screen and screw to OOS and locked out. Once the rag was removed, placed the screen and screw back in service and in auto. Reset alarms and ran the screen couple times with no issues | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | Nobleton Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Assisted with Aer. Tank Inlet Channel Cleaning. Completed Vortex and Sludge Blower Inspections. Oil Reservoirs and Belts OK. Greased Bearings and Replaced Air Filters Where Necessary. Returned to Service and Cleared Associated Alarms. | FLAG | stage2_low_confidence | 0.037348 | ML: above threshold (no LLM available) — 0.037 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.037348 | 0 | 0
2026-03 | 2026-03-16 | Nobleton Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. Lowered and Activated Decant Pump. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:25. WAS Valves #2 and 3 Manual Open. Removed Rags and Debris from Bar-screen Influent Channel. Returned Bar-screen to Differential Level Set-point Operation. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pumps #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Completed Filter Air Lift Inspection, Performance and Function OK. Wasting Complete, Reset Batch Wasting Set-point. Wasted 20 m3 from Each Clarifier. Returned WAS Valves #2 and 3 to Manual Closed. Removed Rags and Debris from Aer. Tanks #1 and 2 Inlet Gates and Effluent Weirs. | FLAG | stage2_low_confidence | 0.01611 | ML: above threshold (no LLM available) — 0.016 |  | 0.01611 | 0 | 0
2026-03 | 2026-03-23 | Nobleton Water Resource Recovery Facility | WW-WEST | - Removed supernatant back into the front of the process - Performed in-house lab and recorded readings on SharePoint. Flows coming into the plant is still elevated due to rainfall and snowmelt. No issues with lab numbers, tss is good. Adjusted alum manual pump speed from 18% to 22% - Enabled RAS batch wasting mode at 9:40. Wasted 12.5 m^3 from train 1 and 12.5 m^3 from train 2 then reset RAS batch wasting mode at 13:38 - Added 2 bags of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint. No new issues - Unplugged filter 1, east side - Changed the smaller 12x24x2 filter on the hvac rooftop | FLAG | stage2_low_confidence | 0.068995 | ML: above threshold (no LLM available) — 0.069 | plugged [infrastructure] | 0.068995 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Water Resource Recovery Facility | WW-WEST | Received delivery of alum. Reviewed and signed bill of lading and certificate of analysis. Filled tank from 0.75 m to 3.56 m. | FLAG | stage2_low_confidence | 0.010436 | ML: above threshold (no LLM available) — 0.01 |  | 0.010436 | 0 | 0
2026-03 | 2026-03-26 | Nobleton Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed online DO probe verification , both aeration tank DO probes within approximately 0.70mg/L range when compared with handheld probe -Completed aeration outlet weir cleaning , valve stems and probes are clean -Completed filter inlet cleaning -Completed aeration blower room , aeration MCC & building stairs comprehensive housekeeping | FLAG | stage2_low_confidence | 0.024726 | ML: above threshold (no LLM available) — 0.025 |  | 0.024726 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Water Resource Recovery Facility | WW-WEST | On site to troubleshoot Alum pump 5. Found analogue fault on pump display. Checked control and power wiring. Tightened all connections. Fault has been resolved. Tested analogue signal and measured correct reading from Scada command. Tested pump in manual with help of operations. Ok. Alum Pump 5 is back in service. | FLAG | stage2_low_confidence | 0.069117 | ML: above threshold (no LLM available) — 0.069 | fault [equipment_failure]; scada [control_system] | 0.069117 | 0 | 0
2026-03 | 2026-03-19 | Nobleton Water Resource Recovery Facility | WW-WEST | Onsite for scheduled PMs. Called ROC to inform of hi level alarms being triggered from sump pit inspections. Inspected sump pit in process building basement - hi level alarm triggered and both pumps activate with floats. Inspected sanitary sump pit in headworks - hi level alarm triggered and pumps activated with floats. Cleared alarms. Placed filter air compressors into off and LOTO for inspection. Drained water from lines and tank. Checked and cleaned air filters, checked belts all ok. Placed compressors back into auto and confirmed operation. Cleaned filter building, swept floors and cleaned bathroom. Assisted with aeration tank channel clean. | FLAG | stage2_low_confidence | 0.025453 | ML: above threshold (no LLM available) — 0.025 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.025453 | 0 | 0
2026-03 | 2026-03-17 | Nobleton Water Resource Recovery Facility | WW-WEST | - wasted 12 m^3 from train 1 and 12 m^2 from train 2 then reset RAS batch wasting mode at 13:06 - checked station and recorded readings on SharePoint. No new issues - due to high flows coming in from snow melt. Placed alum pump 1, 3, 4 into manual speed at 37% to reduce alum dosage. Notified TL we need alum delivery next Friday | FLAG | stage2_low_confidence | 0.022371 | ML: above threshold (no LLM available) — 0.022 |  | 0.022371 | 0 | 0
2026-03 | 2026-03-20 | Nobleton Water Resource Recovery Facility | WW-WEST | Reset barscreen over tork. Watched screen run. No visible issues. Reset scada alarms. Screen operating in auto. | FLAG | stage2_low_confidence | 0.013173 | ML: above threshold (no LLM available) — 0.013 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.013173 | 0 | 0
2026-03 | 2026-03-20 | Nobleton Water Resource Recovery Facility | WW-WEST | Checked barscreen okay Adjusted torque sensor. Ran okay. | FLAG | stage2_low_confidence | 0.0099354 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099354 | 0 | 0
2026-03 | 2026-03-10 | Nobleton Water Resource Recovery Facility | WW-WEST | Had ops add another bad of soda ash per aeration tank due to lower pH. Reduced alum to post aeration further from 220mg/L to 215mg/L. | FLAG | stage2_low_confidence | 0.01097 | ML: above threshold (no LLM available) — 0.011 |  | 0.01097 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Water Resource Recovery Facility | WW-WEST | - Performed in-house lab and recorded readings on SharePoint. Higher effluent TSS and RAS/WAS TSS due to high flow event. - Added 2 bags of soda ash each to aeration tank 1 and 2 - Removed rags from aeration outlet - Checked station and recorded readings on SharePoint. No issues - Cleaned clarifier inlet channel - Changed alum pumps 1, 3 and 4 into manual speed at 25% to reduce the alum usage for high flow event. Changed alum setpoint back to 225 mg/L from 200 mg/L for aeration train 1 and 2. Changed filter inlet alum setpoint from 15 mg/L to 19.5 mg/L Update: Enabled RAS batch wasting mode. Wasted 25 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode | FLAG | stage2_low_confidence | 0.056207 | ML: above threshold (no LLM available) — 0.056 |  | 0.056207 | 0 | 0
2026-03 | 2026-03-22 | Nobleton Water Resource Recovery Facility | WW-WEST | Added 2 bags soda ash to each train. | FLAG | stage2_low_confidence | 0.010072 | ML: above threshold (no LLM available) — 0.01 |  | 0.010072 | 0 | 0
2026-03 | 2026-03-17 | Nobleton Water Resource Recovery Facility | WW-WEST | - Added 2 bags of soda ash to each aeration tank - Performed in-house lab and recorded readings on SharePoint - Enabled RAS batch wasting mode at 9:30 - Transferred sludge from the thickening tank to the holding tank | FLAG | stage2_low_confidence | 0.011352 | ML: above threshold (no LLM available) — 0.011 |  | 0.011352 | 0 | 0
2026-03 | 2026-03-18 | Nobleton Water Resource Recovery Facility | WW-WEST | Performed in-house lab and recorded readings on SharePoint Collected weekly regulatory samples | FLAG | stage2_low_confidence | 0.018176 | ML: above threshold (no LLM available) — 0.018 | regulatory [regulatory] | 0.018176 | 0 | 0
2026-03 | 2026-03-27 | Nobleton Water Resource Recovery Facility | WW-WEST | - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash per aeration tank - Checked station and recorded readings on SharePoint. No new issues - Enabled RAS batch wasting mode at 8:40. - Set autowasting for 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 12:05. - Picked rags out of aeration train 1 outlet and headworks inlet. | FLAG | stage2_low_confidence | 0.018718 | ML: above threshold (no LLM available) — 0.019 |  | 0.018718 | 0 | 0
2026-03 | 2026-03-26 | Nobleton Water Resource Recovery Facility | WW-WEST | - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash per aeration tank - Checked station and recorded readings on SharePoint. No new issues - Enabled RAS batch wasting mode at 9:00. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 12:05 | FLAG | stage2_low_confidence | 0.018373 | ML: above threshold (no LLM available) — 0.018 |  | 0.018373 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Water Resource Recovery Facility | WW-WEST | Collected weekly regulatory samples Performed in-house lab and recorded readings on SharePoint | FLAG | stage2_low_confidence | 0.018176 | ML: above threshold (no LLM available) — 0.018 | regulatory [regulatory] | 0.018176 | 0 | 0
2026-03 | 2026-03-24 | Nobleton Water Resource Recovery Facility | WW-WEST | - Checked station and recorded readings on SharePoint. No new issues - Enabled RAS batch wasting mode at 8:44. Wasted 19 m^2 from train 1 and wasted 19 m^2 from train 2 then reset RAS batch wasting mode at 12:34 - assisted with clarifier area housekeeping. Picked up some soda ash bags from the perimeter of the facility | FLAG | stage2_low_confidence | 0.021758 | ML: above threshold (no LLM available) — 0.022 |  | 0.021758 | 0 | 0
2026-03 | 2026-03-24 | Nobleton Water Resource Recovery Facility | WW-WEST | - Performed in-house lab and recorded readings on SharePoint. No issues with number - Added 1 bag of soda ash to each aeration tank | FLAG | stage2_low_confidence | 0.013062 | ML: above threshold (no LLM available) — 0.013 |  | 0.013062 | 0 | 0
2026-03 | 2026-03-03 | Nobleton Water Resource Recovery Facility | WW-WEST | - Added 2 bags of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 8:57. Placed WAS valves and pumps to auto. Auto batch wasting from 10-12, set to waste 11 m^3 from train 1 and 11 m^3 from train 2 - Performed daily in-house lab and recorded readings on SharePoint. No new issues - Checked station and recorded readings on SharePoint. No new issues | FLAG | stage2_low_confidence | 0.023627 | ML: above threshold (no LLM available) — 0.024 |  | 0.023627 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Water Resource Recovery Facility | WW-WEST | - Added 1 bag of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 8:50. Wasted 17.5 m^3 from train 1 and 17.5 m^3 from train 2 then reset RAS batch wasting mode once done - Performed station check and recorded readings on SharePoint - Performed DO probe inspection and cleaning. No issues - Removed floating solids. Removed rags from aeration inlet sluice gate and the outlet | FLAG | stage2_low_confidence | 0.022154 | ML: above threshold (no LLM available) — 0.022 |  | 0.022154 | 0 | 0
2026-03 | 2026-03-06 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, flushed screw press drain lines, replaced bins following pick up. -Monthly JHSC H&S inspection completed, no issues noted. -Consolidated Dry Well Pump Floor Inspection completed. -RS pump & motor inspection completed. -Pump 1: 1310L/s. -Pump 2: 975L/s at 0% speed, 1230L/s at 25%, 1460L/s at 50%, 1860L/s at 100%. -Pump 3: 1310L/s. -Pump 4: 1290L/s. -Pump 5 OOS. -Pump 6: 1165L/s. -Check valve inspections completed. -Sump pit inspection completed. -Dry well flood alarm completed, Sump High High Level Alarm confirmed by ROC. -Air relief valve inspection completed. -Seal water strainer inspection completed. -Air compressor inspection completed. -BAS check completed. -Ran Pump 1 in auto duty 1 again until it failed again on Motor/Bearing High Temp Alarm. -Pumps 1 and 5 remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; failed [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] | sso [critical]; flood [critical]; failed [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-30 | Markham Leslie Pumping Station | WW-CEAST | Station check complete and the readings have been entered in the sharepoint. Changed out the rag bin. | FLAG | stage2_low_confidence | 0.012317 | ML: above threshold (no LLM available) — 0.012 |  | 0.012317 | 0 | 0
2026-03 | 2026-03-04 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, hosed down floor, repositioned screw press to better align with floor drain. -Bar screen bin removal completed. -Monthly diesel generator test run completed, readings entered into SharePoint. -1058 - Transferred site to generator power. -1241 - Transferred site back to utility power. -Gen. 1: Start hours: 231:42, Stop hours: 233:41, Run time: 1hr, 59min. -Gen. 2: Start hours: 119:35, Stop hours: 121:33, Run time: 1hr, 58min. -Gen. 3: Start hours: 105:54, Stop hours: 107:52, Run time: 1hr, 58min. -Hazardous waste collection and removal completed. -Overflow kit inspection completed. -Ran Pump 1 in auto, duty 1. Pump ran from 12:55-1450 before faulting again on Motor/Bearing High Temp Alarms. Left pump faulted and OOS for the night. -Pump 5 OOS with VFD Fault following generator testing. Work request created for issue. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; fault [equipment_failure]; faulted [equipment_failure]; faulting [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure]; pump fault [infrastructure]; hazard [safety] | overflow [critical]; fault [equipment_failure]; faulted [equipment_failure]; faulting [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure]; pump fault [infrastructure]; hazard [safety] |  | 1 | 1
2026-03 | 2026-03-02 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Reset Earth Fault on AHU1. -Reset Fault 47, Stack Overtemp Fault on Pump 1. -Test ran Pump 1 in auto, duty 1. Pump 1 ran for just under two hours before faulting again. Fault 47, Overtemp Fault back on Pump 1 MCC panel and SCADA is showing Fault Alarm, Motor/Bearing High Temp Alarm, and Motor/Bearing High Temp Trip Alarm. -Left Pump 1 in manual off, OOS for the night. -Hoist inspections completed on site, no issues noted. -Checked screen room, flushed screw press drain lines, replaced bins, cleaned floor in screen room. -Pump 1 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulting [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] | fault [equipment_failure]; faulting [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-10 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete consolidated wet well inspection work order. -Wet well high level alarm test completed and confirmed by ROC. -Wet well inspection and cleaning completed. -Wet well valve exercises completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Maintenance team able to clear faults on Generator 3 and Pump 5. Both are now back in service. -Pump 1 remains OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] | fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-02 | Markham Leslie Pumping Station | WW-CEAST | LSSS - Pump 1 fault alarm. Checked site, pump duty rotated to pump 5. Phil R logged into the facility logbook to complete work orders. Will monitor site. *Wong book, should be in ROC wastewater* | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; work order [maintenance_action]; alarm [control_system] | fault [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Cleared fault on Pump 1 and ran in auto, duty 1 for close to two hours before pump faulted again. -Pump 1 back OOS for the weekend. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, replaced bins following pick up, flushed screw press drain lines, topped up bar screen oil. -Consolidated dry well valve exercise work order completed. -Pump discharge valves are automatically exercised each day as pumps cycle through duty rotation. -Pump isolation valves all fully exercised. -Forcemain header and tie valves all fully exercised. -Forcemain drain valve exercised. -Cleared all alarms following work. -Pump 1 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; pump fault [infrastructure] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-03 | 2026-03-19 | Markham Leslie Pumping Station | WW-CEAST | On site to check automatic phone dialer. No dial tone on line. Need Bell technician | FLAG | stage2_low_confidence | 0.015188 | ML: above threshold (no LLM available) — 0.015 |  | 0.015188 | 0 | 0
2026-03 | 2026-03-27 | Markham Leslie Pumping Station | WW-CEAST | On site for pump PM?s LOTO before PM?s with electricians Completed pump PM?s on pumps 4,5, and 6. Greased pumps Greased driveshafts Checked oil levels on pumps 5 and 6 Lower bearings need to be topped up on pumps 5-6 | FLAG | stage2_low_confidence | 0.0072895 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072895 | 0 | 0
2026-03 | 2026-03-18 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -bins out for pickup, screen room clean, bins rotated -Housekeeping -pump 1 remains OOS, 5 pumps available in auto -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-16 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Checked screen room, changed out rag bin, flushed screw press drain lines, topped up bar screen oil. -Consolidated monthly surge tank inspection completed. Exercised valves and flushed transmission lines. -Pump 1 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-27 | Markham Leslie Pumping Station | WW-CEAST | Run pump 1 Greased during run. Temp stabilized a few times Pump shut down Allowed to cool Started pump and regressed upper bearing. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062148 | 0 | 0
2026-03 | 2026-03-19 | Markham Leslie Pumping Station | WW-CEAST | On site with total Lift for annual inspections | FLAG | stage2_low_confidence | 0.012727 | ML: above threshold (no LLM available) — 0.013 |  | 0.012727 | 0 | 0
2026-03 | 2026-03-27 | Markham Leslie Pumping Station | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Reset fault on Pump 1 and test run pump for maintenance team. -Checked screen room, changed out rag bin for the weekend, replaced bins following pick up, flushed screw press drain lines, bar screen oil topped up. -Assisted maintenance team with pump testing and maintenance activities. -Pump 1 is currently still running, but if it faults again it will remain OOS for the weekend. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure] | fault [equipment_failure]; oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-25 | Markham Leslie Pumping Station | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Ran Pump 1 in auto, duty 1 until pump faulted again. -Pump 1 remains OOS. -Rag bins placed out for pickup. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; pump fault [infrastructure] | sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; pump fault [infrastructure] |  | 1 | 1
2026-03 | 2026-03-20 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, changed out rag bin, replaced bins following pick up, flushed screw press drain lines, topped up bar screen oil, cleaned rags off floor. -Completed cleaning tasks around yard and doorways. -Pump 1 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-23 | Markham Leslie Pumping Station | WW-CEAST | On site for odour control PM. Completed. | FLAG | stage2_low_confidence | 0.012462 | ML: above threshold (no LLM available) — 0.012 |  | 0.012462 | 0 | 0
2026-03 | 2026-03-11 | Markham Leslie Pumping Station | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, changed out rag bin, topped up bar screen oil, flushed screw press drain lines. -Placed rag bins out for pick up. -Ran Pump 1 in auto, duty 1 until Pump Fault came back in with Motor/Bearing High Temp Alarm. -Pump 1 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; pump fault [infrastructure] | fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | Markham Leslie Pumping Station | WW-CEAST | On site to check pump 5 VFD. Found auxiliary power fault. Was able to reset fault. Suspect it happened during power transfer last week. Operations tested pump 5 in manual. Pump is working ok. Pump 5 back in auto duty rotation. Also onsite to check generator 3. Local control panel screen was off. Found loose fuse holder on front of panel. Repaired. Screen is back on. No more issues. | FLAG | stage2_low_confidence | 0.12801 | ML: above threshold (no LLM available) — 0.128 | fault [equipment_failure]; oos [equipment_failure]; repair [maintenance_action] | 0.12801 | 0 | 1
2026-03 | 2026-03-09 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Washed Bayview Steeles OCF mist eliminator filters in screen room and left filters out to dry. -Checked screen room, changed out rag bin, flushed screw press drain lines, hosed down floor. -Odour control scrubber system inspection completed. Inspected filters, greased fan shaft in screen room OCU. -Station check completed, readings entered into SharePoint. -Bypass sampling kit inspection completed. -Ran Pump 1 in auto, duty 1 until Motor/Bearing High Temp Alarms came back in. -At 1132, Generator 3 Warning Alarm and Generator 3 DGC Not in Auto Alarm came in. Inspected Generator 3, found generator screen/panel blank, appears as though their is no power to Gen. 3 panel. Unable to reset alarms locally on generator or at GMCP panel. Work request created for issue. -Pump 1 and 5 OOS, Generator 3 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | bypass [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 1
2026-03 | 2026-03-23 | Markham Leslie Pumping Station | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 4 hours, except, pump 1, which is in manual/off out of service. Standby power generators available in auto. Switch sump pump duty from pump 1 to 2. Ran sump pump 2 for several minutes to removed stagnant water/sewage from the sump pit. Drained condensates from the surge tanks air compressors. Blew down bubblers. Cleared/reset alarms. Checked dry well, ok. Checked bar screens. Found screw press drain clog. Unclogged said drain, afterwards, cleaned/hosed down bar screen room. Switched rag bin. Added oil on the screen chain oil reservoir. Both are almost empty. Adjusted dripping port to a minimal opening. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; drip [infrastructure]; clog [infrastructure]; clogged [infrastructure] | sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; drip [infrastructure]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 0
2026-03 | 2026-03-25 | Markham Leslie Pumping Station | WW-CEAST | On site completed bar screen rag bin removal and replacement. Switched rag bin Pushed out rag bins for pick up by Miller Waste tomorrow. Cleaned screen room. | FLAG | stage2_low_confidence | 0.012739 | ML: above threshold (no LLM available) — 0.013 |  | 0.012739 | 0 | 0
2026-03 | 2026-03-31 | Mount Albert Wells 1 & 2 | EAST | Under direction of OIC Dan Zhou Started well pump 2 in manual on @ 08:49 hrs. for sampling | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032605 | 0 | 0
2026-03 | 2026-03-31 | Mount Albert Wells 1 & 2 | EAST | On Site for; - Station checks - Regulatory sampling micro (W11705406) Data in PWQ Workbook Regulatory samples of well 2 taken @ 09:34 hrs. Influent Grab @ 09:33 hrs. FCl: 1.87 mg/L Analyzer FCl: 1.95 mg/L Effluent Grabs @ 09:34 hrs. FCl: 1.26 mg/L TCL: 1.56 mg/L Analyzer FCl: 1.32 mg/L @ 09:42 hrs. placed well pump 2 back in auto Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-31 | Mount Albert Wells 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Regulatory sampling, micro (11705406) Data in PQW workbook @ 14:10 hrs. placed well pump 2 in manual off, silicate pumps 1/2 and hypo pumps 1/2 in manual/manual speed 0%. Verified flow path of well pump 1 is valved to waste @ 14:12 started well pump 1 in local Regulatory sample taken for well 1 @ 14:42 hrs. @ 14:43 placed well pump 1 in local off @ 14:44 returned silicate pumps 1/2 and hypo pumps 1/2 to auto, auto speed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0062113 | 0 | 0
2026-03 | 2026-03-03 | Mount Albert Wells 1 & 2 | EAST | On site to accept hypo delivery Start 45cm Stop 88cm | FLAG | stage2_low_confidence | 0.0083264 | ML: above threshold (no LLM available) — 0.008 |  | 0.0083264 | 0 | 0
2026-03 | 2026-03-04 | Mount Albert Wells 1 & 2 | EAST | On site to top up silicate tank.? Before level: 61.6cm After level: 120 cm | FLAG | stage2_low_confidence | 0.0077032 | ML: above threshold (no LLM available) — 0.008 |  | 0.0077032 | 0 | 0
2026-03 | 2026-03-13 | Mount Albert Wells 1 & 2 | EAST | Under direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Influent Grab @ 14:16 hrs. FCl: 1.42 mg/L Analyzer FCl: 1.44 mg/L Effluent Grabs @ 14:27 hrs. FCl: 1.31 mg/L TCL: 1.74 mg/L Analyzer FCl: 1.33 mg/L Checked valving for silicate system and water flush line. Tested silicate pump 2. Placed back in service on auto duty rotate. Quick report made (W11733156) Duty inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-09 | Mount Albert Wells 1 & 2 | EAST | On Site for; - Station checks - Operational sampling, iron Data in PWQ Workbook Influent Grab @ 11:28 hrs. FCl: 1.86 mg/L Analyzer FCl: 1.89 mg/L Effluent Grabs @ 11:30 hrs. FCl: 1.35 mg/L TCL: 1.73 mg/L Analyzer FCl: 1.30 mg/L @ 11:43 returned well pump 2 to auto Duty inactive Equipment OOS: Silicate pump 2 Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-06 | Mount Albert Wells 1 & 2 | EAST | On Site for; - Station checks - Turbidity analyzer maintenance Data in PWQ Workbook Influent Grab @ 10:29 hrs. FCl: 1.33 mg/L Analyzer FCl: 1.37 mg/L Effluent Grabs @ 10:31 FCl: 1.42 mg/L TCL: 1.74 mg/L Analyzer FCl: 1.33 mg/L Turbidity analyzer maintenance: @ 10:39 placed well pump 2 in manual off, no flow directed to users Start clean @ 10:43 hrs. Stop clean @ 10:53 hrs. Turbidity spike due to new vial installation retaining static (formed bubbles), re cleaned new vial, once any remaining bubbles leave vial, NTU should stabilize. Informed on call OIC Jack Palmer. @ 11:18 returned pump 2 to auto Duty inactive Equipment OOS: Silicate pump 2 Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-10 | Mount Albert Wells 1 & 2 | EAST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-12 | Mount Albert Wells 1 & 2 | EAST | Silicate top up: Before: 360L (76.5) After: 493L (104.7) | FLAG | stage2_low_confidence | 0.0075169 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075169 | 0 | 0
2026-03 | 2026-03-02 | Mount Albert Wells 1 & 2 | EAST | On Site for; - Station checks - JHSC Health and Safety inspection Data in PWQ Workbook Influent Grab @ 10:38 FCl: 1.35 mg/L Analyzer FCl: 1.32 mg/L Effluent Grabs @ 10:42 FCl: 1.28 mg/L TCL: 1.55mg/L Analyzer FCl: 1.22 mg/L Duty Inactive Equipment OOS: Silicate pump 2 Station running nominally | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-09 | Mount Albert Wells 1 & 2 | EAST | Under direction of OIC Dan Zhou @ 10:45 hrs. Placed well pump 2 in manual on for operational sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034345 | 0 | 0
2026-03 | 2026-03-04 | Mount Albert Wells 1 & 2 | EAST | Under direction of OIC Dan Zhou On Site for; - Station checks - Regulatory sampling micro (W11637246), manganese sampling (W11638464) Data in PWQ Workbook Regulatory samples taken @ 10:42 hrs. @ 10:05 well pump 2 interlock due to manual switch of hypo and silicate pumps @ 10:20 manually stated well pump 2 @ 10:25 placed hypo pump2 in manual speed 25 % and silicate pump 1 in manual speed 35 % Verified well pump 1 is valved to waste @ 10:27 started well pump 1 Influent Grab @ 10:43 FCl: 1.90 mg/L Analyzer FCl: 1.97 mg/L Effluent Grabs @ 10:42 FCl: 1.52 mg/L TCL: 1.91 mg/L Analyzer FCl: 1.42 mg/L @ 10:55 placed well pump 1 back in local off, and well pump 2 in auto, returned silicate pump 1 and hypo pump 2 speed setpoints back in auto Equipment OOS: Silicate pump 2 Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-26 | Mount Albert Wells 1 & 2 | EAST | Station Check (no issues found) Input data to PWQ 11:41 Verified CL17s (mg/l) Influent Free: Grab 1.36, A 1.39 Effluent Free: Grab 1.20, A 1.26 Effluent Total: Grab 1.37 Silicate top up (70.8 to 107.4cm) Hypo tank transfer (preparation for small leak repair): Tank #1 (60.0 to 87.3cm) (placed in service) Tank #2 (50.4 to 23.2 cm) (placed out of service) Instrumentation on site for "loss of heartbeat" repair Diesel fuel Lo alarm adjusted from 21.0cm to 22.0 cm | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; repair [maintenance_action]; alarm [control_system]; leak [infrastructure] | out of service [equipment_failure]; repair [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-17 | Mount Albert Wells 1 & 2 | EAST | Under Direction of OIC Patrick Fobert On site for PM's; - Turbidity analyzer maintenance - Influent and Effluent AIT maintenance - Deep well exhaust valve test - Sodium hypochlorite panel boards inspection - Silicate pumps maintenance - Sodium hypochlorite pumps maintenance - High/low temp alarm test - Butterfly valve exercise - Sodium hypochlorite system maintenance - Well 2 bore hole inspection - Generator test run Chlorine analyzer maintenance: Start clean @ 09:22 hrs. Stop clean @ 09:59 hrs. Analyzer verification: Effluent grab @ 10:30 hrs. FCl: 1.34 mg/L Analyzer: FCl: 1.34 mg/L Influent grab @ 10:40 hrs. FCl: 1.42 mg/L Analyzer: FCl: 1.42 mg/L Turbidity meter maintenance: Start @ 09:28 hrs. Stop @ 09:47 hrs. Pre clean NTU: 0.043 Post clean NTU: 0.038 Building Low temp alarm manually triggered @ 10:08 hrs. , alarm in @ 10:10 hrs. Building High temp alarm manually triggered @ 10:18 hrs. , alarm in @ 10:22 hrs. *Replaced pump dosing head on silicate pump 2 (pump head cavity is msaller than pump 1). New max flow is 100 mL/min. Adjusted max flow silicate dosing setpoint on SCADA to 100 mL/min.* Generator test run: Start Fuel: 1486 L Stop Fuel: 1454 L Start Hours: 208.85 Stop Hours: 210.25 Start Time: 13:18 hrs. Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 13:18 hrs. Switched ATS to Test for generator power @ 13:28 hrs. Placed generator under facility load, Well pump 2 in Manual ON @ 13:50 hrs. placed well pump1 in manual on local, valved to waste *under load* Operating Current: 69 Amps Operating Frequency: 60.05 Hz Operating Voltage: 602.85 Volts Engine speed: 1798 RPM Water/coolant Temp: 88.68 C Oil Pressure: 392 kpa Oil Temperature: 83.00 C @ 14:14 hrs. well pump 1 in local off for ATS switch @ 14:18 placed well pump 2 in manual off for ATS switch @ 14:22 hrs. Toggled ATS to normal @ 14:32 power switched to station power @ 14:42 cooldown stopped @ 14:44 placed well pump 2 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure]; scada [control_system]; alarm [control_system]; leak [infrastructure] | 1.8637e-05 | 0 | 0
2026-03 | 2026-03-19 | Mount Albert Wells 1 & 2 | EAST | Silicate top up | FLAG | stage2_low_confidence | 0.011807 | ML: above threshold (no LLM available) — 0.012 |  | 0.011807 | 0 | 0
2026-03 | 2026-03-16 | Mount Albert Wells 1 & 2 | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ Workbook Influent Grab @ 14:32 hrs. FCl: 1.53 mg/L Analyzer FCl: 1.59 mg/L Effluent Grabs @ 14:34 hrs. FCl: 1.40 mg/L TCL: 1.74 mg/L Analyzer FCl: 1.31 mg/L Changed buffer and analyzer reagents for influent and effluent AIT's. Silicate pump 2 fault alarm on March 14 due to air releif valve plug being compromised. Threading in pump head will not hold plug in place. Informed acting team lead Patrick Fobert, (part being sourced). Duty inactive Equipment OOS: Silicate Pump 2 Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; alarm [control_system] | fault [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-25 | Mount Albert Wells 1 & 2 | EAST | @ 08:52 started well pump 2 for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037311 | 0 | 0
2026-03 | 2026-03-25 | Mount Albert Wells 1 & 2 | EAST | On Site for; - Station checks - Regulatory sampling micro (W11690092) Data in PWQ Workbook Regulatory samples taken well 2 taken @ 09:48 hrs. , well 1 raw sample taken @ 10:22 hrs. Influent Grab @ 09:32 hrs. FCl: 1.88 mg/L Analyzer FCl: 1.95 mg/L Effluent Grabs @ 09:48 hrs. FCl: 1.28 mg/L TCL: 1.56 mg/L Analyzer FCl: 1.24 mg/L NTU: 0.068 NTU @ 10:01 placed well pump 2 in manual off Verified well pump 1 is valved to waste @ 10:07 hrs. placed hypo pumps 1/2 in manual speed 0 % and silicate pumps 1/2 in manual speed 0 % @ 10:12 hrs. started well pump 1 in local, valved to waste Disregard fail to start silicate and hypo pump alarms, due to not dosing raw well water, valved to waste @ 10:22 placed well pump 1 back in local off, returned silicate pumps 1/2 and hypo pumps 1/2 speed setpoints back in auto @ 10:24 hrs. placed well pump 2 back in auto Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; regulatory [regulatory]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | Mount Albert Wells 1 & 2 | EAST | Under direction of OIC Partrick Fobert Started well pump 2 for regulatory sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0057532 | 0 | 0
2026-03 | 2026-03-11 | Mount Albert Wells 1 & 2 | EAST | On site to complete station check. Collecting weekly Bac-t Samples. W11656823 Weekly Bac-t Samples. Time: 14:04 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.93 2.01 Time: 14:07 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.30 1.29 Total: 1.56 At 14:00 started up well 1 to run to waste to collect raw water sample. Verified analyzers with grabs. Checked site and trends. Gen tank 1 hi alarm disregard. Silicate pump 2 OOS till part can be replaced. At 14:38 stopped well 1. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | Mount Albert Wells 1 & 2 | EAST | On Site for; - Station checks - Regulatory sampling micro (W11672709) Data in PWQ Workbook Regulatory samples taken well 2 taken @ 09:33 hrs. , well 1 raw sample taken @ 09:55 hrs. Influent Grab @ 09:24 hrs. FCl: 1.88 mg/L Analyzer FCl: 1.96 mg/L Effluent Grabs @ 09:33 hrs. FCl: 1.36 mg/L TCL: 1.76 mg/L Analyzer FCl: 1.30 mg/L Verified well pump 1 is valved to waste @ 09:39 placed hypo pumps 1/2 in manual speed 0 % and silicate pumps 1/2 in manual speed 0 % *Disregard fail to start silicate and hypo pump alarms, due to not dosing raw well water, valved to waste @ 09:39 placed well pump 2 in manual off and well pump 1 in local on for raw well 1 sample @ 09:54 placed well pump 1 back in local off, returned silicate pump 1/2 and hypo pump 1/2 speed setpoints back in auto @ 10:00 hrs. placed well pump 2 back in auto Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; regulatory [regulatory]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-20 | Mount Albert Wells 1 & 2 | EAST | On Site for; - Station checks - Turbidity analyzer maintenance Data in PWQ Workbook Influent Grab @ 12:53 hrs. FCl: 1.45 mg/L Analyzer FCl: 1.44 mg/L Effluent Grabs @ 12:57 hrs. FCl: 1.38 mg/L TCL: 1.72 mg/L Analyzer FCl: 1.35 mg/L @ 13:11 placed well pump 2 in manual off for turbidity analyzer maintenance Clean start @ 13:12 hrs. Clean stop @ 13:20 hrs. Noticed slow drip leak on interconnect valve on hypo tank 2 side. Created work order for W-Maint (W11749660) @ 13:35 placed well pump 2 in auto. Duty inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure]; drip [infrastructure] | oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure]; drip [infrastructure] |  | 1 | 0
2026-03 | 2026-03-25 | Mount Albert Wells 1 & 2 | EAST | Changed well 2 flow setpoint from 22 l/s to 27 l/s. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046513 | 0 | 0
2026-03 | 2026-03-23 | Mount Albert Wells 1 & 2 | EAST | On Site for; - Station checks Data in PWQ Workbook Duty inactive during grabs Influent Grab @ 11:55 hrs. FCl: 1.28 mg/L Analyzer FCl: 1.31 mg/L Effluent Grabs @ 11:59 hrs. FCl: 1.40 mg/L TCL: 1.71 mg/L Analyzer FCl: 1.32 mg/L Isolated hypo tank 1 to drain hypo tank 2 for interconnect valve repair. Duty active Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action] | oos [equipment_failure]; repair [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-30 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - clean silicate containment area Cleaned silicate containment area and surrounding area plus sprayed down piping gallery room. During clean, ROC called that eyewash flow alarm is going off. Can't clear alarm remotely or on site at OIT. Attempted to resolve the issue at the eyewash and cannot. Made work order # W11768770 and informed team Lead Dan Zhou | FLAG | stage2_low_confidence | 0.046824 | ML: above threshold (no LLM available) — 0.047 | work order [maintenance_action]; alarm [control_system]; containment [safety] | 0.046824 | 0 | 0
2026-03 | 2026-03-31 | Mount Albert Well 3 | EAST | Under Direction of OIC Dan Zhou @ 12:52 hrs. placed well pump 3 in manual on for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032573 | 0 | 0
2026-03 | 2026-03-12 | Mount Albert Well 3 | EAST | Silicate top up | FLAG | stage2_low_confidence | 0.011807 | ML: above threshold (no LLM available) — 0.012 |  | 0.011807 | 0 | 0
2026-03 | 2026-03-31 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11705406) Data in PQW Workbook Regulatory samples taken @ 13:47 hrs. Influent Grabs @ 13:46 hrs. FCl: 1.75 mg/L Analyzer: FCl: 1.77 mg/L Effluent Grabs @ 13:47 hrs. FCl: 1.72 mg/L TCl: 1.95 mg/L Analyzer: FCl: 1.71 mg/L NTU: 0.065 NTU @ 13:52 placed well pump 3 back in auto Duty inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-09 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Operational sampling, iron Data in PQW Workbook @ 09:56 hrs. placed well pump 3 in manual on for operational sampling Influent Grabs @ 10:25 hrs. FCl: 1.73 mg/L Analyzer: FCl: 1.75 m,g/L Effluent Grabs @ 10:28 hrs. FCl: 1.83 mg/L TCl: 1.89 mg/L Analyzer: 1.88 mg/L NTU: 0.56 NTU @ 10:40 hrs. returned well pump 3 to auto Duty inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-02 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PQW Workbook Influent Grabs @ 09:43 FCl: 1.59 mg/L TCl: 1.78 mg/L Analyzer: FCl: 1.53 m,g/L Effluent Grabs @ 09:49 FCl: 1.49 mg/L TCl: 1.76 mg/L Analyzer: 1.52 mg/L NTU: 0.67 NTU Changed influent and Effluent analyzer buffer and reagents Duty Inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-12 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for PM's - Chemical system inspection (silicate) - Supply fans check - Exhaust fans check - Chlorine leak detector test - Dechlorination puck dispenser inspection and cleaning - Chlorine scrubber media sampling - Standby power generator test run - JHSC Health and safety inspection - Deep well exhaust valve check - Turbidity analyzer maintenance and calibration - Chlorine analyzer maintenance - Chlorine scrubber check - Chlorine cylinder emergency repair kit inspection @ 09:17 hrs. informed ROC about PM's @ 09:19 hrs. placed well pump 3 in manual off for PM's Chlorine analyzer maintenance: Influent analyzer: Clean start @ 09:32 hrs. Clean stop @ 09:15 hrs. Post clean verification: Grab @ 12:28 hrs. FCl: 1.42 mg/L Analyzer: FCl: 1.47 mg/L Effluent analyzer: Clean start @ 09:32 hrs. Clean stop @ 09:15 hrs. Post clean verification: Grab @ 12:31 hrs. FCl: 1.47 mg/L Analyzer: FCl: 1.48 mg/L Turbidity meter maintenance and calibration: Clean start @ 09:47 hrs. Clean stop @ 10:05 hrs. Pre clean/calibration NTU: 0.081 Post clean/calibration NTU: 0.058 Chlorine leak detector triggered @ 12:19 hrs. Generator test run: Start Fuel: 882.8 L/ 876.6 L Stop Fuel: 876.7 L/868.4 L Start Hours: 379:33 Stop Hours: 380:45 Start Time: 12:43 hrs. Stop Time (including cool down): 13:58 hrs. Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 12:43 hrs. Switched ATS to Test for generator power @ 12:55 hrs. Placed generator under facility load Well pump 3 in Manual ON *under load* Operating Current: 41 Amps Operating Frequency: 60.1 Hz Operating Voltage: 605 Volts Engine speed: 1800 RPM Water/coolant Temp: 181 f Oil Pressure: 56 kpa @ 13:47 hrs. placed well pump 3 in manual off for ATS switch @ 13:48 hrs. Toggled ATS to normal @ 13:52 hrs. power switched to station power @ 13:58 hrs. cooldown finished @ 14:17 hrs. returned well pump 3 to auto. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; fault [equipment_failure]; repair [maintenance_action]; leak [infrastructure] | emergency [critical]; fault [equipment_failure]; repair [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | Mount Albert Well 3 | EAST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-04 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11637246), manganese sampling (W11638464) Data in PQW Workbook Regulatory samples taken @ 09:32 hrs. @ 08:50 hrs. started well pump3 in manual for sampling Influent Grabs @ 09:33 FCl: 1.68 mg/L Analyzer: FCl: 1.68 m,g/L Effluent Grabs @ 09:32 FCl: 1.66 mg/L TCl: 1.88 mg/L Analyzer: 1.74 mg/L NTU: 0.78 NTU @ 09:48 returned well pump 3 to auto Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-06 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Turbidity analyzer maintenance Data in PQW Workbook @ 09:20 informed ROC of turbidity analyzer maintenance, placed well pump3 in manual off, no water directed to users Turbidity Analyzer maintenance: Start clean @ 09:33 hrs. Stop clean @ 09:45 hrs. @ 09:45 disregard turbidity out of range alarm, due to improper flow to instrument Influent Grabs @ 09:50 hrs. FCl: 1.61 mg/L Analyzer: FCl: 1.65 m,g/L Effluent Grabs @ 09:52 hrs. FCl: 1.55 mg/L TCl: 1.89 mg/L Analyzer: 1.65 mg/L NTU: 0.50 NTU @ 10:01 hrs. returned well pump 3 to auto Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-11 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11656823) Data in PQW Workbook Regulatory samples taken @ 14:36 hrs. Influent Grabs @ 14:36 hrs. FCl: 1.73 mg/L Analyzer: FCl: 1.73 m,g/L Effluent Grabs @ 14:36 hrs. FCl: 1.71 mg/L TCl: 1.96 mg/L Analyzer: FCl: 1.68 mg/L mg/L NTU: 0.078 NTU @ 14:26 hrs. deactivated MTETNL tower duty Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-25 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou @ 10:17 hrs. Started well pump 3 in manual on for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003274 | 0 | 0
2026-03 | 2026-03-20 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Turbidity analyzer maintenance Data in PQW Workbook Influent Grabs @ 11:03 hrs. (duty active for grabs) FCl: 1.69 mg/L Analyzer: FCl: 1.75 mg/L Effluent Grabs @ 11:06 hrs. FCl: 1.65 mg/L TCl: 1.98 mg/L Analyzer: FCl: 1.68 mg/L NTU: 0.065 NTU Turbidity analyzer maintenance: @ 11:40 hrs. placed well pump 3 in manual off for turbidity analyzer maintenance Start clean @ 11:42 hrs. Stop clean @ 11:55 hrs. Post clean NTU: 0.053 @ 12:08 placed well pump 3 back in auto Duty inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-25 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11690092) - Operational sampling, (iron, NTU, FCl, TCl, temp) Data in PQW Workbook Regulatory samples taken @ 10:59 hrs. Influent Grabs @ 10:58 hrs. FCl: 1.85 mg/L Analyzer: FCl: 1.89 mg/L Effluent Grabs @ 10:59 hrs. FCl: 1.66 mg/L TCl: 1.92 mg/L Analyzer: FCl: 1.67 mg/L NTU: 0.072 NTU @ 11:13 placed well pump 3 back in auto Duty inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-18 | Mount Albert Well 3 | EAST | @ 09:56 Started well pump 3 in manual on for regulatory sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0064259 | 0 | 0
2026-03 | 2026-03-23 | Mount Albert Well 3 | EAST | On site to complete chlorine cylinder change. Start: 0.0/64kg Stop: 68/64kg Also completed chlorine system inspection tested vacuum. No leaks detected. Cleared alarms that were from this inspection. Any changes in trends are due to work order being completed. System back to normal. | FLAG | stage2_low_confidence | 0.054735 | ML: above threshold (no LLM available) — 0.055 | work order [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.054735 | 0 | 0
2026-03 | 2026-03-23 | Mount Albert Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Chlorine gas system inspection (worked with Phill De Groot) - Silicate system hot water flush and inspection - Chlorine cylinder change (worked with Pill De Groot) - Comprehensive housekeeping Data in PQW Workbook @ 09:36 hrs. informed ROC of chlorine gas system inspection @ 09:36 placed well in auto for gas chlorine system inspection, and silicate system flush Influent Grabs @ 11:16 hrs. FCl: 1.56 mg/L Analyzer: FCl: 1.60 mg/L Effluent Grabs @ 11:18 hrs. FCl: 1.53 mg/L TCl: 1.83 mg/L Analyzer: FCl: 1.61 mg/L NTU: 0.058 NTU @ 11:25 placed well pump 3 back in auto Duty inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | Mount Albert Well 3 | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks - Regulatory sampling, micro (W11672709) Data in PQW Workbook Regulatory samples taken @ 11:02 hrs. Influent Grabs @ 10:59 hrs. FCl: 1.68 mg/L Analyzer: FCl: 1.70 mg/L Effluent Grabs @ 11:02 hrs. FCl: 1.62 mg/L TCl: 1.84 mg/L Analyzer: FCl: 1.66 mg/L mg/L NTU: 0.058 NTU @ 11:10 placed well pump 3 back in auto Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-24 | Mount Albert Well 3 | EAST | On site with Ernesto hidalgo to work on BAS system. | FLAG | stage2_low_confidence | 0.01305 | ML: above threshold (no LLM available) — 0.013 |  | 0.01305 | 0 | 0
2026-03 | 2026-03-16 | Mount Albert Well 3 | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PQW Workbook Influent Grabs @ 11:41 hrs. FCl: 1.59 mg/L Analyzer: FCl: 1.58 mg/L Effluent Grabs @ 12:57 hrs. FCl: 1.56 mg/L TCl: 1.81 mg/L Analyzer: FCl: 1.59 mg/L NTU: 0.053 NTU Duty inactive Equipment OOS: None Facility: OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-26 | Mount Albert Well 3 | EAST | Station Check (no issues found) Input data to PWQ 14:10 Verified CL17s (mg/l) Influent Free: Grab 1.54, A 1,52 Effluent Free: Grab 1.48, A 1.50 Effluent Total Grab 1.58 #11696586 Turb maint. Silicate pump #1 performed draw down (ok) and verified no leak Silicate top up (90.7 to 109.4cm) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | leak [infrastructure] | 0.0064193 | 0 | 0
2026-03 | 2026-03-19 | Mount Albert Well 3 | EAST | Silicate top up (79.1 to 96.0cm) | FLAG | stage2_low_confidence | 0.0096997 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096997 | 0 | 0
2026-03 | 2026-03-31 | Mount Albert North Elevated Tank | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11705406) - Operational sampling, (iron, FCl, TCl, temp, ATP) Data in PQW workbook Regulatory sample taken @ 08:35 hrs. Grabs @ 08:35 hrs. FCl: 1.31 mg/L TCl: 1.57 mg/L Analyzer: FCl: 1.33 mg/L Changed buffer and analyzer reagents. Tower draining for sampling Facility: OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.00088496 | 0 | 0
2026-03 | 2026-03-06 | Mount Albert Well 3 | EAST | On site to remove extra parts from camlok installation | FLAG | stage2_low_confidence | 0.013297 | ML: above threshold (no LLM available) — 0.013 |  | 0.013297 | 0 | 0
2026-03 | 2026-03-09 | Mount Albert North Elevated Tank | EAST | Under direction of OIC Dan Zhou. Initiated deep cycle - Duty 1 band changed to 42-85 %. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038267 | 0 | 0
2026-03 | 2026-03-04 | Mount Albert North Elevated Tank | EAST | On site to check station and equipment.? Tower is filling.? 10:51 grab chlorine residual from outlet: FCL= 1.39 mg/l, TCL= 1.64 mg/l.? Analyzer free = 1.37 mg/l.? 10:51 collected micro sample, YD 11637264. And MN sample, W11638464. 10:52 collected in house samples. Replaced CL17 reagents. Reviewed trends, no major concerns. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049618 | 0 | 0
2026-03 | 2026-03-11 | Mount Albert North Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11656823 Weekly Bac-t Sample. Time: 13:40 Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.37 Total: 1.59 Entered data into PWQ sheet. Verified analyzer with grabs. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. Activated duty at 13:45. | FLAG | stage2_low_confidence | 0.010145 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.010145 | 0 | 0
2026-03 | 2026-03-13 | Mount Albert North Elevated Tank | EAST | Changed tower duty 1 start setpoint to 60 %. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044996 | 0 | 0
2026-03 | 2026-03-18 | Mount Albert North Elevated Tank | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks - Regulatory sampling, Micro (W11672709) Regulatory samples taken @ 08:18 hrs. Grabs Talken @ 08:18 hrs. FCl: 1.34 mg/L TCl:1.54 mg/L Analyzer: FCl: 1.37 mg/L Equipment OOS: none Tower Draining Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-19 | Mount Albert North Elevated Tank | EAST | Under direction of OIC Patrick Fobert On site for PM's; - Portable generator test run - Chlorine analyzer maintenance - JHSC Health and safety inspections - Sump pit system inspection - Heat trace system inspection - Low temp alarm test - Comprehensive cleaning Ran portable generator for 15 mins, no issues observed Sump pit system working Heat trace system operational Low temp alarm triggered @ 10:09 hrs. Chlorine analyzer maintenance: Tower draining, pre grab verification; Grab @ 09:59 hrs. FCl: 1.33 mg/L Analyzer: FCl: 1.36 mg/L Start clean @ 10:03 hrs. Stop clean @ 10:33 hrs. Post clean Analyzer verification: Grab @ 11:02 hrs. FCl: 1.38 mg/L Analyzer: FCl: 1.37 mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00010126 | 0 | 0
2026-03 | 2026-03-09 | Stouffville Zone 1 Booster Pumping Station | EAST | Attended site for station check Collected grab samples and recorded results and observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.014644 | ML: above threshold (no LLM available) — 0.015 |  | 0.014644 | 0 | 0
2026-03 | 2026-03-13 | Stouffville Zone 1 Booster Pumping Station | EAST | On site to check station and equipment. Pump 2 is running in duty 1. Station readings entered in PWQ sheet. Reviewed trends, no issues. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070583 | 0 | 0
2026-03 | 2026-03-09 | Stouffville Zone 1 Booster Pumping Station | EAST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-02 | Stouffville Zone 1 Booster Pumping Station | EAST | Attended site for station check Collected grabs from the header, 14:13, in mg/L FCl 1.85; TCl 2.01 Inspected pumps, pipes, valves, equipment, all okay. Recorded observations in the shared station PWQ sheet | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049917 | 0 | 0
2026-03 | 2026-03-26 | Stouffville Zone 1 Booster Pumping Station | EAST | Changed the duty 1 start setpoint from 60% to 40% to deep cycle zone 1 ET. Changed the FCV flow setpoint from 25 to 50 l/s. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005452 | 0 | 0
2026-03 | 2026-03-19 | Stouffville Zone 1 Booster Pumping Station | EAST | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside PAC panel. ROC is informed and all Well and high lift pumps in ST area were in manual off before commencing the work This included STW3, STW12, STRS48 High Lift pumps, STPSMR Pumps, STPSTL pumps Historian hrbt alarm and Comm fail alarms were triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 09:18 AM to 10:30 AM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; alarms [control_system] | scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-17 | Stouffville Zone 1 Booster Pumping Station | EAST | Attended site for generator test run and silicate delivery Received sodium silicate. Levels: Start 20.98 cm Stop 89.37 cm Fuel Start 725 L Stop 692 L Hours Start 516.7 Stop 518.3 Run statistics Current 69.5 A Frequency 60 Hz Power 620 kW Speed 1800 RPM Coolant temp 180 F Exhaust temp 580 F Oil pressure 55 PSI Oil temp 230 F Loaded generator with well 3 and one pump at the pump station Reviewed station trends and checked equipment - okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00051268 | 0 | 0
2026-03 | 2026-03-20 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check Recorded observations and grabs in the shared PWQ sheet, 10:45 FCl grab 1.78 mg/L TCl grab 1.95 mg/L Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006386 | 0 | 0
2026-03 | 2026-03-24 | Stouffville Zone 1 Booster Pumping Station | EAST | Attended site for preventative maintenance Completed valve exercise Completed housekeeping | FLAG | stage2_low_confidence | 0.011585 | ML: above threshold (no LLM available) — 0.012 |  | 0.011585 | 0 | 0
2026-03 | 2026-03-23 | Stouffville Zone 1 Booster Pumping Station | EAST | On site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.01119 | ML: above threshold (no LLM available) — 0.011 |  | 0.01119 | 0 | 0
2026-03 | 2026-03-06 | Stouffville Zone 1 Booster Pumping Station | EAST | Attended site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.012228 | ML: above threshold (no LLM available) — 0.012 |  | 0.012228 | 0 | 0
2026-03 | 2026-03-30 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site to complete station check. Time: 14:08 Influent Total: Grab (mg/l) Analyzer (mg/l) Total: 1.40 1.47 Time: 14:10 SIM Free Grab (mg/l) Analyzer (mg/l) Free: 1.67 1.74 Time: 14:12 Effluent Free Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.56 Time: 14:14 Effluent Total Grab (mg/l) Analyzer (mg/l) Total: 2.28 2.34 verified analyzers with grabs. Checked station and trends. No OOS equipment. No outstanding alarms on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0019735 | 0 | 0
2026-03 | 2026-03-31 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for facility station check and equipment verifications Duty is active - STETTL Level - 60% Pumps 1 and 3 running in duty 1 - 110 L/s Chlorinator #2 dosing at 25%, 37 kg/day, DF = 59%, chlorine booster pump pressure - 245 psi Recorded data in PWQ sheets Verified chlorine analyzer readings: 09:06 to 09:16 (Grab/Analyzer mg/L) Influent TCL: 1.38 / 1.43 Effluent FCL: 1.93 / 1.96 Effluent TCL: 4.40 / 4.34 Sim FCL: 1.64 / 1.69 Reviewed trends, equipment OOS: None Station and equipment okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-06 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for facility station check and equipment verifications Duty is active - STETTL Level - 85% Pumps 1 and 2 running in D1, 110 L/s flow, Discharge pressure - 725 kpa Chlorinator #1 dosing at 32%, 39 kg/D, cl2 booster pump pressure ~ 245 psi (1690 kpa), DF = 77% Verification of chlorine analyzers @09:30 to 09:40 Grabs / Analyzers (mg/L) Influent TCL: 1.47 / 1.44 Effluent FCL: 1.94 / 1.99 Effluent TCL: 4.66 / 4.60 Simulated FCL: 1.69 / 1.74 No adjustments needed to analyzers Reagent levels ok Equipment OOS: None Reviewed trends, no abnormalities observed Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-09 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for facility station check and equipment verifications Duty is active - STETTL Level - 67% Manual stopped pumps @08:58, in order to start diesel generator. Duty rotated pumps - Placed P2 and 3 to D1, placed P1 to D2 Start Hours: 463.3 Start Fuel: 114 / 57 cm / 4817 / 2211 L Started generator @09:02, no issues with power transfer. Started pumps @09:08 to test station under generator power. Collected generator readings @09:35 Stopped pumps @10:30, switched generator back to auto Generator stopped @10:50 Stop Hours: 465.1 Stop Fuel: 4817 / 2216 L No issues with generator run or transfer test - See attached run sheet in Elog attachments for full data Verification of chlorine analyzers @10:35 to @10:43 Grabs / Analyzers (mg/L) Influent TCL: 1.53 / 1.48 Effluent FCL: 1.71 / 1.69 Simulated FCL: 1.77 / 1.69 No adjustments needed to analyzers Changed right bank chlorine cylinders with Jack Palmer - tested for leaks, no issues Reagent levels ok Equipment OOS: None Pumps back in auto @10:50 Reviewed trends, no abnormalities observed Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; leak [infrastructure] | oos [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-05 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for monthly maintenance PM's - Chlorine leak detector test, and halogen valve test, all okay - Chlorine scrubber inspection - JHSC Health and safety inspection - Critical air valve flush / inspect - Chlorine emergency kit inspection Alarms cleared, station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | emergency [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-04 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for facility station check, and equipment verifications: Duty is active - STETTL Level is 80% Pumps 1 and 2 running in D1 - 110 L/s Chlorinator #1 dosing at 32%, 39 kg/day, booster pump pressure ~ 240 psi Verification of chlorine analyzers from 08:52 to 09:02 (mg/L) Influent TCL: Grab: 1.45 / Analyzer: 1.46 Effluent FCL: Grab: 1.97 / Analyzer: 2.02 Effluent TCL: Grab: 4.71 / Analyzer: 4.67 Sim FCL: Grab: 1.66 / Analyzer: 1.74 No adjustments needed to AITs Deactivated duty @09:06 to allow operator more time to sample the Stouffville wells Reviewed trends, equipment OOS: None Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-12 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for monthly PMs. Informed ROC - Pump #4 (Jockey) monthly maintenance and test run @13:50 - Started pump #4 for monthly test run (Jockey pump) @13:55 - Observed that chlorinator #3 (The chlorinator tied to pump #4 was not dosing. Found that the discharge valve from the chlorinator was closed. Opened valve. Immediately stopped pump #4. @14:00 - Started backflushing to waste, added dechlor pucks to outfall @14:02 - Effluent free chlorine lolo alarm came in (Pumps are already off) @14:07 - Free chlorine residual analyzer is reading 1.86 mg/L. It did not take long to backflush as the jockey pump was only running at 30 L/s for less than 5 minutes. Stopped backflushing @14:10 @14:13 - restarted pump #4 with chlorinator #3 properly dosing now @15:00 - stopped pump #4, left in manual off as per normal Closed valves on chlorinator #3 as they were found before. Will inquire as to why they are closed. Station operation normal | FLAG | stage2_low_confidence | 0.072619 | ML: above threshold (no LLM available) — 0.073 | alarm [control_system] | 0.072619 | 0 | 0
2026-03 | 2026-03-02 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site to check station and equipment. Duty is active upon arrival. 11:40 chlorine residuals on grab/analyzer in mg/l: Influent Total: 1.52/1.48 Effluent Free: 1.97/1.97 Effluent Total: 4.65/4.74 (Standardized according to 3 grabs? average) Sim. Free: 1.70/1.68 Replaced reagents for Influent total and effluent free analyzers. Other station readings are in PWQ sheets. Reviewed trends, Station is under normal operation. Equipment OOS: none. | FLAG | stage2_low_confidence | 0.010233 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure] | 0.010233 | 0 | 0
2026-03 | 2026-03-11 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site to respond to a work order for exhaust fans 6 and 7 tripped. Found both VFDs faulted with some sort of previous under voltage event. Like Could've been caused by a power outage or even a generator test. Pushing the stop button on the VFD keypad reset the fault. | FLAG | stage2_low_confidence | 0.083187 | ML: above threshold (no LLM available) — 0.083 | fault [equipment_failure]; faulted [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; work order [maintenance_action] | 0.083187 | 0 | 0
2026-03 | 2026-03-13 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for station check and equipment verifications Duty is active on arrival - STETTL Level - 64% Pumps 2 and 3 running in Duty, 110 L/s, 690 kpa discharge pressure Chlorinator #1 dosing at 31%, 39 kg/day, DF = 75% Verified chlorine analyzer readings: (Grab/Analyzer mg/L) Influent TCL: 1.53 / 1.48 Effluent FCL: 2.15 / 2.08 Effluent TCL: 4.47 / 4.62 Sim FCL: 1.70 / 1.73 No adjustments needed to analyzers Installed new pressure gauge on pump #3 discharge Reviewed trends, equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-03 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Under direction of OIC Dan Zhou On site for; - Diesel receiving Tank 1; Start V: 2987 L Start cm: 73 cm Stop V: 4797 L Stop cm: 113 cm Tank 2; Start V: 2209 L Start cm: 57 cm Stop V: 2209 L Stop cm: 57 cm *note: tank 2 did not equalize or uptake fuel, LIT remained the same on tank. informed team lead Dan Zhou. *note 2: overfill device stopped fueling at 113 cm. Total received: 1832 L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00060223 | 0 | 0
2026-03 | 2026-03-11 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for station check and equipment verifications Duty is active - STETTL Level - 78% Pumps 2 and 3 running in D1 - 110 L/s Chlorinator #2 dosing at 25 %, 38 kg/day Verified chlorine analyzers with grab residuals (Grab/Analyzer mg/L) @14:30 to 14:40 Influent TCL: 1.55 / 1.49 Effluent FCL: 1.99 / 2.05 Effluent TCL: 4.51 / 4.49 Sim FCL: 1.75 / 1.77 No adjustments needed to analyzers Reviewed trends, equipment OOS: None Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-26 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site to check station and equipment. Duty is not active upon arrival. Switched pump duty so that P1 and P3 are in duty 1. P2 = duty 2. Reviewed trends, no issue. Chlorine train 1 is man/off. Further testing will be done next week. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065464 | 0 | 0
2026-03 | 2026-03-16 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for station check and equipment verifications Duty is not active - STETTL Level - 62% - Activated system duty @10:05 Pumps 2 and 3 running in Duty, 110 L/s, 692 kpa discharge pressure Chlorinator #1 dosing at 32%, 40 kg/day, DF = 77%, booster pump pressure ~ 240 psi Verified chlorine analyzer readings: (Grab/Analyzer mg/L) @10:25 to 10:37 Influent TCL: 1.52 / 1.46 Effluent FCL: 2.07 / 2.10 Effluent TCL: 4.45 / 4.78 Sim FCL: 1.71 / 1.68 Adjusted effluent TCL analyzer based on grab sample Reviewed trends, equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for facility station check and equipment verifications Duty is active - STETTL Level - 70% Pumps 2 and 3 running in D1 - 110 L/s, 694 kpa discharge pressure Chlorinator #1 dosing at 30%, DF = 75%, 38 kg/day, Chlorine booster pump pressure ~240 psi Recorded data in PWQ sheets Verified analyzer readings @12:25 - 12:35 (Grab / analyzer mg/L) Influent TCL: 1.48 / 1.45 Effluent FCL: 2.11 / 2.06 Effluent TCL: 4.40 / 4.51 Sim FCL: 1.73 / 1.68 No adjustments needed to analyzers Reviewed trends, equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-20 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Attended site for CMU5 W11749627 effluent and sim free chlorine lo and lo lo. Appears that chlorine cylinder bank 2 regulator failed to open during chlorine bank switchover. Initiated backflush at 11:38, at approximately 24 L/s, following dechlorination protocol. Effluent free chlorine grab collected at 11:48, 0.13 mg/L Replaced chlorine cylinder bank 1 and tested chlorine regulators on bank 1 and 2 Completed backflush at 13:08 for a total of 90 minutes. Estimated water loss is 129.6 cubic meters. Reported water loss in CMU5 W11749627 Verified chlorine analyzers, 13:42, in mg/L Effluent free chlorine - G 1.62; A 1.68 Sim free chlorine - G 1.62; 1.56 Placed station pumps 1-3 back in auto for supervised start up, 13:50 Station and equipment okay | FLAG | stage2_low_confidence | 0.023495 | ML: above threshold (no LLM available) — 0.023 | failed [equipment_failure] | 0.023495 | 0 | 0
2026-03 | 2026-03-16 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | Vibration readings | FLAG | stage2_low_confidence | 0.021831 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021831 | 0 | 0
2026-03 | 2026-03-25 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for station check and equipment verifications: Duty is active - STETTL level 68% Recorded data in PWQ sheets Pumps 2 and 3 running in D1 - 110 L/s, 707 kpa discharge pressure Verified chlorine analyzer readings - no adjustments needed. Tested chlorinator #1 line while running station, observed an audible noise coming from ejector #1. Suspect it may have been the cause of the effluent Lolo lockout yesterday. Left Chlorinator #1 OOS again. Chlorinator #2 is dosing in auto. Reviewed trends, equipment OOS: Chlorinator #1 Station operation okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; noise [equipment_failure] | oos [equipment_failure]; noise [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-24 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site responding to Effluent free chlorine Lolo and Simulated free Lolo alarms CMU5 #W11756650 Arrived on site @19:10. STETTL duty is active - tower level is 60% and floating at duty start. Took grab residuals on effluent Free Chlorine: @19:15 to 19:21 0.07, 0.09, 0.07 mg/L Analyzer reading: 0.04 mg/L 3 grab residuals indicate a free chlorine residual greater than 0.05 mg/L, therefore it is not a reportable incident. Also took grab residual on Simulated free analyzer @19:22 - 0.17 mg/L Free chlorine Started backflushing @19:25 at approximately 23 L/s. Added dechlor pucks to facility outfall. Reviewed trending - Observed that chlorinator #1 was dosing at the time of the incident, the same chlorinator that was running when a similar issue occured on 03/20/2026. Tested chlorinator #1 in local with chlorine booster pump running, and it seems to be functioning normally, vacuum and booster pump pressure are within regular range. Placed chlorinator / booster pump #1 to manual off and disabled duty rotation. Stopped backflushing @20:28 - Effluent free residual is 1.57 mg/L. Total water loss is approx 86.94 m3 after back flushing for 63 minutes. Effluent free residual grabs @20:36 Grabs: 1.76, 1.77 mg/L Analyzer: 1.70 mg/L @20:40 - Cleared alarms, and pumps 2 and 3 started in auto. Chlorinator #2 is dosing in Duty 1 Simulated free chlorine residual analyzer is recovering - reading 0.99 mg/L @21:08 Equipment OOS: Chlorinator #1 / Chlorine booster pump #1 Informed ROC site is back to normal operation Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system]; incident [safety] | oos [equipment_failure]; alarm [control_system]; alarms [control_system]; incident [safety] |  | 1 | 0
2026-03 | 2026-03-23 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | EAST | On site for station check and equipment verification, and to complete chlorine analyzer maintenance Tower level - 63%, and duty is not active. Placed pumps to manual off Completed chlorine analyzer maintenance @09:30 to @10:10. Completed on all analyzers, Influent TCL, Effluent FCL / TCL, Sim FCL Verified analyzer readings @10:20 to 10:30 (Grabs/Analyzer mg/L) Influent TCL: 1.45 / 1.47 Effluent FCL: 1.69 / 1.67 Effluent TCL: 2.46 / 2.47 Sim FCL: 1.73 / 1.71 Placed pumps to auto @10:33 - system duty is now active Recorded data in PWQ sheets Reviewed trends, equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-11 | Stouffville Zone 2 Elevated Tank | EAST | Attended site for sampling and station check Sampling MBHP W11656903 Sodium W11722238 Collected samples and verified free chlorine analyzer, 11:22, in mg/L FCl - G 1.69; A 1.64 TCl - G 1.90 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0027598 | 0 | 0
2026-03 | 2026-03-31 | Stouffville Zone 2 Elevated Tank | EAST | Attended site for station check and sampling Bac-T: W11705508 ANSCAN: W11705815 Verified free chlorine analyzer and collected samples while draining, 8:30, in mg/L FCl - G 1.63; A 1.64 TCl - G 1.86 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041013 | 0 | 0
2026-03 | 2026-03-04 | Stouffville Zone 2 Elevated Tank | EAST | On site for station check and sampling work orders MBDW - W11637348 HAA - W11692878 ANSCAN - W11637675 Collected samples and verified free chlorine analyzer while draining, 10:43, in mg/L Free chlorine: G 1.62; A 1.63 Total chlorine: G 1.81 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.0057928 | 0 | 0
2026-03 | 2026-03-10 | Stouffville Zone 2 Elevated Tank | EAST | ROC notified me about sodium exceedance at 11am. March 04, 2026 sample showed 62.3 mg/l sodium. 13:50 Verbal notification to YR Health Connection, Eugenia Huk 1-800-361-5653 x4, case# 4367316. 14:03 Verbal notification to SAC, Julian Aristizabal, AWQI171786. Will complete form 4444E later. | FLAG | stage1_keyword | 0.95 | Critical keyword match: exceedance [regulatory] | exceedance [regulatory] |  | 1 | 0
2026-03 | 2026-03-24 | Stouffville Zone 2 Elevated Tank | EAST | Attended site for preventative maintenance Completed housekeeping Completed chlorine analyzer maintenance Completed lo temp alarm test Completed heat trace inspection Completed sump pit inspection | FLAG | stage2_low_confidence | 0.012139 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.012139 | 0 | 0
2026-03 | 2026-03-19 | Stouffville Zone 2 Elevated Tank | EAST | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside NAC panel. ROC is informed and all Well and high lift pumps in ST area were in manual off before commencing the work This included STW3, STW12, STRS48 High Lift pumps, STPSMR Pumps, STPSTL pumps Comm fail alarm was triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 10:45 AM to 11:04 AM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; alarms [control_system] | scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | Stouffville Zone 2 Elevated Tank | EAST | On site for sampling W11672797 and station check Collected sample while draining, 9:08, and verified free chlorine analyzer, in mg/L FCl - G 1.58; A 1.57 TCl - G 1.77 Recorded observations in the shared PWQ sheet. Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048673 | 0 | 0
2026-03 | 2026-03-25 | Stouffville Zone 2 Elevated Tank | EAST | On site for station check and sampling W11690172 Collected sample while draining, 11:05, and verified free chlorine analyzer (mg/L) FCl - G 1.64; A 1.64 TCl - 1.76 Replaced chlorine analyzer reagents Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038749 | 0 | 0
2026-03 | 2026-03-04 | Stouffville Zone 1 Elevated Tank | EAST | On site for sampling W11637348 and station check Verified free chlorine analyzer and collected samples, 14:07, mg/L FCl G 1.34; A 1.32 TCl G 1.57 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043844 | 0 | 0
2026-03 | 2026-03-31 | Stouffville Zone 1 Elevated Tank | EAST | On site for station check and sampling BacT - W11705508 ANSCAN - W11705815 Collected samples while draining and verified free chlorine analyzer, 14:05, in mg/L FCl - G 1.29; A 1.24 TCl - 1.50 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031476 | 0 | 0
2026-03 | 2026-03-18 | Stouffville Zone 1 Elevated Tank | EAST | On site for station check and sampling W11672797 Collected sample, 14:45, and verified free chlorine analyzer (mg/L) FCl - G 1.40; A 1.43 TCl - G 1.60 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044816 | 0 | 0
2026-03 | 2026-03-19 | Stouffville Zone 1 Elevated Tank | EAST | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside NAC panel. ROC is informed and all Well and high lift pumps in ST area were in manual off before commencing the work This included STW3, STW12, STRS48 High Lift pumps, STPSMR Pumps, STPSTL pumps Comm fail alarms was triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 09:18 AM to 10:30 AM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; alarms [control_system] | scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | Markham PD6 Reservoir | EAST | On site for station check, and weekly micro sampling (W11705564) Reservoir level - 49% and on drain cycle Recorded station readings in PWQ sheets Verification of chlorine analyzer @10:05 Grab samples (mg/L) North cell: @10:05 FCL: 0.07 TCL: 1.51 South Cell: @10:10 FCL: 0.03 TCL: 1.56 Analyzer reading: 1.53 mg/L - no adjustment needed Collected micro sample @10:12 from North cell Collected in-house operational monitoring samples for ATP and Phosphorus Completed advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.34 mg/L Free NH: 0.07 mg/L Total NH: 0.34 mg/L NO2: 0.003 mg/L Temp: 3.7 C pH: 8.03 Reviewed trends, equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-25 | Stouffville Zone 1 Elevated Tank | EAST | On site for station check and sampling W11690172 Collected sample and verified free chlorine analyzer, 13:15, in mg/L FCl - G 1.29; A 1.30 TCl - G 1.50 Replaced free chlorine analyzer reagents Recorded observations in the shared PWQ sheet Reviewed station trends Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029221 | 0 | 0
2026-03 | 2026-03-11 | Markham PD6 Reservoir | EAST | On site for station check, and weekly micro sampling (W11656945) Reservoir level - 51% and on drain cycle Recorded station readings in PWQ sheets Verification of chlorine analyzer @08:50 Grab samples (mg/L) North cell: @08:48 FCL: 0.02 TCL: 1.50 South Cell: @08:53 FCL: 0.03 TCL: 1.56 Analyzer reading: 1.54 mg/L - no adjustment needed Collected micro sample @08:55 from North cell Collected in-house operational monitoring samples for ATP and Phosphorus Completed advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.27 mg/L Free NH3: 0.07 mg/L Total NH3: 0.32 mg/L NO2: 0.004 mg/L pH: 8.04 Temp: 4.1 C Reviewed trends, equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-05 | Markham PD6 Reservoir | EAST | On site for monthly maintenance: Informed ROC - High / Low water level alarms test - Reservoir is on a drain cycle, ROC requested Toronto to place their pumps man/off while testing. Tested low alarms @10:13, and high alarms @10:16. Placed all alarm setpoints back to original values after testing - Dehumidifier inspection and test - 2 tonne hoist inspection (3M) Upper Level - Overhead hoist inspection (3M) Lower level - JHSC Health and safety inspection - Building flood alarm test @10:38 - Sump pit inspections - Mainline valves exercises - MV100 to MV600 from 10:45 to 11:40. Ensured there was always a flow path for reservoir draining to system. No issues with valves - External venting screens inspections - Chlorine analyzer maintenance from 11:50 to 12:35 - Cleaned and primed analyzer. Verified analyzer reading after maintenance with grab residual @12:30 Grab: 1.48 mg/L / Analyzer: 1.52 mg/L Alarms cleared, informed ROC, station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | Markham PD6 Reservoir | EAST | On site for station check and weekly micro sampling (W11637404) Reservoir level - 60% and draining Reviewed trends - no concerns observed Recorded data in PWQ sheets Grab samples (mg/L) North cell @09:43 FCL: 0.04 TCL: 1.45 South Cell @09:49 FCL: 0.03 TCL: 1.53 Analyzer: 1.51 mg/L Collected micro sample from North cell @09:53 Collected in-house operational monitoring samples for ATP / Phosphorus Advanced Monitoring using SL1000 / Nitrification control monitoring: Mono: 1.21 mg/L Free / Total NH3: 0.10 / 0.34 mg/L NO2: 0.004 mg/L pH: 8.03 Temp: 4.8 C Station operation normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0010598 | 0 | 0
2026-03 | 2026-03-18 | Markham PD6 Reservoir | EAST | On site for station check, and weekly micro sampling (W11672839) Reservoir level - 47% and on drain cycle Recorded station readings in PWQ sheets Verification of chlorine analyzer @08:45 Grab samples (mg/L) North cell: @08:45 FCL: 0.03 TCL: 1.48 South Cell: @08:49 FCL: 0.02 TCL: 1.53 Analyzer reading: 1.51 mg/L - no adjustment needed Collected micro sample @08:52 from North cell Collected in-house operational monitoring samples for ATP and Phosphorus Completed advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.25 mg/L Free NH3: 0.10 mg/L Total NH3: 0.35 mg/L NO2: 0.00 mg/L Temp: 4.5 C Reviewed trends, equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-17 | Markham PD6 Reservoir | EAST | Under direction of OIC Joe Mazza. Notified ROC of the work. Performed battery maintenance on UPS in the PAC panel. Charged new batteries and tested drawdown. Applied new service sticker. No operations affected by this work. | FLAG | stage2_low_confidence | 0.014542 | ML: above threshold (no LLM available) — 0.015 |  | 0.014542 | 0 | 0
2026-03 | 2026-03-25 | Markham PD6 Reservoir | EAST | On site for station check, and weekly micro sampling (W11690214) Reservoir level - 43% and on drain cycle Recorded station readings in PWQ sheets Verification of chlorine analyzer @09:40 Grab samples (mg/L) North cell: @09:43 FCL: 0.06 TCL: 1.48 South Cell: @09:40 FCL: 0.05 TCL: 1.60 Analyzer reading: 1.52 mg/L - no adjustment needed Collected micro sample @09:45 from North cell Collected in-house operational monitoring samples for ATP and Phosphorus Completed advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.31 mg/L NO2: 0.003 mg/L Temp: 3.8 C pH: 8.06 Reviewed trends, equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-30 | Keswick Water Treatment Plant | CENTRAL | This is an entry for March/29/2026. Received call from ROC at 08:07 about filter 2 back wash interlocked and OOS. When signed into SCADA found that both filter 1 and 2 were going to have a backwash at the same time. Also found that low lift pump 3 was having un-commanded stops, so put pump 3 to manual off at 08:24. Filter 2 will not be able to do its backwash till the backwash tank level drops down low enough for it to start. Will inform ROC of what is happening. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | Keswick Water Treatment Plant | CENTRAL | Completed filter performance check: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049915 | 0 | 0
2026-03 | 2026-03-31 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet Grab: free=1.71mg/L total=1.98mg/L@12:00 Analyzer: free=1.69mg/L total=1.90mg/L -Changed low lift free reagents - OK -Collected weekly BacT sample YD #W11705592, weekly algae sample YD #W11705322, monthly THM sample YD #W11705294 & GLIP sample -Calibrated low lift pH probe due to high pH | FLAG | stage2_low_confidence | 0.015371 | ML: above threshold (no LLM available) — 0.015 |  | 0.015371 | 0 | 0
2026-03 | 2026-03-04 | Keswick Water Treatment Plant | CENTRAL | 11:11 remote Filter performance check. Both filters are at 100% performance. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047264 | 0 | 0
2026-03 | 2026-03-12 | Keswick Water Treatment Plant | CENTRAL | Received call from ROC regarding low CL2 influent. Plant not running. Checked trends, looks like CL2 influent has been slowly dropping over the past run cycle, now currently reading 1.09mg/l and triggering low alarm. Initiated Backwash on Filter #1 as it was getting close to backwash, this way, can draw down clearwell and refill with higher chlorinated water. Increased Post CL2 dosage factor from 142% to 155%. Influent increased to 1.20mg/l while filter was draining for backwash. Will inform Central crew this morning, may look at increasing PACL dosage due to increased raw turbidity and will monitor/adjust POST CL2 dosage depending on influent CL2 levels. | FLAG | stage2_low_confidence | 0.054976 | ML: above threshold (no LLM available) — 0.055 | not running [equipment_failure]; alarm [control_system] | 0.054976 | 0 | 0
2026-03 | 2026-03-05 | Keswick Water Treatment Plant | CENTRAL | Remotely reviewed filter performance. Both filters 100% and ok. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053042 | 0 | 0
2026-03 | 2026-03-12 | Keswick Water Treatment Plant | CENTRAL | Onsite to receive chlorine cylinder delivery. Lo influent chlorine alarm triggered with analyzer reading 1.09 mg/l. Raw turbidity readings erratic. Found raw water analyzer flow too low and corrected. Tested post injection chlorine system as duty started and found no issues with regulator or chlorinators. 14:45 Took influent clear well grab: 1.35. Analyzer 1.31 and climbing. No issues found. | FLAG | stage2_low_confidence | 0.019251 | ML: above threshold (no LLM available) — 0.019 | alarm [control_system] | 0.019251 | 0 | 0
2026-03 | 2026-03-13 | Keswick Water Treatment Plant | CENTRAL | Filter performance reviewed, both 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043681 | 0 | 0
2026-03 | 2026-03-03 | Keswick Water Treatment Plant | CENTRAL | filter performance checked, both 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043503 | 0 | 0
2026-03 | 2026-03-13 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Performed filter performance review - 100% | FLAG | stage2_low_confidence | 0.010858 | ML: above threshold (no LLM available) — 0.011 |  | 0.010858 | 0 | 0
2026-03 | 2026-03-11 | Keswick Water Treatment Plant | CENTRAL | Reviewed filter performance both 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043484 | 0 | 0
2026-03 | 2026-03-10 | Keswick Water Treatment Plant | CENTRAL | -Collected GAC sample -Changed chlorine cylinder -Put filter back to service - refilled filter 1 to 35cm - set high wash time from 420s to 180 and backwashed filter 1 to re-stratify media - during sampling, there is sample to turbidimeter which caused a high turbidimeter reading=0.465NTU and filter 1's effluent valve was always closed - after backwashing, run filter to waste until turbidity came below 0.1NTU | FLAG | stage2_low_confidence | 0.038819 | ML: above threshold (no LLM available) — 0.039 |  | 0.038819 | 0 | 0
2026-03 | 2026-03-02 | Keswick Water Treatment Plant | CENTRAL | Under direction of OIC (Ben H) Station and equipment check Completed labs, no issues Plant not running during readings Filter performance review via scada both F1 and F2 100% Ops normal | FLAG | stage2_low_confidence | 0.022733 | ML: above threshold (no LLM available) — 0.023 | not running [equipment_failure]; scada [control_system] | 0.022733 | 0 | 0
2026-03 | 2026-03-02 | Keswick Water Treatment Plant | CENTRAL | Test backflow preventer Passed | FLAG | stage2_low_confidence | 0.010526 | ML: above threshold (no LLM available) — 0.011 |  | 0.010526 | 0 | 0
2026-03 | 2026-03-02 | Keswick Water Treatment Plant | CENTRAL | Onsite to look for CO2 leak, found 2 small leaks within the CO2 valve cabinet. Checked filter performance both filters 100% | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Reviewed filter performance -Collected weekly BacT sample YD #W11656973 & GLIP samples -Responded lolo CO2 adjusted pH - reviewed trends and noticed pH drop was correlated to water temperature - increased sample flow to temp probe | FLAG | stage2_low_confidence | 0.019019 | ML: above threshold (no LLM available) — 0.019 |  | 0.019019 | 0 | 0
2026-03 | 2026-03-04 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet Grab: free=1.65mg/L total=1.97mg/L@11:40 Analyzer: free=1.66mg/L total=2.03mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11637432, monthly sample YD #W11637633, 11637162, & GLIP samples | FLAG | stage2_low_confidence | 0.012717 | ML: above threshold (no LLM available) — 0.013 |  | 0.012717 | 0 | 0
2026-03 | 2026-03-05 | Keswick Water Treatment Plant | CENTRAL | Under direction of oic (Ben H) onsite to complete monthly maximo workorders Change chlorine cylinder with JZ (Post chlorination right side) Station ops normal | FLAG | stage2_low_confidence | 0.015742 | ML: above threshold (no LLM available) — 0.016 |  | 0.015742 | 0 | 0
2026-03 | 2026-03-12 | Keswick Water Treatment Plant | CENTRAL | Informed TL Ben Hess of changes made to Chlorine and PACL setpoints. Was recommended by Ben to increase Settling tank valve open waste time from 2 minutes back to 4 minutes. Made that adjustment. Adjusted Pre chlorine dosing from 82 to 86%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053768 | 0 | 0
2026-03 | 2026-03-06 | Keswick Water Treatment Plant | CENTRAL | 11:30 reviewed filter performance. Both filters 100%. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042428 | 0 | 0
2026-03 | 2026-03-09 | Keswick Water Treatment Plant | CENTRAL | Under direction of oic (Ben H), onsite to complete station check PLant not running at time of check Took grabs from treated @ 10:10 am Total: 1.98 mg/l Free: 1.75 mg/l All other readings on PD sheets Topped up PACL day tank Chemicals/reagents ok Informed ROC (Angelica C) With the assistance of Ben H performed manual backwash of filter 1, leaving drained and OOS for media sampling tomorrow | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; not running [equipment_failure] | oos [equipment_failure]; not running [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-05 | Keswick Water Treatment Plant | CENTRAL | Attended SCADA in response to a call from RO Christian Van Beek regarding a CO2 dosing interruption, filter 1 and 2 low level and low settled water conduit level. Checked raw water pH, and low lift pumps. Monitored filter and conduit level top up. Reset all alarms. Achieving desired filter turbidity. Station and equipment okay. Back in normal operation. | FLAG | stage2_low_confidence | 0.011619 | ML: above threshold (no LLM available) — 0.012 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.011619 | 0 | 0
2026-03 | 2026-03-11 | Keswick Water Treatment Plant | CENTRAL | Received call from ROC for High Settling Water turbidity. Plant running at the time. Logged into SCADA, settled water turbidity increasing as well as raw turbidity. Could be due to increased flooding/runoff from rain. Monitored Filter effluent turbidity, head loss and runtime. No issues, filter turbidity below 0.100ntu. Able to filter out higher turbidity. Will keep plant running as duty shut off will be soon. | FLAG | stage2_low_confidence | 0.02488 | ML: above threshold (no LLM available) — 0.025 | flood [critical]; scada [control_system] | 0.02488 | 0 | 0
2026-03 | 2026-03-16 | Keswick Water Treatment Plant | CENTRAL | Checked filter performance, both 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043477 | 0 | 0
2026-03 | 2026-03-17 | Keswick Water Treatment Plant | CENTRAL | Checked filter performance both 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043281 | 0 | 0
2026-03 | 2026-03-25 | Keswick Water Treatment Plant | CENTRAL | Completed filter performance check: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049915 | 0 | 0
2026-03 | 2026-03-24 | Keswick Water Treatment Plant | CENTRAL | -Received CO2 delivery -Adjusted raw sample flow -Decreased post chlorine dosage from 155 to 150 and PACL dosage from 15mg/L to 14mg/L due to improved raw water quality | FLAG | stage2_low_confidence | 0.012603 | ML: above threshold (no LLM available) — 0.013 |  | 0.012603 | 0 | 0
2026-03 | 2026-03-26 | Keswick Water Treatment Plant | CENTRAL | Attending site to check low flow to Raw Water Turbidimeter (W11761664). Replaced flow sensor. Checked existing sensor and found rubber debris blocking flow sensor impeller. ROC was notified before and after maintenance activities. | FLAG | stage2_low_confidence | 0.04484 | ML: above threshold (no LLM available) — 0.045 | impeller [equipment_failure] | 0.04484 | 0 | 0
2026-03 | 2026-03-25 | Keswick Water Treatment Plant | CENTRAL | -Lowered post chlorine dosage from 150 to 145 due to high clearwell influent free -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11690242 | FLAG | stage2_low_confidence | 0.013906 | ML: above threshold (no LLM available) — 0.014 |  | 0.013906 | 0 | 0
2026-03 | 2026-03-24 | Keswick Water Treatment Plant | CENTRAL | 07:34 Remotely reviewed turbidity performance. Both filters at 100%. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037908 | 0 | 0
2026-03 | 2026-03-17 | Keswick Water Treatment Plant | CENTRAL | -Responded PACL P1 & Low Lift P3 uncommand stop - PACL P1 & Low Lift P3 restarted in auto duty 1 as of 1530 - reviewed trends - PACL day tank level is reclining & low lift flow meter is reading @ 70L/s - Both PACL P1 & Low Lift P3 were running normally in this cycle - I was assuming a power blip caused the uncommand stop alarm since the two alarm came in at the same time | FLAG | stage2_low_confidence | 0.020189 | ML: above threshold (no LLM available) — 0.02 | alarm [control_system] | 0.020189 | 0 | 0
2026-03 | 2026-03-16 | Keswick Water Treatment Plant | CENTRAL | ROC called for fluoride residual lolo while plant is running. Instructed ROC to switch fluoride duty and monitor. | FLAG | stage2_low_confidence | 0.0081418 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081418 | 0 | 0
2026-03 | 2026-03-18 | Keswick Water Treatment Plant | CENTRAL | 12:05 completed filter turbidity performance review remotely. Both filters at 100%. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048992 | 0 | 0
2026-03 | 2026-03-26 | Keswick Water Treatment Plant | CENTRAL | Completed filter performance check: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049915 | 0 | 0
2026-03 | 2026-03-23 | Keswick Water Treatment Plant | CENTRAL | -on site to install pacl day tank containment flood alarm. Installed and tested wiring back to pac panel. Let Matt S know our landing spot. Under direction of oic. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; containment [safety] | flood [critical]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-23 | Keswick Water Treatment Plant | CENTRAL | 15:04 Remotely reviewed filter turbidity performance. Both filters running at 100%. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048859 | 0 | 0
2026-03 | 2026-03-20 | Keswick Water Treatment Plant | CENTRAL | Check drip oiler Cleaned drip oiler wiped dry and clean re installed and filled | FLAG | stage2_low_confidence | 0.020971 | ML: above threshold (no LLM available) — 0.021 | drip [infrastructure] | 0.020971 | 0 | 0
2026-03 | 2026-03-27 | Keswick Water Treatment Plant | CENTRAL | -Tested high lift pump 2's flow control valve -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.010983 | ML: above threshold (no LLM available) — 0.011 |  | 0.010983 | 0 | 0
2026-03 | 2026-03-18 | Keswick Water Treatment Plant | CENTRAL | Under direction of oic JZ, station and equipment check Take weekly bacT sample and grabs @ 11:40 am (plant running) Treated Total: 1.98 mg/l Treated Free: 1.70 mg/l All other readings on PD sheets Topped up chemicals as needed Completed monthly maximo workorders Informed ROC (Christian V) of ongoings CL2 Leak alarm test complete Analyzer (fluoride) maintenance complete, verified grabs (PD sheets) Ops normal | FLAG | stage2_low_confidence | 0.013273 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; leak [infrastructure] | 0.013273 | 0 | 0
2026-03 | 2026-03-20 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Changed chlorine cylinder -Changed clear well free reagents -Low lift turbidimeter fault alarm outstanding - flow sensor faulted - A CMP already in - I will email instrumentation team again today | FLAG | stage2_low_confidence | 0.043563 | ML: above threshold (no LLM available) — 0.044 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] | 0.043563 | 0 | 0
2026-03 | 2026-03-27 | Keswick Water Treatment Plant | CENTRAL | Completed filter performance check: filter 1- 100%, filter 2- 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049915 | 0 | 0
2026-03 | 2026-03-20 | Keswick Water Treatment Plant | CENTRAL | 09:00 remotely checked Filter turbidity performance. Both filters at 100%. No issues found. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046873 | 0 | 0
2026-03 | 2026-03-19 | Keswick Water Treatment Plant | CENTRAL | 10:26 completed filter turbidity performance review remotely. Both filters at 100%. No issues fou | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048328 | 0 | 0
2026-03 | 2026-03-23 | Keswick Water Treatment Plant | CENTRAL | Attending site to check flow sensor on Raw Water Turbidimeter (W11726557). Flowmeter was fouled and replaced. ROC was notified before and after maintenance activities. Associated alarms were cleared. | FLAG | stage2_low_confidence | 0.04423 | ML: above threshold (no LLM available) — 0.044 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.04423 | 0 | 0
2026-03 | 2026-03-16 | Keswick Water Treatment Plant | CENTRAL | Under direction of OIC completed station check and labs Topped up all chemicals Troubleshoot fluoride pump, (air locked) Adjusted flow to RAW turbidimeter, was reading false too high Change chlorine cylinder w/ JZ (pre) Completed maximo workorders OPs normal | FLAG | stage2_low_confidence | 0.012109 | ML: above threshold (no LLM available) — 0.012 |  | 0.012109 | 0 | 0
2026-03 | 2026-03-31 | Sutton Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC Samples. W11706392 Weekly Bac-t Sample. W11706364 VOC Samples. Time: 10:00 Grab (mg/l) Analyzer (mg/l) Free: 1.18 1.13 Total: 1.49 Entered data into PWQ sheet. Verified analyzer on site with grabs. Checked site and trends. No OOS equipment on site. No outstanding alarms. CL-17 reagents have been changed on site. | FLAG | stage2_low_confidence | 0.0094266 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0094266 | 0 | 0
2026-03 | 2026-03-06 | Keswick Water Treatment Plant | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Changed filter top free reagents | FLAG | stage2_low_confidence | 0.014384 | ML: above threshold (no LLM available) — 0.014 |  | 0.014384 | 0 | 0
2026-03 | 2026-03-12 | Keswick Water Treatment Plant | CENTRAL | Reviewed filter performance both 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043484 | 0 | 0
2026-03 | 2026-03-09 | Keswick Water Treatment Plant | CENTRAL | Remotely reviewed fitter performance. Both filters are 100%. Filter 1 placed oos for media sampling. Adjusted flow from 80 to 40 L/s. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-10 | Keswick Water Treatment Plant | CENTRAL | 08:42 Remote filter turbidity performance review. Both filters at 100%. Filter 1 is oos and drained for media sampling. No issues found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-14 | Keswick Water Treatment Plant | CENTRAL | Increased PACL dosage from 12 to 15mg/l due to high settling tank and raw turbidity. Reduced flow rate in filters from 40L/S to 30L/S and High Lift flow rate from 80L/S to 60L/S. Will continue to monitor plant operation. | FLAG | stage2_low_confidence | 0.010209 | ML: above threshold (no LLM available) — 0.01 |  | 0.010209 | 0 | 0
2026-03 | 2026-03-03 | Keswick Water Treatment Plant | CENTRAL | Under direction of oic Ben H onsite to complete monthly maximo workorders Informed ROC (Christian V) of ongoings New diesel generator test run on building power Start Hours: 43 hrs 48 min Stop Hours: 45 hrs 9 min With plant "off" Settled water analyzer and turbidimeter cleaned @ 10:00 am Cleaned Filter 1 and 2 Turbidimeters @ 10:30 am Cleaned Raw water analyzers and turbidimeter @ 11:30 am Cleaned Clearwell analyzer @ 1:00 pm ack/reset all alarms and placed plant back to auto Ops normal | FLAG | stage2_low_confidence | 0.011711 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.011711 | 0 | 0
2026-03 | 2026-03-04 | Sutton Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. Collecting monthly VOC Samples. W11638376 Weekly Bac-t Sample. W11638348 Monthly VOC Samples. Time: 08:35 Grab (mg/l) Analyzer (mg/l) Free: 1.29 1.24 Total: 1.60 Verified analyzer on site. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. | FLAG | stage2_low_confidence | 0.010604 | ML: above threshold (no LLM available) — 0.011 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.010604 | 0 | 0
2026-03 | 2026-03-03 | Sutton Elevated Tank | EAST | On site to complete following work orders: W11635386 JHSC Inspection W11654557 Chlorine Analyzer Maintenance W11656475 Inlet/Outlet Heat Trace Insp. W11656484 Sump Pit System Inspection. W11656497 Low Temp Alarm Test W11660678 Cleaning W11656718 Portable Gas Generator Test Verifying chlorine analyzer with grabs after completing maintenance. Time: 10:25 Grab (mg/l) Analyzer (mg/l) Free: 1.30 1.25 Calibrated chlorine pocket colorimetre it passed. No issues with analyzer maintenance. No issues with work orders on site. Any changes in trends are due to work orders being completed. | FLAG | stage2_low_confidence | 0.013457 | ML: above threshold (no LLM available) — 0.013 | work order [maintenance_action]; alarm [control_system] | 0.013457 | 0 | 0
2026-03 | 2026-03-18 | Sutton Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11673527 Weekly Bac-t Sample. Time: 08:36 Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.20 Total: 1.52 Verified analyzer with grabs. Checked site and trends. No outstanding alarms on site. No OOS equipment. | FLAG | stage2_low_confidence | 0.010958 | ML: above threshold (no LLM available) — 0.011 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.010958 | 0 | 0
2026-03 | 2026-03-11 | Sutton Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11657667 Weekly Bac-t Sample. Time: Grab (mg/l) Analyzer (mg/l) Free: Total: At 08:50 shut down Sutton ET duty tower is currently at 8.32m duty shuts down at 8.50m. Verified analyzer with grabs. Entered data into PWQ sheet. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. | FLAG | stage2_low_confidence | 0.012412 | ML: above threshold (no LLM available) — 0.012 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.012412 | 0 | 0
2026-03 | 2026-03-25 | Sutton Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11690826 Weekly Bac-t Sample. Time: 09:10 Grab (mg/l) Analyzer (mg/l) Free: 1.23 1.16 Total: 1.52 Verified analyzer with grabs all ol. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. | FLAG | stage2_low_confidence | 0.012049 | ML: above threshold (no LLM available) — 0.012 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.012049 | 0 | 0
2026-03 | 2026-03-25 | Sutton Elevated Tank | EAST | Deactivate Sutton PRV duty to stagger duty activation together with plant duty. Plant duty is off right now and KSTKWP = 62%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054586 | 0 | 0
2026-03 | 2026-03-25 | Sutton Elevated Tank | EAST | Deactivated Sutton PRV duty in order to test re-chlor logic at KSETDP. Re-activated duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060685 | 0 | 0
2026-03 | 2026-03-30 | Keswick Deer Park Elevated Tank | EAST | On site for station check/analyzer verification and to verify the function of CL2 Dosing system. 09:45hrs: Adjusted Pre-Injection Cl2 Analyzer Free from 1.36mg/l to 1.53mg/l based on multiple Cl2 grab residuals. 09:55hrs: Adjusted Post-Injection Cl2 Analyzer Free from 1.40mg/l to 1.71mg/l based on multiple Cl2 grab residuals. 10:10hrs: Adjusted Outlet Cl2 Analyzer Free from 1.40mg/l to 1.71mg/l based on multiple Cl2 grab residuals. Activated GWTP @ 10:15hrs to observe Chlorine dosing system. Conducted zero point calibration on Pre-Injection and Post injection Cl2 Analyzers due to drifting when inlet flow was registering. Informed ROC of the work and to disregard chlorination alarms during this time. Conducted additional CL2 grab residuals to ensure accuracy of the CL2 Analyzers. Adjusted Chlorine dosing target setpoint from 1.80mg/l to 1.50mg/l. Monitored Chlorination system while tower was filling, did not see any issues, system seems to be dosing accurately. Will continue to monitor. | FLAG | stage2_low_confidence | 0.11918 | ML: above threshold (no LLM available) — 0.119 | alarm [control_system]; alarms [control_system] | 0.11918 | 0 | 0
2026-03 | 2026-03-31 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t sample. Collecting VOC sample. Time: 10:45 Pre-injection Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.67 Time: 10:48 Post-injection Grab (mg/l) Analyzer (mg/l) Free: 1.64 1.71 Total: 1.91 1.83 Time: 10:55 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.55 1.60 Total: 1.95 2.00 Verified analyzers on site with grabs. Checked site and trends. Entered data into PWQ sheet. No OOS equipment on site. No outstanding alarms on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.002524 | 0 | 0
2026-03 | 2026-03-05 | Keswick Deer Park Elevated Tank | EAST | Repair leak on chlorine injection line | FLAG | stage2_low_confidence | 0.037884 | ML: above threshold (no LLM available) — 0.038 | repair [maintenance_action]; leak [infrastructure] | 0.037884 | 0 | 0
2026-03 | 2026-03-02 | Keswick Deer Park Elevated Tank | EAST | Back on site to verify the post and pre-injection analyzers with grabs. Time: 12:39 Pre-Injection Grab (mg/l) Analyzer (mg/l) Free: 0.38 0.39 Time: 12:43 Post-Injection Grab (mg/l) Analyzer (mg/l) Free: 0.35 0.33 Total: 0.65 0.59 Verified analyzers with grabs. Analyzers are reading correctly on site. All valves inside the valve gallery are reading in the correct position. At 13:02 started opening the drain valve on the inlet riser to bring up the Pre and Post-injection readings. Taking grabs to verify Pre and Post Injection readings. Time: 13:18 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.11 1.16 Total: 1.45 1.75-1.45 Time: 13:21 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 0.50 0.53 After multiple grabs adjusted the post injection total from a 1.75mg/l to a 1.45mg/l at 13:18. Closed the inlet drain at 13:22. Wasted 9.6m3 sodium thiosulphate was at the outfall. Called Joe Mazza at 13:24 to activate duty at the GWTP to make sure the altitude valve here on site will open. Altitude valve is operating normally and opening with duty active. Analyzers are reading correctly on site. Time: 13:55 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 0.95 1.37-0.95After multiple grabs adjusted the pre injection free from a 1.37mg/l to a 0.95mg/l at 13:57. Time: 14:06 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.02 1.13-1.02 Total: 1.30. 1.50-1.30 after multiple grabs adjusted the post injection free from 1.13mg/l to 1.02mg/l. Also adjusted the total from a 1.50mg/l to a 1.30mg/l at 14:07 Time: 14:10 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.01 0.98 Total: 1.30 1.36 Before leaving site analyzers have been checked and adjusted properly while on the fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070843 | 0 | 0
2026-03 | 2026-03-13 | Keswick Deer Park Elevated Tank | EAST | On site for station check. Collected Cl2 grab residuals on: Inlet tap: FCL: 1.01mg/l Analyzer FCL: 1.03mg/l TCL: 1.35mg/l Analyzer TCL: 1.41mg/l Outlet tap: FCL: 0.96mg/l Analyzer FCL: 1.38mg/l TCL: 0.98mg/l Analyzer TCL: 1.42mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-12 | Keswick Deer Park Elevated Tank | EAST | 9:44 On site to assist Chris I and Tyler S to isolate and inlet pipe in order to modify the chlorine injection line. Tower is on a draining cycle. 11:20 maintenance needs parts for the injection line. Reopened inlet pipe. Rechlor system remains isolated and OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-04 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Collecting Weekly Bac-t Sample. Collecting VOC Samples. Collecting Q1 Samples. W11638390 Weekly Bac-t Sample W11638362 VOC Samples. W11673942 Q1 Samples. Time: 09:50 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.31 1.26 Time: 09:53 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.29 1.36 Total: 1.76 1.75 Time: 09:55 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.84 0.85 Total: 1.27 1.21 Verified analyzers on site. Checked station and trends. No outstanding alarms. No OOS equipment. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0018903 | 0 | 0
2026-03 | 2026-03-02 | Keswick Deer Park Elevated Tank | EAST | On site to see if ET can go on line. Will be flushing the water to waste to see if residual will come up. Sodium thiosulphate is in place for wasting. Started flushing to waste at 09:30 at 11L/s. Taking grab sample to verify analyzer is reading correctly. Time: 09:35 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.96 1.00 Total: 1.35 1.36 After taking grabs the tower can be put online. Flushed 9.9m3 to waste. Outlet is fully open on both the riser and the main. Tightened down the packing for the drain valve to stop the leaking from happening. Taking one last grab before leaving site. Time: 10:10 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.05 1.00 Total: 1.36 1.48 After multiple grabs were taken adjusted the total analyzer on the outlet from a 1.48mg/l to a 1.36mg/l at 10:16. Due to the fact that the boost has not been tested yet. The alarms for the post-injection can be disregarded. | FLAG | stage2_low_confidence | 0.071049 | ML: above threshold (no LLM available) — 0.071 | oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | 0.071049 | 0 | 0
2026-03 | 2026-03-02 | Keswick Deer Park Elevated Tank | EAST | Deactivated alarm for post-injection combined chlorine residual LOLO Alarm. | FLAG | stage2_low_confidence | 0.0074961 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0074961 | 0 | 0
2026-03 | 2026-03-06 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. On site to commission chlorine system. Time: 09:30 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.19 1.14 Time: 09:32 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.29 1.21 Total: 1.68 1.74 Time: 09:35 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.94 1.02 Total: 1.41 1.48 Verified analyzers with grabs all ok. Checked site and trends. Entered data into PWQ sheet. No outstanding alarms. Chlorine system OOS work being done on it to bring it back on line. At 10:00 called ROC about work being completed on site. After testing chlorine injection point system with the booster pump. Found it to be unsafe team lead will be creating a work order for maintenance to redo the chlorine injection system. Alarms have been cleared. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; unsafe [safety] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; unsafe [safety] |  | 1 | 0
2026-03 | 2026-03-03 | Keswick Deer Park Elevated Tank | EAST | On site to test the booster pumps and chlorine system to see if it is ready to come online. After opening the valves and testing the booster pump found a leak on the 1 1/2? line. Informed team lead and work order is being created for maintenance to take a look. | FLAG | stage2_low_confidence | 0.145 | ML: above threshold (no LLM available) — 0.145 | oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure] | 0.145 | 0 | 0
2026-03 | 2026-03-09 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Time: 10:50 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.21 1.21 Time: 10:55 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.26 1.21 Total: 1.69 1.66 Time: 11:00 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.01 1.02 Total: 1.49 1.54 Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Checked station and trends. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0027944 | 0 | 0
2026-03 | 2026-03-18 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11673541 Weekly Bac-t Sample. Time: 09:46 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.17 1.04-1.17 After multiple grabs were taken adjusted the Pre Injection from a 1.04mg/l to 1.17mg/l at 09:47 Time: 09:50 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.02 1.04 Total: 1.52 1.44 Time: 09:53 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.01 0.95 Total: 1.32 1.31 Verified analyzers with grabs. Checked station and trends. Chlorine system OOS due to PCS work needing to be done. No outstanding alarms. Entered data into PWQ sheet. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Time: 10:45 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.18. 1.15 Time: 11:00 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.16 1.14 Total: 1.73 2.16-1.73 after multiple grabs adjusted the treated total from a 2.16mg/l to a 1.73mg/l at 11:31. Time: 11:30 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.14 1.44 -1.14 Total: 1.60 1.65 After multiple grabs adjusted the treated free on the outlet analyzer from 1.44mg/l to 1.14mg/l at 11:35. Verified analyzers with grabs. Cleared outstanding hihi total alarm on post chlorine analyzer. No OOS equipment on site. Electrician Dan Boate on site to confirm heat trace system is working correctly. | FLAG | stage2_low_confidence | 0.0080605 | ML: above threshold (no LLM available) — 0.008 | oos [equipment_failure]; alarm [control_system] | 0.0080605 | 0 | 0
2026-03 | 2026-03-16 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Time: 10:40 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.00 0.94 Time: 10:42 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 0.97 1.04 Total: 1.36 1.31 Time: 10:50 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.91 0.91 Total: 1.35 1.30 Verified analyzers with grabs all ok. No outstanding alarms on site. Entered data into PWQ sheet. Checked site and trends. Chlorine system currently OOS until it is tested properly. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | Keswick Deer Park Elevated Tank | EAST | On site to test and verify proper operation of heat trace system. | FLAG | stage2_low_confidence | 0.014021 | ML: above threshold (no LLM available) — 0.014 |  | 0.014021 | 0 | 0
2026-03 | 2026-03-27 | Keswick Deer Park Elevated Tank | EAST | Made following changes with in training with Chris Scott: Chlorinator 1 and 2 dose factor to 100%. Chlorine setpoint from 1.5 to 1.8 mg/l Loop update rate from 60s to 180s. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046948 | 0 | 0
2026-03 | 2026-03-23 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Completing following work orders: Portable generator test, JHSC inspection. Time: 11:30 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.40 1.32 Time: 11:35 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.23 1.22 Total: 1.50 1.54 Time: 11:42 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.16 1.15 Total: 1.41 1.47 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. Chlorine system currently OOS due to commissioning issues. Entered data into PWQ sheet. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | Keswick Deer Park Elevated Tank | EAST | On site to complete chlorine system commissioning with PCS. Opening up all valves for the chlorine booster pump and putting pump into auto. Chlorine system is currently in auto and ready for test. All alarms due to chlorine are due to the testing that is taking place. Activated duty at 09:50. Joe Mazza on site to help with troubleshooting chlorine system. Was able to get system activated and tested. Chlorine system is now online set points have been adjusted accordingly. Loop Update rate: 31sec to 60sec Automatic dosing step value: 2% to 1% Any changes in trends are due to work being done on chlorine system. All alarms have been activated for chlorine system and any alarms that came in were due to chlorine system commissioning. | FLAG | stage2_low_confidence | 0.23142 | ML: above threshold (no LLM available) — 0.231 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.23142 | 0 | 0
2026-03 | 2026-03-20 | Keswick Deer Park Elevated Tank | EAST | On site to work with PCS on the rechlorination system at the tower to make sure the dosing logic is working. At 09:45 informed ROC that work was going to be completed on the chlorine system. At 09:51 activated duty to start work. Was not able to complete chlorine commissioning due to instrumentation at the treatment plant needing the plant off to complete their calibrations. Will reschedule this to another day. Chlorination system has been put to manual off till the work can be completed. | FLAG | stage2_low_confidence | 0.053424 | ML: above threshold (no LLM available) — 0.053 |  | 0.053424 | 0 | 0
2026-03 | 2026-03-25 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11690840 Weekly Bac-t Sample. Time: 10:13 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.45 Time: 10:16 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.30 Total: 1.88 1.32 after multiple grabs were taken adjusted the post injection total from 1.32mg/l to 1.88mg/l at 10:20. Time: 10:25 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.21 1.26 Total: 1.52 1.53 Also while on site troubleshooting chlorine dosing points to make sure everything is linear with each other. Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. Tested the chlorination system to see if it is all linear and after testing everything is good and dosing properly. | FLAG | stage2_low_confidence | 0.0089812 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0089812 | 0 | 0
2026-03 | 2026-03-11 | Keswick Deer Park Elevated Tank | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11657681 Weekly Bac-t Sample. Time: 09:52 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.05 0.98 Time: 09:55 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 0.96 0.98 Total: 1.38 1.31 Time: 10:03 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.88 0.80 Total: 1.36 1.32 Checked station and found heat tracer for the inlet/outlet off and not working, checked breaker a couple times and found it still not to be working. Will make a work order for electricians to check it out. Checked trends. No outstanding alarms on site. Entered data into PWQ sheet. | FLAG | stage2_low_confidence | 0.0096704 | ML: above threshold (no LLM available) — 0.01 | not working [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.0096704 | 0 | 0
2026-03 | 2026-03-13 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.010636 | ML: above threshold (no LLM available) — 0.011 |  | 0.010636 | 0 | 0
2026-03 | 2026-03-10 | Keswick West Park Reservoir | CENTRAL | -Finished the following work orders *Chemical system inspection *CL17 analyzer maintenance *H&S inspection -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.013946 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action] | 0.013946 | 0 | 0
2026-03 | 2026-03-06 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.010636 | ML: above threshold (no LLM available) — 0.011 |  | 0.010636 | 0 | 0
2026-03 | 2026-03-11 | Keswick West Park Reservoir | CENTRAL | Station and equipment check Take weekly BacT sample W11657912 and grabs @ 8:05 am (draining) Total: 1.80 mg/l Free: 1.44 mg/l Analyzer Total: 1.79 mg/l Analyzer Free: 1.46!mg/l No adjustments required Chemicals/reagents ok Ops ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048771 | 0 | 0
2026-03 | 2026-03-04 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet Grab: free=1.39mg/L total=1.71mg/L@8:45 Analyzer: free=1.44mg/L total=1.78mg/L -Checked CL17 reagents - OK -Collected weeky BacT sample YD #W11638785 & monthly sample YD #W11638771 | FLAG | stage2_low_confidence | 0.011126 | ML: above threshold (no LLM available) — 0.011 |  | 0.011126 | 0 | 0
2026-03 | 2026-03-17 | Keswick West Park Reservoir | CENTRAL | *Test run portable generator | FLAG | stage2_low_confidence | 0.012497 | ML: above threshold (no LLM available) — 0.012 |  | 0.012497 | 0 | 0
2026-03 | 2026-03-23 | Keswick West Park Reservoir | CENTRAL | -Tested chlorine leak alarm -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-18 | Keswick West Park Reservoir | CENTRAL | Station and equipment check Take weekly BacT sample W11673668 and grabs @ 8:10 am (draining) Total: 1.74 mg/l Free: 1.41 mg/l Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060744 | 0 | 0
2026-03 | 2026-03-20 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Changed treated total reagents | FLAG | stage2_low_confidence | 0.01423 | ML: above threshold (no LLM available) — 0.014 |  | 0.01423 | 0 | 0
2026-03 | 2026-03-16 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | FLAG | stage2_low_confidence | 0.010636 | ML: above threshold (no LLM available) — 0.011 |  | 0.010636 | 0 | 0
2026-03 | 2026-03-27 | Keswick West Park Reservoir | CENTRAL | -Performed station check - logged station readings into PWQ sheet -Changed treated free reagents | FLAG | stage2_low_confidence | 0.014166 | ML: above threshold (no LLM available) — 0.014 |  | 0.014166 | 0 | 0
2026-03 | 2026-03-25 | Keswick West Park Reservoir | CENTRAL | Station and equipment check Take weekly BacT sample W11690908 @ 8:00 am Total: 1.60 mg/l Free: 1.28 mg/l (Draining) Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004826 | 0 | 0
2026-03 | 2026-03-02 | Keswick West Park Reservoir | CENTRAL | Station and equipment check Took grabs @ 2:50 pm Total: 1.78 mg/l Free: 1.50 mg/l No adjustments to analyzers needed Chemicals/reagents ok Ops normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046091 | 0 | 0
2026-03 | 2026-03-31 | Musselman's Lake Elevated Tank | EAST | Under Direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro, (W11705392) - Operational sampling (iron, FCl, TCl, Temp, ATP) Data in PWQ workbook Regulatory sample taken @ 12:32 hrs. Grabs Taken @ 12:32 hrs. Grab FCl: 1.25 mg/L Grab TCl: 1.43 mg/L Analyzer: FCl: 1.27 mg/L Tower draining Facility: OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.00091527 | 0 | 0
2026-03 | 2026-03-11 | Musselman's Lake Elevated Tank | EAST | Under Direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro, (W11656809) Data in PWQ workbook Regulatory sample taken @ 11:57 Grabs Taken @ 11:57 hrs. Grab FCl: 1.36 mg/L Grab TCl: 1.56 mg/L Analyzer: FCl: 1.32 mg/L Changed AIT buffer and indicator reagents. Tower draining Facility: OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.00071795 | 0 | 0
2026-03 | 2026-03-25 | Musselman's Lake Elevated Tank | EAST | Under Direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro, (W11690078) Data in PWQ workbook Regulatory sample taken @ 11:55 hrs. Grabs Taken @ 11:55 hrs. Grab FCl: 1.27 mg/L Grab TCl: 1.48 mg/L Analyzer: FCl: 1.27 mg/L Tower draining Facility: OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.00087304 | 0 | 0
2026-03 | 2026-03-19 | Musselman's Lake Elevated Tank | EAST | Under direction of OIC Patrick Fobert On site for PM's; - Chlorine analyzer maintenance - Heat trace system inspection - Sump pit system inspection - Comprehensive cleaning - Manual valve exercise - JHSC health and safety inspection - Portable generator test Pre chlorine analyzer grab verification: Grab @ 12:08 hrs. FCl: 1.29 mg/L Analyzer: FCl: 1.29 mg/L Chlorine analyzer maintenance: Clean start @ 12:10 hrs. Clean Stop @ 12:43 hrs. Post clean verification Grab @ 13:01 FCl: 1.30 mg/L Analyzer: FCl: 1.28 mg/L Heat trace system operational Low temp alarm manually triggered @ 12:37 hrs. Portable gas generator for 20 mins. No observed issues. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00014781 | 0 | 0
2026-03 | 2026-03-18 | Musselman's Lake Elevated Tank | EAST | Under Direction of OIC Patrick Fobert On site for; - Station checks - Regulatory sampling, micro, (W11672695) Data in PWQ workbook Regulatory sample taken @ 12:00 hrs. Grabs Taken @ 12:00 hrs. Grab FCl: 1.27 mg/L Grab TCl: 1.50 mg/L Analyzer: FCl: 1.28 mg/L Tower draining Facility: OK | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.00088976 | 0 | 0
2026-03 | 2026-03-04 | Musselman's Lake Elevated Tank | EAST | On site to check station and equipment.? Tower is filling.? 14:05 grab chlorine residual from outlet: F = 1.59 mg/l, T= 1.78 mg/l.? Analyzer free= 1.58 mg/l. 14:05 collected micro sample, YD W11637232 15:06 collected in house samples.? CL17 reagents are at 50%? 14:18 opened the drain for 2 minutes to verify the outfall pipes. It's draining. Reviewed trends. No issue.? | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061518 | 0 | 0
2026-03 | 2026-03-31 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Collecting Weekly Bac-t sample. Collecting VOC sample. Time: 12:00 Header Grab (mg/l) Analyzer (mg/l) Free: 1.32 1.28 Total: 1.60 1.68 Time: 12:05 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.65 1.29-1.65 Total: 2.00 2.08 At 12:05 adjusted the inlet free from 1.29mg/l to 1.65mg/l after multiple grabs were taken. Time: 12:10 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.34 1.40 Total: 1.75 1.76 Entered data into PWQ sheet. Verified analyzers with grabs. Checked site and trends. Cleared outstanding alarms. No OOS equipment on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0021849 | 0 | 0
2026-03 | 2026-03-09 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Time: 10:05 Header Grab (mg/l) Analyzer (mg/l) Free: 1.45 1.49 Total: 1.70 1.76 Time: 10:10 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.39 Total: 1.85 1.86 Time: 10:13 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.39 Total: 1.75 1.71 Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Checked station and trends. Entered data into the PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0024085 | 0 | 0
2026-03 | 2026-03-13 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site for station check. Collected Cl2 grab residuals on: Header tap: FCL: 1.34mg/l Analyzer FCL: 1.40mg/l TCL: 1.70mg/l Analyzer TCL: 1.67mg/l Inlet tap: FCL: 1.72mg/l Analyzer FCL: 1.72mg/l TCL: 1.71mg/l Analyzer TCL: 1.71mg/l Outlet tap: FCL: 1.36mg/l Analyzer FCL: 1.29mg/l TCL: 1.67mg/l Analyzer TCL: 1.62mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-05 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete following work orders: W11636028 Inlet/Outlet Heat Trace Inspection. W11634972 Circulation Pump Test W11635323 Standby Power Generator Test W11660858 Housekeeping W11635084 Chlorine Gas Detectors Test W11635455 JHSC Inspection W11636037 Chlorine Analyzer Maintenance W11636277 Ventilation System Inspection W11636374 Actuated Valve Exercise/Inspection W11636387 Dehumidifier Cleaning and Inspection W11636782 Chlorine Scrubber Check W11638272 Chemical System Inspection Leaving site to assist maintenance at Deer Park will be back on site. Back on site to complete some more work orders. caused lo free alarms on all analyzers. verifying analyzers with grabs Time: 13:25 Header Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.51 Total: 1.82 1.84 Time: 13:30 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.70-1.53 Total: 1.90 1.89 after multiple grabs were taken adjusted the inlet free from a 1.70mg/l to a 1.53mg/l at 13:32. Time: 13:40 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.43 1.60-1.43 Total: 1.78 1.79 after multiple grabs adjusted the outlet free analyzer reading from a 1.60mg/l to a 1.43mg/l, at 13:40. Pocket colorimeter passed calibration test with vials. Tried to run generator on site still causing issues. will inform team lead and team tomorrow morning including on call operator tonight. Was not able to complete the chemical system inspection, or the chlorine gas detector test. will come back to site to do that. Any changes in trends or alarms created were due to work orders being completed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.0057535 | 0 | 0
2026-03 | 2026-03-02 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Time: 11:50 Header Grab (mg/l) Analyzer (mg/l) Free: 1.44. 1.40 Total: 1.78 1.85 Time: 11:57 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.66-1.42 Total: 1.73 1.76 Time: 12:00 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.52 Total: 1.77 1.80 After taking multiple grabs adjusted the inlet free analyzer from a 1.66mg/l to a 1.42mg/l at 11:57 No outstanding alarms on site. No OOS equipment on site. Checked site and trends. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0034504 | 0 | 0
2026-03 | 2026-03-11 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11657681 Weekly Bac-t Sample. Time: 11:07 Header Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.42 Total: 1.71 1.70 Time: 11:11 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.40. 1.11-1.40 Total: 1.67 1.72 Time: 11:15 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.30 1.35 Total: 1.66 1.64 At 11:11 adjusted the inlet free after multiple grabs from 1.11mg/l to 1.40mg/l. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0029115 | 0 | 0
2026-03 | 2026-03-04 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC Samples. W11638390 Weekly Bac-t Sample. W11638362 VOC Samples. Time: 10:48 Header Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.54 Total: 1.90 1.92 Time: 10:50 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.56 1.47 Total: 1.82 1.83 Time: 10:55 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.63 Total: 1.77 1.76 Verified analyzers with grabs all ok. Checked station and trends. Entered data into PWQ sheet. No outstanding alarms on site. No OOS equipment. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0019491 | 0 | 0
2026-03 | 2026-03-06 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Time: 08:15 Header Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.46 Total: 1.74 1.79 Time: 08:18 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.45 Total: 1.78 1.79 Time: 08:22 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.37 1.37 Total: 1.73 1.74 Verified analyzers with grabs all ok. Checked station and trends. No outstanding alarms on site. No OOS equipment on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0025654 | 0 | 0
2026-03 | 2026-03-16 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Time: 09:20 Header Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.44 Total: 1.72 1.72 Time: 09:25 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.36 Total: 1.74 1.67 Time: 09:28 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.32 Total: 1.75 1.67 Verified analyzers with grabs all ok. Checked site and trends. Making work order for the portable generator issues here on site. Entered data into PWQ sheet. No outstanding alarms on site. No OOS equipment. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.0051401 | 0 | 0
2026-03 | 2026-03-25 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11690840 Weekly Bac-t Sample. Time: 11:41 Header Grab (mg/l) Analyzer (mg/l) Free: 1.24. 1.37-1.24 Total: 1.58 1.63 After multiple grabs adjusted the header free residual from a 1.37mg/l to a 1.24mg/l at 11:42. Time: 11:45 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.31 1.11-1.31 Total: 1.66 1.75 After multiple grabs were taken adjusted the inlet free from a 1.11mg/l to a 1.31mg/l at 11:46 Time: 11:50 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.25 Total: 1.58 1.60 Verified analyzers. Checked station and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0036461 | 0 | 0
2026-03 | 2026-03-23 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Completing following work order. Chlorine gas emergency test. Time: 12:28 Header Grab (mg/l) Analyzer (mg/l) Free: 1.31 1.34 Total: 1.66 1.62 Time: 12:30 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.68-1.38 Total: 1.66 1.69 After multiple grabs adjusted the inlet free residual reading from a 1.68mg/l to a 1.38mg/l at 12:31. Time: 12:35 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.26 1.23 Total: 1.64 1.58 Verified analyzers with grabs. Checked station and trends. Completed work order with out issue. Cleared alarms associated with work order at 12:37. No OOS equipment on site. Entered data into PWQ sheet. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; emergency [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | sso [critical]; emergency [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On its to complete station check. Time: 09:46 Header Grab (mg/l) Analyzer (mg/l) Free: 1.36 1.33 Total: 1.70 1.76 Time: 09:50 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.89-1.53 Total: 1.88 1.97 After multiple grabs adjusted the inlet free from a 1.89mg/l to a 1.53mg/l at 09:52. Time: 09:57 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.30 Total: 1.70 1.72 Verified analyzers with grabs. Checked station and trends. No OOS equipment on site. No outstanding alarms on site. Entered data into PWQ. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.002879 | 0 | 0
2026-03 | 2026-03-02 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | Test backflow preventer Passed | FLAG | stage2_low_confidence | 0.010526 | ML: above threshold (no LLM available) — 0.011 |  | 0.010526 | 0 | 0
2026-03 | 2026-03-19 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | Chris Iliohan Tyler Smith. Picked up Honda generator for repairs. Left a working generator (non electric start) onsite until we can get this one working | FLAG | stage2_low_confidence | 0.03915 | ML: above threshold (no LLM available) — 0.039 | repair [maintenance_action] | 0.03915 | 0 | 0
2026-03 | 2026-03-30 | Markham Pumping Station | EAST | On site to complete station check. Time: 13:30 Grab (mg/l) Analyzer (mg/l) Free: 0.07 0.02 Total: 1.40 1.32 Checked station and trends. No OOS equipment on site. No outstanding alarms on site. Verified analyzer with grabs. | FLAG | stage2_low_confidence | 0.012146 | ML: above threshold (no LLM available) — 0.012 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.012146 | 0 | 0
2026-03 | 2026-03-18 | Keswick Woodbine Elevated Tank and Rechlorination Facility | EAST | On site to complete station check. Collecting weekly Bac-t Sample. W11673541 Weekly Bac-t Sample. Time: 10:32 Header Grab (mg/l) Analyzer (mg/l) Free: 1.36 1.37 Total: 1.61 1.69 Time: 10:40 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.37 1.44 Total: 1.67 1.55-1.67 After multiple grabs adjusted the treated total inlet analyzer from a 1.55mg/l to 1.67mg/l at 10:43. Time: 10:45 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.31 1.27 Total: 1.70 1.65 Verified analyzers with grabs. Checked station and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0035425 | 0 | 0
2026-03 | 2026-03-10 | Markham Pumping Station | EAST | On site with Total Power for generator annual PM. In able to load test as water pump is leaking. | FLAG | stage2_low_confidence | 0.025474 | ML: above threshold (no LLM available) — 0.025 | leak [infrastructure]; leaking [infrastructure] | 0.025474 | 0 | 0
2026-03 | 2026-03-02 | Markham Pumping Station | EAST | On site to check station and equipment. Requested ROC to exercise each pump for 15 minutes earlier. P2 is running upon arrival by ROC. 12:50 chlorine residuals grab/analyzer in mg/l: Total: 1.31/1.31 Free: 0.03/0.02 Other station readings are in PWQ sheets. Reviewed trends, Station is under normal operation. Equipment OOS: none. | FLAG | stage2_low_confidence | 0.0087327 | ML: above threshold (no LLM available) — 0.009 | oos [equipment_failure] | 0.0087327 | 0 | 0
2026-03 | 2026-03-06 | Markham Pumping Station | EAST | On site for facility station check and equipment verifications All pumps in manual off as per normal operation Verified analyzer readings: @10:30 Grab free: 0.05 / Analyzer: 0.01 mg/L Grab total: 1.40 / Analyzer: 1.32 mg/L Reviewed trends, equipment ok Station operation normal | FLAG | stage2_low_confidence | 0.0078169 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078169 | 0 | 0
2026-03 | 2026-03-16 | Markham Pumping Station | EAST | On site for station check and equipment verifications Remotely started pump #2 in manual @10:44 for station check Pump #2 running - 370 L/s, 496 kpa discharge pressure Recorded data in PWQ sheets Verified analyzer readings @11:08 Grab free: 0.05 / Analyzer: 0.02 mg/L Grab total: 1.29 / Analyzer: 1.30 mg/L No adjustments needed Reviewed trends Equipment OOS: None Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-20 | Markham Pumping Station | EAST | Station Check (no issues found) Input data to PWQ 12:30 Verified Depolox (mg/l) Free: Grab 0.05, A 0.02 Total: Grab 1.31, A 1.36 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050566 | 0 | 0
2026-03 | 2026-03-31 | Markham Milliken Elevated Tank | EAST | On site for station check and weekly micro sampling (W11705564) Tower level - 68% and draining Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals @13:15 Grab free: 0.03 mg/L / Analyzer: 0.00 mg/L Grab total: 1.55 mg/L / Analyzer: 1.57 mg/L Collected micro sample @13:20 Advanced monitoring using SL1000 / Nitrification control monitoring Mono: 1.40 mg/L Free NH3: 0.06 mg/L Total NH3: 0.33 mg/L NO2: 0.004 mg/L pH: 8.01 Temp: 4.1 C Reviewed trends Station operation normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0022139 | 0 | 0
2026-03 | 2026-03-12 | Markham Pumping Station | EAST | On site for station check, equipment verifications, and to complete monthly PMs - JHSC Health and safety inspection - Flood alarm test - Dehumidifier inspection and cleaning - Ventilation system inspection - Diesel Generator test run and hours log Pre checks: Oil level: Ok Coolant Level: Ok Coolant Recirc Pump: Ok Fluid Leaks: Ok Battery Terminals / Cables: Ok Battery Cell Levels: N/A Start Hours: 591.2 (Started @10:50) Start Fuel: 97.6 / 97.8 cm (541/542 L) Ran Pump #1 during generator run Data While Generator running: AMPs: 202 / 199 / 199 amps Voltage: 600 V Frequency: 59.9 hz Engine Speed: 1798 RPMs Oil Temp: 197 F Oil Pressure: 61 psi Coolant Temp: 183 F Exhaust: 672 / 691 F Stop Hours: 592.4 (Stopped @12:06) Stop Fuel: 93.4 / 93.2 cm (518 / 517 L) No issues with test or power transfer Verified chlorine analyzer readings: @13:00 Grab FCL: 0.02 mg/L / Analyzer: 0.01 mg/L Grab TCL: 1.29 mg/L / Analyzer: 1.31 mg/L Reviewed trends, equipment ok Recorded readings in PWQ sheets Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; leak [infrastructure] | flood [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-04 | Markham Milliken Elevated Tank | EAST | On site for station check and weekly micro sampling (W11637404) Tower level - 82% and filling Recorded station readings in PWQ sheets Verified analyzer readings with grab residuals @12:20 Grab/ Analyzer (mg/L) FCL: 0.04 / 0.00 TCL: 1.65 / 1.65 No adjustments needed Collected micro sample @12:24 Collected in-house operational monitoring samples for ATP and phosphorus Advanced monitoring using SL1000 / Nitrification control monitoring: Mono: 1.44 mg/L Free / Total NH3: 0.07 / 0.35 mg/L NO2: 0.004 mg/L pH: 8.00 Temp: 4.3 C Reviewed trends, equipment OOS: None Station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-25 | Markham Milliken Elevated Tank | EAST | On site for station check and weekly micro sampling (W11690214) Tower level - 54% and draining Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals @11:59 Grab free: 0.08 mg/L / Analyzer: 0.00 mg/L Grab total: 1.65 mg/L / Analyzer: 1.63 mg/L Collected micro sample @12:03 Advanced monitoring using SL1000 / Nitrification control monitoring Mono: 1.41 mg/L Free NH3: 0.06 mg/L Total NH3: 0.35 mg/L NO2: 0.004 mg/L pH: 8.02 Temp: 3.9 C Reviewed trends Station operation normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0022139 | 0 | 0
2026-03 | 2026-03-18 | Markham Milliken Elevated Tank | EAST | On site for station check and weekly micro sampling (W11672839) Tower level - 68% and filling Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals @10:51 Grab free: 0.02 mg/L / Analyzer: 0.00 mg/L Grab total: 1.62 mg/L / Analyzer: 1.62 mg/L Collected micro sample @10:55 Collected in-house operational sampling for ATP and phosphorus Advanced monitoring using SL1000 / Nitrification control monitoring Mono: 1.40 mg/L Free NH3: 0.03 mg/L Total NH3: 0.31 mg/L NO2: 0.003 mg/L pH: 8.04 Temp: 3.9 C Reviewed trends, equipment ok Station operation normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026265 | 0 | 0
2026-03 | 2026-03-31 | Markham PD5 Reservoir | EAST | On site for station check and weekly micro sampling (W11705564) Reservoir level - 54% and draining (West cell only) East cell is OOS for capital projects Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals: @11:00 Grab Free: 0.06 mg/L / Analyzer: 0.03 mg/L Grab total: 1.42 mg/L / Analyzer: 1.42 mg/L Collected micro sample from west cell @11:12 Collected in-house operational samples for ATP and phosphorus Advanced monitoring using SL1000 / nitrification control monitoring: Mono: 1.20 mg/L Free NH3: 0.07 mg/L Total NH3: 0.31 mg/L NO2: 0.004 mg/L pH: 8.05 Temp: 7.1 C Reviewed trends Equipment OOS: East Reservoir cell for capital projects | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-11 | Markham Milliken Elevated Tank | EAST | On site for station check and weekly micro sampling (W11656945) Tower level - 79% and filling Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals @11:20 Grab free: 0.04 mg/L / Analyzer: 0.01 mg/L Grab total: 1.70 mg/L / Analyzer: 1.69 mg/L Collected micro sample @11:25 Collected in-house operational sampling for ATP and phosphorus Advanced monitoring using SL1000 / Nitrification control monitoring Mono: 1.48 mg/L Free NH3: 0.05 mg/L Total NH3: 0.34 mg/L NO2: 0.003 mg/L pH: 8.04 Temp: 4.3 C Completed the following PMs: - Chlorine analyzer maintenance: See above for grabs verifications. No issues - Actuated valve exercise from 11:51 to 11:56. Tower was filling, called ROC to request metro to turn off PD6s pumps while exercising the valve. Called ROC back to tell Metro they can resume normal operations - Manual valves exercise - ran the tower draining through the bypass line while testing the mainline actuated valve - JHSC health and safety inspection - Dehumidifier inspection and test - Low temperature alarm test - Inlet / Outlet heat trace system inspection - Sump pit inspection - Level transmitter flush and inspection Equipment all back to auto Reviewed trends Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system] | bypass [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | Markham PD5 Reservoir | EAST | On site for station check and weekly micro sampling (W11637404) Reservoir level is 48% - East cell is OOS for capital upgrades Contractors on site interior and exterior for capital projects Verification of chlorine analyzer: @10:50 West Cell grabs / analyzers: FCL: 0.08 mg/L / 0.03 mg/L TCL: 1.37 mg/L / 1.40 mg/L Collected sample @10:55 from west cell Collected advanced operational monitoring samples @10:55 for ATP and phosphorus Advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.16 mg/L Free / Total NH3: 0.10 / 0.33 mg/L NO2: 0.004 mg/L pH: 8.02 Temp: 6.4 C Reviewed trends, equipment OOS: East cell Station operation ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-25 | Markham PD5 Reservoir | EAST | On site for station check and weekly micro sampling (W11690214) Reservoir level - 54% and draining (West cell only) East cell is OOS for capital projects Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals: @10:30 Grab Free: 0.02 mg/L / Analyzer: 0.01 mg/L Grab total: 1.37 mg/L / Analyzer: 1.31 mg/L Collected micro sample from west cell @10:35 Collected in-house operational samples for ATP and phosphorus Advanced monitoring using SL1000 / nitrification control monitoring: Mono: 1.19 mg/L Free NH3: 0.08 mg/L Total NH3: 0.32 mg/L NO2: 0.004 mg/L pH: 8.03 Temp: 6.6 C Free Chlorine fault alarm was generated during sampling, analyzer faulted due to not enough flow with sample tap running. Cleared alarm, no further issues Reviewed trends Equipment OOS: East Reservoir cell for capital projects | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-11 | Markham PD5 Reservoir | EAST | On site for station check and weekly micro sampling (W11656945) Outstanding Free Chlorine analyzer fault alarm from 09:02. Checked analyzer, no issues observed. Contractor informed that the analyzer tubing was leaking, likely bumped by a contractor working, which caused the fault, they rectified the issue. Alarm cleared on SCADA Reservoir level - 64% and draining (West cell only) East cell is OOS for capital projects Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals: @09:35 Grab Free: 0.07 mg/L / Analyzer: 0.02 mg/L Grab total: 1.44 mg/L / Analyzer: 1.48 mg/L Collected micro sample from west cell @09:42 Collected in-house operational samples for ATP and phosphorus Advanced monitoring using SL1000 / nitrification control monitoring: Mono: 1.23 mg/L Free NH3: 0.07 mg/L Total NH3: 0.32 mg/L NO2: 0.003 mg/L pH: 8.04 Temp: 6.5 C Completed the following PMs: - JHSC Health and safety inspection - Chlorine analyzer maintenance - see grabs above for verifications - External venting system inspection - High / Low water level alarms test Reviewed trends Equipment OOS: East Reservoir cell for capital projects Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | fault [equipment_failure]; oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-26 | Markham PD5 Reservoir | EAST | On site to respond chlorine fault alarm. The analyzer drain line was pinched at the door and air locked as a result. Informed Jeff B (site super for contractor). Reinstate the drain line. 11:22 chlorine residual from west cell. Grab free = 0.04 analyzer free = 0.01 Grab total = 1.44 analyzer total = 1. Building low temp outstanding. Adjusted low temp sensor to 4 degree C. Reset alarms. No outstanding alarms. East cell remains offline and OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | Markham PD5 Reservoir | EAST | On site for station check and weekly micro sampling (W11672839) Reservoir level - 61% and filling (West cell only) East cell is OOS for capital projects. Contractors on site. Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals: @09:45 Grab Free: 0.03 mg/L / Analyzer: 0.00 mg/L Grab total: 1.38 mg/L / Analyzer: 1.35 mg/L Collected micro sample from west cell @09:50 Collected in-house operational samples for ATP and phosphorus Advanced monitoring using SL1000 / nitrification control monitoring: Mono: 1.21 mg/L Free NH3: 0.04 mg/L Total NH3: 0.28 mg/L NO2: 0.004 mg/L pH: 8.03 Temp: 6.6 C Free Chlorine fault alarm was generated during sampling, analyzer faulted due to not enough flow with sample tap running. Cleared alarm, no further issues Entered East Cell (OOS) Restricted space. Contractors also on site. Inspected leakage from interconnect valve, the leakage is the same / similar amount to the previous inspection by Ops. Reviewed trends Equipment OOS: East Reservoir cell for capital projects Station ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 0
2026-03 | 2026-03-31 | Stouffville Well 3 | EAST | On site for station check and Bac-T sampling W11705508 Collected raw and treated samples, verified analyzers, 11:15, in mg/L Influent FCl - G 2.50; A 2.47 Effluent FCl - G 2.40; A 2.53 Effluent TCl - G 2.80 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048822 | 0 | 0
2026-03 | 2026-03-11 | Stouffville Well 3 | EAST | On site for sampling W11656903 and station check Collected raw and treated samples, 10:45, and verified chlorine analyzers, in mg/L Influent FCl - G 2.54; A 2.51 Effluent FCl - G 2.58; A 2.48 Adjusted to match average of grabs Effluent TCl - G 2.80 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059337 | 0 | 0
2026-03 | 2026-03-30 | Stouffville Well 3 | EAST | Attended site for station check Replaced eyewash station water Verified chlorine analyzers. Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.013426 | ML: above threshold (no LLM available) — 0.013 |  | 0.013426 | 0 | 0
2026-03 | 2026-03-31 | Stouffville Well 3 | EAST | Attended site for CMU5 W11769468 influent and effluent free low and low low lockout Grabs, 8:15, in mg/L Effluent FCl: 0.35; Analyzer 0.32 Effluent TCl: 0.45 Replaced influent and effluent free chlorine CL17 analyzer reagents and primed Acknowledged alarms and placed well in local off to prevent unwanted start up Initiated backflush, following dechlorination protocol, 8:19 Completed backflush, 9:04 Found stuck regulator on chlorine cylinder 1 that failed to open on chlorine bank transfer. Manually opened regulator Verified chlorine analyzers after backflush, 9:07, in mg/L Influent FCl - G 1.26; A 1.23 Effluent FCl - G 1.57; A 1.56 Effluent TCl - G 1.78 Placed well manual on, 9:09, for supervised start up | FLAG | stage2_low_confidence | 0.0102 | ML: above threshold (no LLM available) — 0.01 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0102 | 0 | 0
2026-03 | 2026-03-10 | Stouffville Well 3 | EAST | Attended site for preventative maintenance Changed chlorine cylinder bank 2 with Travis Wyatt Completed Chlorine analyzer cleaning Turbidimeter cleaning Silicate pump and line flush Chlorine system inspection Silicate pump inspection Isolated well from distribution and depressurized to hot flush silicate lines. Primed and reset PSV on chemical board. Backflushed well with dechlorination pucks in catch to purge excess silicate from priming the lines Test ran the well while on site and rotated silicate pumps to ensure proper operation Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049373 | 0 | 0
2026-03 | 2026-03-06 | Stouffville Well 3 | EAST | On site for station check Inspected chlorine and silicate systems Reviewed station trends Checked pump and process piping Recorded observations and analyzer verification in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.011376 | ML: above threshold (no LLM available) — 0.011 |  | 0.011376 | 0 | 0
2026-03 | 2026-03-02 | Stouffville Well 3 | EAST | On site for station check Verified chlorine analyzers, 13:26, in mg/L Influent FCl G 2.56; A 2.48 Effluent FCl G 2.44; A 2.46 Effluent TCl G 2.72 Reviewed SCADA and station trends Checked station and equipment Inspected chlorine and silicate system Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0041137 | 0 | 0
2026-03 | 2026-03-13 | Stouffville Well 3 | EAST | On site to check station and equipment. Well 3 is man/on since Zone 1 ET is filling. 13:23 chlorine grab residual / analyzer in mg/l: Influent free: 2.48 / 2.55 Effluent free: 2.54 / 2.58 Effluent total: 2.64 Reviewed trends. No issue. Chlorinator 2 is OOS and isolated from the system. | FLAG | stage2_low_confidence | 0.01047 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure] | 0.01047 | 0 | 0
2026-03 | 2026-03-24 | Stouffville Well 3 | EAST | Attended site for chlorine cylinder change with Patrick Fobert Changed chlorine cylinder bank 1, tested and inspected chlorine system | FLAG | stage2_low_confidence | 0.012815 | ML: above threshold (no LLM available) — 0.013 |  | 0.012815 | 0 | 0
2026-03 | 2026-03-18 | Stouffville Well 3 | EAST | Onsite to perform annual maintenance/Rebuild chlorinators #2. Informed ROC and Jack onsite isolated gas cylinders and purged the lines. Tested halogen system, confirmed operation as intended. We rebuilt both the chlorinators. Connected both the chlorinators back to hard PVC chlorine line. performed vacuum test. No leak found. Performed gas calibration and Performed verification and Put both chlorinators back in service. All the related alarms were cleared. No issues. Back flushed well for five minute duration under the direction of OIC Jack Palmer, following dechlorination protocol and he started the well remotely. Monitored for while. No issues. Informed ROC, armed the building and left the site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; leak [infrastructure] | alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-26 | Stouffville Well 3 | EAST | Attended site for station check and silicate line flush, pump maintenance and inspection Isolated and depressurized station header for work Hot water flushed silicate pumps 1 and 2 into common injection point from suction side Disassembled and rebuilt silicate pump 1 suction and discharge check valves on pump head Cleaned and flushed PSV and PRVs on chemical board, set to 450 and 625 kPa respectively Primed silicate pumps and line to injection point Re-pressurized station header and backflushed excess silicate, dechlorinating at catch basin Test ran well in manual, cycling silicate pump duty while supervised on site Station and equipment okay | FLAG | stage2_low_confidence | 0.037944 | ML: above threshold (no LLM available) — 0.038 |  | 0.037944 | 0 | 0
2026-03 | 2026-03-19 | Stouffville Well 3 | EAST | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside PAC panel. ROC is informed and Well 3 was in manual off before commencing the work Historian hrbt alarm and Comm fail alarms were triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 09:18 AM to 09:53 AM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; alarms [control_system] | scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | Stouffville Well 3 | EAST | On site for station check Recorded observations in the shared PWQ sheet Shut well down and cleaned turbidimeter cuvette Placed silicate pump 1 in duty 1 Station and equipment okay | FLAG | stage2_low_confidence | 0.0086145 | ML: above threshold (no LLM available) — 0.009 |  | 0.0086145 | 0 | 0
2026-03 | 2026-03-04 | Stouffville Well 3 | EAST | On site for sampling W11637348 and station check Collected raw and treated sample, 10:05, and verified chlorine analyzers in mg/L Influent free Cl: G 2.58; A 2.52 Effluent free Cl: G 2.48; A 2.48 Effluent total Cl: G 2.80 Inspected station equipment Recorded observations in the shared PWQ sheet Chlorinator 2 is out of service - booster pump local off Station and equipment okay Well 3 back in auto | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; oos [equipment_failure] | out of service [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | Stouffville Well 3 | EAST | On site for station check and sampling W11672797 Completed JHSC inspection Collected raw and treated water samples, 9:42, and verified chlorine analyzers (mg/L) Influent FCl - G 2.58; A 2.54 Effluent FCl - G 2.42; A 2.57 Adjusted to match average of grabs Effluent TCl - G 2.76 Placed well in manual off, closed both chlorine cylinders and purged both chlorine trains for Instrumentation to install chlorinator 2 today. Informed RO Christian Van Beek. He will leave the well manual off for Instrumentation to perform their work. Recorded observations in the shared PWQ sheet Tested emergency halogen system - gas detector succeeded in quantifying the test gas, but the halogen valves failed to close. W11743947 CMU4 created for Electrical Maintenance to attend Station and equipment okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; failed [equipment_failure] | emergency [critical]; failed [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-20 | Stouffville Well 3 | EAST | Attended site for station check Recorded observations and analyzer verification in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.013761 | ML: above threshold (no LLM available) — 0.014 |  | 0.013761 | 0 | 0
2026-03 | 2026-03-17 | Stouffville Well 3 | EAST | Attended site to receive sodium silicate delivery. Approximate start level 20 cm Approximate stop level 89 cm | FLAG | stage2_low_confidence | 0.0095748 | ML: above threshold (no LLM available) — 0.01 |  | 0.0095748 | 0 | 0
2026-03 | 2026-03-25 | Stouffville Well 3 | EAST | On site for station check and sampling W11690172 Collected raw water and treated water samples, 10:35, and verified chlorine analyzers (mg/L) Influent FCl - G 2.38; A 2.46 Adjusted to match average of grabs Effluent FCl - G 2.36; A 2.39 Effluent TCl - G 2.74 Replaced free and total chlorine analyzer reagents Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054062 | 0 | 0
2026-03 | 2026-03-09 | Stouffville Well 3 | EAST | Attended site for station check Collected grab samples and recorded results and observations in the shared PWQ sheet Station and equipment okay Received delivery of 8 full chlorine cylinders and returned 8 empty. | FLAG | stage2_low_confidence | 0.01065 | ML: above threshold (no LLM available) — 0.011 |  | 0.01065 | 0 | 0
2026-03 | 2026-03-31 | Stouffville Well 1 & 2 | EAST | On site for station check and Bac-T sampling W11705508 Collected well 2 raw and treated sample, 9:45, verified analyzers, in mg/L Influent FCl - G 3.26; A 3.38 Effluent FCl - G 2.01; A 1.94 Effluent TCl - G 2.38 Received hypo delivery Start 900/ 900 L Stop 1255/ 1281 L Collected well 1 raw sample, 10:22 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.002625 | 0 | 0
2026-03 | 2026-03-13 | Stouffville Well 1 & 2 | EAST | On site to check station and equipment. Well 1 is running in duty 1. Placed well 1 man/on since Zone 1 ET is filling. 11:36 chlorine grab residual / analyzer in mg/l: Influent free: 3.54 / 3.48 Effluent free: 2.01 / 1.90 (Standardized with 3 grabs? average of 1.97 mg/l) Effluent total: 2.54 Lowered chlorine residual setpoint from 3.50 mg/l to 3.40 mg/l. Reviewed trends. No issue. Hypo tank 1 is OOS and isolated from the system. | FLAG | stage2_low_confidence | 0.011899 | ML: above threshold (no LLM available) — 0.012 | oos [equipment_failure] | 0.011899 | 0 | 0
2026-03 | 2026-03-09 | Stouffville Well 1 & 2 | EAST | On site for station check Verified analyzers and recorded observations in the shared PWQ sheet. Station manual off while waiting for hypo delivery Station and equipment okay | FLAG | stage2_low_confidence | 0.013171 | ML: above threshold (no LLM available) — 0.013 |  | 0.013171 | 0 | 0
2026-03 | 2026-03-15 | Stouffville Well 1 & 2 | EAST | ROC called regarding Well 1 Fault due to power outage this afternoon. Will leave off until Monday, Well #2 available and in duty. | FLAG | stage2_low_confidence | 0.010625 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure] | 0.010625 | 0 | 0
2026-03 | 2026-03-10 | Stouffville Well 1 & 2 | EAST | On site for hypo delivery: Tank #1 will not be filled, as it OOS for replacement Tank #2 start: 42.2 cm Tank #2 stop: 200.6 cm Manual started well #1 after hypo tank filled @14:22 | FLAG | stage2_low_confidence | 0.013571 | ML: above threshold (no LLM available) — 0.014 | oos [equipment_failure] | 0.013571 | 0 | 0
2026-03 | 2026-03-09 | Stouffville Well 1 & 2 | EAST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-04 | Stouffville Well 1 & 2 | EAST | On site for sampling W11637348 and station check Collected well 2 raw and treated sample, verified free chlorine analyzers, 8:30, mg/L Influent free: G 3.46; A 3.54 Effluent free: G 2.03; A 2.01 Effluent total: G 2.52 Recorded observations in the shared PWQ sheet Equalized hypo tanks by opening tie valve - left open Placed wells 1 and 2 manual off, 8:40, and rotated well 1 to duty 1, well 2 duty 2 Placed well 1 in manual on for raw water sampling, 8:51 Collected well 1 raw sample, 9:05 Zone 2 duty deactivated, zone 1 activated. Leaving well 1 manual on and monitoring elevated turbidity remotely while offsite. Station and equipment okay. Off site at 9:20 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067263 | 0 | 0
2026-03 | 2026-03-06 | Stouffville Well 1 & 2 | EAST | Attended site for station check Recorded observations and analyzer verification in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.013761 | ML: above threshold (no LLM available) — 0.014 |  | 0.013761 | 0 | 0
2026-03 | 2026-03-02 | Stouffville Well 1 & 2 | EAST | On site for station check Verified free chlorine analyzers, 12:15, mg/L Influent free - G 3.84; A 3.72 Effluent free - G 2.03; A 2.02 Effluent total - G 2.74 Checked station and equipment Inspected chemical system Reviewed trends and SCADA Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0039541 | 0 | 0
2026-03 | 2026-03-20 | Stouffville Well 1 & 2 | EAST | Attended site for station check. Recorded observations and analyzer verification in the shared PWQ sheet Reviewed station trends Station and equipment okay | FLAG | stage2_low_confidence | 0.01288 | ML: above threshold (no LLM available) — 0.013 |  | 0.01288 | 0 | 0
2026-03 | 2026-03-23 | Stouffville Well 1 & 2 | EAST | On site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.01119 | ML: above threshold (no LLM available) — 0.011 |  | 0.01119 | 0 | 0
2026-03 | 2026-03-27 | Stouffville Well 1 & 2 | EAST | On site to cut the PVC analyzer to waste pipe, and direct it to the storm pipe. Made sure that dechlorination pucks have been put into the storm drain to prevent any chlorine residual from going to environment. | FLAG | stage2_low_confidence | 0.027345 | ML: above threshold (no LLM available) — 0.027 |  | 0.027345 | 0 | 0
2026-03 | 2026-03-11 | Stouffville Well 1 & 2 | EAST | On site for sampling W11656903 and station check Collected well 1 raw and treated samples, 9:27. Verified influent free and effluent free chlorine analyzers, mg/L Influent free Cl - G 3.30; A 3.42 Effluent free Cl - G 1.81; A 2.09 Adjusted to match average of grabs Effluent total Cl - 2.14 Collected raw sample from well 2, 9:50 Found well 2 discharge check valve passing. Consulted with Water Resources, Leanne Paterson and Jason Moore to confirm no chance of water flowing back into aquifer due to check valve on the submersible well pump. Will create a work order for maintenance to replace well 2 discharge valve Wells 1 and 2 manual off for step test tomorrow. ROC informed. Station and equipment okay | FLAG | stage2_low_confidence | 0.030371 | ML: above threshold (no LLM available) — 0.03 | work order [maintenance_action] | 0.030371 | 0 | 0
2026-03 | 2026-03-12 | Stouffville Well 1 & 2 | EAST | Attended site to perform step test with Water Resources, Leanne Paterson and Jason Moore. Steps: 9:00 11 L/s 10:00 22 L/s 11:00 33.5 L/s 12:00 Rest 13:00 well will be returned to auto operation Pumped out hypo tank 1 into temporary day tank in prep for hypo tank 1 replacement. Disregard LIT, tank is empty. Completed silicate and hypo pump inspection. Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038094 | 0 | 0
2026-03 | 2026-03-03 | Stouffville Well 1 & 2 | EAST | On site for preventative maintenance work orders Informed RO, Christian Van Beek Wells manual off for maintenance Completed: Chlorine analyzer maintenance Turbidimeter maintenance and calibration with a 20.7 NTU standard Hypo pump inspection, P1 and P2 Silicate pump inspection, P1 and P2 JHSC inspection Verified chlorine analyzers, 14:31, mg/L Influent free G 3.18; A 3.32 Effluent free G 1.86; A 1.76 Adjusted effluent free chlorine analyzer to match average of grabs Adjusted silicate pump 1 max flow 95mL/min to 90 Test ran well in manual and cycled through hypo and silicate pump duties, verified station function - all okay Station back in service. Left well 2 manual on (duty 1), well 1 off duty 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.0054624 | 0 | 0
2026-03 | 2026-03-25 | Stouffville Well 1 & 2 | EAST | STW12 On site for station check and sampling W11690172 Collected well 1 raw water and treated samples, 9:50, and verified chlorine analyzers (mg/L) Influent FCl - G 3.32; A 3.38 Effluent FCl - G 2.12; A 1.98 Adjusted to match average of grabs Effluent TCl - G 2.60 Collected well 2 raw water sample, 10:15 Reduced hypo pump 2 dosing factor from 50 to 45% to reduced the influent free chlorine from rotating wells Replaced influent and effluent free chlorine analyzer reagents Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047079 | 0 | 0
2026-03 | 2026-03-24 | Stouffville Well 1 & 2 | EAST | Attended site for hypo delivery Start levels: 95.41/ 98.78 cm Stop levels: 197.8/ 200.5 cm Approximately 1500 L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067682 | 0 | 0
2026-03 | 2026-03-19 | Stouffville Well 1 & 2 | EAST | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside PAC panel. ROC is informed and all Well and high lift pumps in ST area were in manual off before commencing the work This included STW3, STW12, STRS48 High Lift pumps, STPSMR Pumps, STPSTL pumps Historian hrbt alarm and Comm fail alarms were triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 01:16 PM to 1:35 PM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system]; alarms [control_system] | scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | Stouffville Well 1 & 2 | EAST | Under Direction of OIC (Patrick Fobert) On site for Hypo Receiving Tank 1; Start cm: 30 cm Stop cm: 82.61 cm Start V: 197 L Stop V: 891 L Tank 2: Start cm: 105.7 cm Stop cm: 139 cm Start V: 695 L Stop V: 914 L Total V on SCADA: 913 L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0018491 | 0 | 0
2026-03 | 2026-03-16 | Stouffville Well 1 & 2 | EAST | Attended site for station check, maintenance support and generator test. Completed station check - all okay Reset fault on the multilin on pump 1. Generator test run: Hours Start 663.5 Stop 664.8 Fuel Start 960 L Stop 943 L Run statistics Exhaust temperature 350 C Oil pressure 25 PSI Coolant temperature 86 C Battery voltage 25 V Oil temperature 160 F Speed 1800 RPM Frequency 60 Hz Well 2 running in manual on and Well 1 back in auto. Off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure] | 0.00094061 | 0 | 0
2026-03 | 2026-03-18 | Stouffville Well 1 & 2 | EAST | On site for station check and sampling W11672797 Collected well 2 raw and treated water samples, 8:05. Verified chlorine analyzers, mg/L. Influent FCl - G 3.32; A 3.39 Effluent FCl - G 1.93; A 1.91 Effluent TCl - G 2.50 Recorded observations in the shared PWQ sheet Confirmed the new hypo tank 1 fittings are not leaking, LIT is calibrated. Waiting on hypo delivery to fill. Collected well 1 raw sample, 8:30. Station and equipment okay | FLAG | stage2_low_confidence | 0.0074106 | ML: above threshold (no LLM available) — 0.007 | leak [infrastructure]; leaking [infrastructure] | 0.0074106 | 0 | 0
2026-03 | 2026-03-17 | Stouffville Well 1 & 2 | EAST | Onsite to check on Hypo TK 2 LIT Informed ROC Found Hypo TK2 LIT reading OOR , tank level at 1.45m Cycled power to LIT Reading OK now at 1.45m Informed ROC, armed building and left site | FLAG | stage2_low_confidence | 0.008054 | ML: above threshold (no LLM available) — 0.008 |  | 0.008054 | 0 | 0
2026-03 | 2026-03-28 | Ballantrae Well 1 & 2 | EAST | This is my first log entry! And now it's been updated! | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-26 | Stouffville Well 1 & 2 | EAST | On site for station check and silicate pump and board maintenance Isolated and depressurized the station header for work Hot flushed silicate pumps 1 and 2 from the suction side Pulled injection points, cleared and reinstalled Flushed silicate chemical board, PSV and PRVs Cleaned silicate pump 1 suction and discharge check valves Primed silicate lines and tested PRVs Re-pressurized station header after silicate pump maintenance Backflushed station header to purge excess silicate from priming operations Test ran well and both silicate pumps Station and equipment okay | FLAG | stage2_low_confidence | 0.018441 | ML: above threshold (no LLM available) — 0.018 |  | 0.018441 | 0 | 0
2026-03 | 2026-03-31 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11705392) - Hypo receiving Data in PWQ Workbook *100 L of hypo received Pre fill L: 321 L Post fill L: 421 L Regulatory samples TW and Raw well 2 taken @ 10:31 hrs. , Raw well 1 taken @ 11:15 hrs. Influent Grab @ 10:28 hrs. FCl: 1.96 mg/L Analyzer: FCl: 2.00 mg/L Effluent Grabs @ 10:31 hrs. FCl: 1.62 mg/L TCl: 1.84 mg/L Analyzer: FCl: 1.63 mg/L @ 10:35 hrs. Placed well pump 2 in manual off @ 10:46 hrs. placed well pump 1 in manual on for raw water sample @ 11:15 hrs. changed well pump 1 to duty 1 and well pump 2 to duty 2. placed well pumps 1 and 2 in auto. Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-11 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou @ 10:59 hrs. well pump 1 in auto @ 11:12 hrs. well pump 2 in auto Duty inactive. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0025392 | 0 | 0
2026-03 | 2026-03-04 | Ballantrae Well 1 & 2 | EAST | On site to top up silicate bulk tank. Start level: 32.9 cm Stop level: 39.9 cm The hot water heater is not working, informed onsite contractor and consultant Adil. | FLAG | stage2_low_confidence | 0.01479 | ML: above threshold (no LLM available) — 0.015 | not working [equipment_failure] | 0.01479 | 0 | 0
2026-03 | 2026-03-06 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 12:22 hrs. FCl: 1.96 mg/L Analyzer: FCl: 1.98 mg/L Effluent Grabs @ 12:26 hrs. FCl: 1.84 mg/L TCl: 2.50 mg/L Analyzer: FCl: 1.85 mg/L Pump 2 active in duty 1 Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-04 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou Remotely Started well pump 1 manually for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037447 | 0 | 0
2026-03 | 2026-03-09 | Ballantrae Well 1 & 2 | EAST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-09 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Operational sampling, iron Data in PWQ Workbook Influent Grab @ 12:50 hrs. FCl: 2.10 mg/L Analyzer: FCl: 2.04 mg/L Effluent Grabs @ 12:47 hrs. FCl: 1.94 mg/L TCl: 2.44 mg/L Analyzer: FCl: 1.88 mg/L Pump 2 active in duty 1 Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-11 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11656809) Data in PWQ Workbook @ 08:23 placed well pumps 1 and 2 in manual off to repair silicate injection point. Replaced parker fitting on injection quill, silicate pump 2 line. @ 09:05 hrs. placed well pump 2 in manual on Regulatory samples TW and Raw well 1 taken @ 09:37, Raw well 2 taken @ 10:25 hrs. Influent Grab @ 09:37 hrs FCl: 2.10 mg/L Analyzer: FCl: 2.07 mg/L Effluent Grabs @ 09:37 hrs. FCl: 1.89 mg/L TCl: 2.50 mg/L Analyzer: FCl: 1.97 mg/L @ 09:43 hrs. Placed well pump 2 in manual off @ 09:55 hrs. placed well pump 1 in manual on for raw water sample Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action]; regulatory [regulatory] | oos [equipment_failure]; repair [maintenance_action]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-10 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for PM's; - Generator test run and inspection - JHSC Health and safety inspections - CL-17 influent and effluent clean/maintenance - Turbidity analyzer clean/maintenance/calibration - Silicate system inspection and maintenance - Hypo delivery receiving - Sodium hypochlorite system inspection and maintenance @ 10:30 hrs. placed well pumps in manual off for generator test run prep Generator test run: Start Fuel: 1014 L Stop Fuel: 998 L Start Hours: 1023.2 Stop Hours: 1024.8 Start Time: 10:36 hrs. Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 10:31 hrs. Switched ATS to Test for generator power @ 11:22 hrs. Placed generator under facility load Well pump 2 in Manual ON *Well pump 1 interlocked due to generator running. Informed ON Call PCS operator Kyle Carlen. Interlock disengages once power is switched to facility power. Start Fuel: 1017 L Stop Fuel: 997 L Start Hours: 658.5 Stop Hours: 650.1 Start Time: 10:31 hrs. *under load* Operating Current: 59 Amps Operating Frequency: 60 Hz Operating Voltage: 570 Volts Engine speed: 1525 RPM Water/coolant Temp: 160 f Oil Pressure: 60 kpa Oil Temperature: 175 f @ 12:00 hrs. placed well pump 2 in manual off for ATS switch @ 12:02 hrs. Toggled ATS to normal @ 12:07 power switched to station power @ 12:14 cooldown stopped Chlorine analyzer maintenance on AIT 1 and 2, well pumps 1 and 2 in manual off, no flow directed to users. Start Clean @ 10:40 hrs. Exited Clean @ 11:10 hrs. Effluent (Treated Water) AIT verification Grab @ 11:17 hrs. FCl: 1.81 mg/L Analyzer FCl: 1.83 mg/L Influent AIT verification Grab @ 11:19 hrs. FCl: 1.89 mg/L Analyzer FCl: 1.87 mg/L Turbidity analyzer maintenance: Start @ 11:01hrs. Stop @ 11:09 hrs. @ 15:17 returned well pumps 1 and 2 to auto Well pump 2 active in Duty 1 @ 15:31 hrs. influent hihi, on well start up, came down next reading | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure]; leak [infrastructure] | 1.9154e-05 | 0 | 0
2026-03 | 2026-03-04 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11637232) Data in PWQ Workbook Regulatory samples TW and Raw well 1 taken @ 14:16, Raw well 2 taken @ 14:36 Regulatory sample Raw well 2 taken @ Influent Grab @ 14:21 hrs FCl: 2.20 mg/L Analyzer: FCl: 2.12 mg/L Effluent Grabs @ 14:16 FCl: 1.89 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.84 @ 14:22 Placed well pump 1 in auto, duty inactive @ 14:27 placed well pump 2 in manual on for raw water sample Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-02 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 15:11 hrs FCl: 1.79 mg/L Analyzer: FCl: 1.77 mg/L Effluent Grabs @ 15:16 FCl: 1.73 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.74 Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-13 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 09:01 hrs. FCl: 1.67 mg/L Analyzer: FCl: 1.68 mg/L Effluent Grabs @ 09:05 hrs. FCl: 1.69 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.64 mg/L Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-15 | Ballantrae Well 1 & 2 | EAST | On site responding to VFD fault alarm on both pumps due to power outage. Both pumps faulted on "Over Current" on VFD. Was able to reset the faults. Duty was active, W2 back into auto, duty 1 and active. No further issues. | FLAG | stage2_low_confidence | 0.046037 | ML: above threshold (no LLM available) — 0.046 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] | 0.046037 | 0 | 0
2026-03 | 2026-03-18 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11672695) Data in PWQ Workbook Silicate pump 1 not drawing silicate. Placed pump in manual off. Removed airlock from pump. Placed pump back in auto. Regulatory samples TW and Raw well 1 taken @ 14:01 hrs. , Raw well 2 taken @ 14:50 hrs. Influent Grab @ 13:55 hrs FCl: 1.98 mg/L Analyzer: FCl: 1.99 mg/L Effluent Grabs @ 14:01 hrs. FCl: 1.89 mg/L TCl: 2.71 mg/L Analyzer: FCl: 1.81 mg/L @ 14:06 hrs. Placed well pump 2 in manual off @ 14:16 hrs. placed well pump 1 in manual on for raw water sample Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-25 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou 13:07 hrs. Started well pump 1 for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030434 | 0 | 0
2026-03 | 2026-03-18 | Ballantrae Well 1 & 2 | EAST | @ 15:20 hrs. Stopped well pump 2 and placed well pumps 1 and 2 in auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043164 | 0 | 0
2026-03 | 2026-03-17 | Ballantrae Well 1 & 2 | EAST | ROC called regarding high station turbidity while W2 was running. Turbidity over 1.00ntu. Manually stopped W2. Investigated Turbidity Analyzer, cleaned vial and turbidity value dropped to below 0.5ntu. Checked silicate pumps, no issues with pumps. Silicate dose in PWQ sheet, dose within range. Placed W1 into duty 1 and monitored start up. Turbidity value dropping below 0.45ntu. Will inform operations tomorrow to observe W2 operation and treated turbidity. W1 currently running and turbidity value <0.45ntu and still dropping. | FLAG | stage2_low_confidence | 0.047969 | ML: above threshold (no LLM available) — 0.048 |  | 0.047969 | 0 | 0
2026-03 | 2026-03-23 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou @ 07:30 hrs. Placed well pumps 1 and 2 in manual off in preparation for March 24, 2026 step test. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003915 | 0 | 0
2026-03 | 2026-03-26 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 13:08 hrs. FCl: 2.01 mg/L Analyzer: FCl: 2.05 mg/L Effluent Grabs @ 13:11 hrs. FCl: 1.82 mg/L TCl: 2.09 mg/L Analyzer: FCl: 1.85 mg/L Well pump 1 in duty 1 Duty active Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-16 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ Workbook Influent Grab @ 09:46 hrs. FCl: 1.66 mg/L Analyzer: FCl: 1.63 mg/L Effluent Grabs @ 09:51 hrs. FCl: 1.62 mg/L TCl: 1.95 mg/L Analyzer: FCl: 1.59 mg/L Changed buffer and analyzer reagents for influent and effluent AIT Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-19 | Ballantrae Well 1 & 2 | EAST | Under Direction of OIC (Patrick Fobert) On site for Hypo Receiving Tank 1; Start cm: 55.34 cm Stop cm: 82.61 cm Start V: not observed L Stop V: 427 L Upon logging into SCADA onsite see silicate pump 1 has failed to start alarm. Checked pump, analog setting in place but not back in analog mode, pressed stop button to set pump in analog. | FLAG | stage2_low_confidence | 0.015761 | ML: above threshold (no LLM available) — 0.016 | failed [equipment_failure]; scada [control_system]; alarm [control_system] | 0.015761 | 0 | 0
2026-03 | 2026-03-20 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Patrick Fobert On site to isolate service line, valved at backflow preventer for new service line tie in. | FLAG | stage2_low_confidence | 0.013066 | ML: above threshold (no LLM available) — 0.013 |  | 0.013066 | 0 | 0
2026-03 | 2026-03-23 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 14:42 hrs. FCl: 1.66 mg/L Analyzer: FCl: 1.64 mg/L Effluent Grabs @ 14:44 hrs. FCl: 1.55 mg/L TCl: 1.83 mg/L Analyzer: FCl: 1.55 mg/L Well pumps 1 and 2 in manual off. Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-20 | Ballantrae Well 1 & 2 | EAST | On site to facilitate and assist with construction project station power outage and replacement of main breaker and associated testing upon completion. | FLAG | stage2_low_confidence | 0.032691 | ML: above threshold (no LLM available) — 0.033 | sso [critical] | 0.032691 | 0 | 0
2026-03 | 2026-03-25 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou Placed well pumps 1 and 2 in auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034804 | 0 | 0
2026-03 | 2026-03-18 | Ballantrae Well 1 & 2 | EAST | @ 13:01 placed well pump 1 in manual on for regulatory sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0063914 | 0 | 0
2026-03 | 2026-03-20 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Patrick Fobert On site for service line tie in verification and re-pressurization of service line at backflow preventer. Ball valve placed by contractor down stream of backflow preventer for additional tie ins. | FLAG | stage2_low_confidence | 0.021189 | ML: above threshold (no LLM available) — 0.021 |  | 0.021189 | 0 | 0
2026-03 | 2026-03-25 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11690078) - Operational sampling, (iron, FCl, TCl, NTU, Temp) Data in PWQ Workbook Regulatory samples TW and Raw well 1 taken @ 14:20 hrs. , Raw well 2 taken @ 15:05 hrs. Influent Grab @ 14:19 hrs. FCl: 1.92 mg/L Analyzer: FCl: 1.95 mg/L Effluent Grabs @ 14:20 hrs. FCl: 1.84 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.83 mg/L @ 14:31 hrs. Placed well pump 2 in manual off Changed duty 1 to well pump 2 and duty 2 to well pump 1 @ 14:39 hrs. placed well pump 1 in manual on for raw water sample Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-24 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Dan Zhou On site for; - Step test (On site with Leanne Paterson from water resources) Step test Part 1 @ 08:55 hrs. changed well setpoint for well pump 1 to 10 L/s @ 09:05 hrs. started well pump 1 for part 1 of step test Step test Part 2 @ 10:05 hrs. changed well setpoint for well pump 1 to 20 L/s Step test Part 3 @ 11:05 changed well setpoint for well pump 1 to 31 L/s @ 12:05 hrs. returned well pump 1 to auto, and well setpoint to 30 L/s, and well pump 2 to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034097 | 0 | 0
2026-03 | 2026-03-24 | Ballantrae Well 1 & 2 | EAST | Under Direction of OIC (Dan Zhou) On site for Hypo Receiving Tank 1; Start cm: 67.9 cm Stop cm: 84.5 cm Start V: 351 L Stop V: 437 L Total Volume received = 86 L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0028194 | 0 | 0
2026-03 | 2026-03-20 | Ballantrae Well 1 & 2 | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ Workbook Well 1 in manual ON for grabs Influent Grab @ 14:18 hrs. FCl: 1.98 mg/L Analyzer: FCl: 1.96 mg/L Effluent Grabs @ 14:20 hrs. FCl: 1.81 mg/L TCl: 2.00 mg/L Analyzer: FCl: 1.77 mg/L @ 14:26 placed well pumps 1 and 2 in auto Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-19 | Ballantrae Well 1 & 2 | EAST | Silicate top up (36.3 to 48.1cm) | FLAG | stage2_low_confidence | 0.0096997 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096997 | 0 | 0
2026-03 | 2026-03-28 | Ballantrae Well 3 | EAST | Time in: 08:10 On site to support contractor to repair the leak on chlorine solution line #2. Engaged E-Stop for chlorine booster pump 2. Depressurized the chlorine solution line 1&2. Contractor applied coatings on the leaky spot for line #2. I replaced the leaky ball valve on chlorine #1 line. Primed chlorine line #1. Tested chlorinator #1 vacuum, it responds well. Opened cylinders, tested chlorinators in local and remote, no issue. Man/Start well 3. Switched silicate pump to #2 to check it's operation, no issue. Verified chlorinator 1 performance, it is dosing at 50%, 25 ppd, vacuum = -90 mbar. Chlorine booster pump 1 discharge pressure = 210 psi. 09:33 verified chlorine analyzer readings: Grab influent = 2.15 mg/l, analyzer = 2.11 mg/l Grab effluent = 1.48 mg/l, analyzer = 1.51 mg/l. Will place well 3 to auto remotely. Time out: 09:55 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action]; leak [infrastructure] | oos [equipment_failure]; repair [maintenance_action]; leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-31 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou @ 11:17 hrs. Placed well pump 3 in manual on for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032573 | 0 | 0
2026-03 | 2026-03-31 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11705392) Data in PWQ workbook Regulatory samples taken @ 11:57 hrs. Influent grabs @ 11:54 hrs. FCl: 2.10 mg/L Analyzer: FCl: 2.18 mg/L Effluent Grabs @ 11:57 hrs. FCl: 1.35 mg/L TCl: 1.67 mg/L Analyzer: FCl: 1.39 mg/L NTU: 0.027 @ 12:04 hrs. placed well pump 3 in auto Duty inactive Well pump 4 in local Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-03 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for PM's - AIT maintenance and clean, effluent and influent - Turbidity analyzer maintenance and clean - Repair AIT line to sight glass and fix leak at y-screen Chlorine analyzer maintenance: Start clean @ 12:43 hrs. Stop clean @ 13:36 hrs. Disregard lo influent and effluent alarm, due to low flow to analyzer and no water directed to users. Adjusted flow. Replaced broken parker fitting on effluent sight glass with 1/2 inch fast and tite, cleaned up flooded area Analyzer verification: Effluent grab @ 13:58 FCl: 1.39 mg/L Analyzer: FCl: 1.42 mg/L Influent grab @ 13:03 FCl: 1.45 mg/L Analyzer: FCl: 1.43 mg/L Tubidity meter maintenance: Start @ 12:55 hrs. Stop @ 13:07 hrs. @ 14:07 hrs. manually activated well 3 @ 14:40 hrs. Returned well 3 to auto, duty deactivated | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | flood [critical]; repair [maintenance_action]; alarm [control_system]; leak [infrastructure] | 0.00080812 | 0 | 0
2026-03 | 2026-03-30 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Test chlorine train 2 system for leaks, place back in service @ 09:05 hrs. informed ROC of chlorine system work @ 09:10 hrs. place BP2 in local on to test for leaks, chlorine cylinders and regulators closed, (no dosing of raw water for leak test) -no leaks observed in chlorine train 2, vacuum produced - Re opened chlorine cylinders and regulators - Placed chlorine train 2 in duty 1 @ 09:26 placed well pump 3 in manual on @ 09:50 hrs. stopped well pump 3, check valve flag showed as closed. @ 10:26 hrs. - Verified by senior OIC team lead Dan Zhou that the flag indicator on the check valve is broken - Restarted well and verified equal pressures before and after check valve and flow rate on FIT verified chlorine system with grabs Effluent: Grab @ 11:31 hrs. FCl: 1.54 m g/L Effluent analyzer FCl: 1.59 mg/L Influent: Grab @ 11:21 hrs. FCl: 2.18 mg/L Analyzer: 2.23 mg/L @ 11:38 hrs. placed well pump 3 in auto, duty inactive System functional Equipment OOS: None Station OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; leak [infrastructure] | oos [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11656809) Data in PWQ workbook @ 13:07 placed well pump 3 in manual on Regulatory samples taken @ 10:47 hrs. Influent grabs @ 10:50 hrs. Influent: FCl: 2.12 mg/L Analyzer: FCl: 2.18 mg/L Effluent Grabs @ 10:47 hrs. FCl: 1.45 mg/L TCl: 1.75 mg/L Analyzer: FCl: 1.46 mg/L NTU: 0.017 @ 11:00 hrs. placed well pump 3 in auto Duty inactive Well pump 4 in local (not commissioned yet) Duty Inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-11 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou @ 10:14 hrs. placed well pump 3 in manual on for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032573 | 0 | 0
2026-03 | 2026-03-06 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Supply fan 1 check - Exhaust fan check - Chlorine leak detector test - Chlorine emergency repair kit inspection - Chlorine scrubber check and inspection - Low temp alarm test - Pump 3 oil drip top up Data in PWQ workbook Duty active for grabs Influent grabs @ 13:15 hrs. Influent: FCl: 2.14 mg/L Analyzer: FCl: 2.19 mg/L Effluent Grabs @ 13:20 hrs. FCl: 1.43 mg/L TCl: 1.83 mg/L Analyzer: FCl: 1.48 mg/L NTU: 0.015 @ 13:47 hrs. duty deactivated, tower @ 92%, placed well pump 3 in manual, for pm's @ 13:49 hrs. raised low temp alarm setting, triggered building low temp alarm @ 13:51 hrs. @ 13:53 hrs. manually triggered chlorine leak alarm, scrubbers turned on, Cl2 gas monitor in silicate room and Cl2 gas room readings present Exhaust fans 1,2,3 triggered manually, louvers opened @ 14:43 hrs. returned well pump 3 to auto Well pump 4 in local (not commissioned yet) Duty Inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; oos [equipment_failure]; repair [maintenance_action]; alarm [control_system]; leak [infrastructure]; drip [infrastructure] | emergency [critical]; oos [equipment_failure]; repair [maintenance_action]; alarm [control_system]; leak [infrastructure]; drip [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | Ballantrae Well 3 | EAST | #11668224 Generator test: 12:14 Pre-Check complete 13:25 Start (412:25 hrs) 14:30 End (413:32 hrs) Fuel Start : 85.9cm (848L), 80.7cm (798L) Fuel End: 84.4cm (837L), 79.8cm(788L) 15:55 reading: 595volts, 75amps, 60hz, oil pres.57psi, coolant temp. 174F, 1800rpm #11718890, #11669695 silicate (hot flush completed ) Silicate top up (175L to 200L) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067568 | 0 | 0
2026-03 | 2026-03-04 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11637232) Data in PWQ workbook @ 13:07 placed well pump 3 in manual on Regulatory samples taken @ 13:30 Influent grabs @ 13:31 hrs. Influent: FCl: 2.10 mg/L Analyzer: FCl: 2.19 mg/L Effluent Grabs @ 13:30 hrs. FCl: 1.47 mg/L TCl: 1.78 mg/L Analyzer: FCl: 1.46 mg/L NTU: 0.017 @ 13:43 placed well pump 3 in auto Well pump 4 in local (not commissioned yet) Duty Inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-09 | Ballantrae Well 3 | EAST | Under direction of oic Dan Zhou @ 13:11 hrs. Returned well pump 3 to auto. Duty active. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032111 | 0 | 0
2026-03 | 2026-03-10 | Ballantrae Well 3 | EAST | Under direction of oic Jack Palmer. On site for Chlorine cylinder change. | FLAG | stage2_low_confidence | 0.014426 | ML: above threshold (no LLM available) — 0.014 |  | 0.014426 | 0 | 0
2026-03 | 2026-03-09 | Ballantrae Well 3 | EAST | McNamara fuel inspection | FLAG | stage2_low_confidence | 0.012327 | ML: above threshold (no LLM available) — 0.012 |  | 0.012327 | 0 | 0
2026-03 | 2026-03-16 | Ballantrae Well 3 | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ workbook Influent grabs @ 09:03 hrs. Influent: FCl: 1.42 mg/L Analyzer: FCl: 1.40 mg/L Effluent Grabs @ 09:05 hrs. FCl: 1.46 mg/L TCl: 1.65 mg/L Analyzer: FCl: 1.47 mg/L NTU: 0.03 Well pump 4 in local Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-25 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou @ 12:02 placed well pump 3 in manual on for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031822 | 0 | 0
2026-03 | 2026-03-20 | Ballantrae Well 3 | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ workbook Influent grabs @ 09:40 hrs. Influent: FCl: 1.43 mg/L Analyzer: FCl: 1.40 mg/L Effluent Grabs @ 09:43 hrs. FCl: 1.41 mg/L TCl: 1.64 mg/L Analyzer: FCl: 1.45 mg/L NTU: 0.03 Well pump 4 in local Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-25 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11690078) - Operational sampling, (iron, NTU, FCl, TCl, Temp) Data in PWQ workbook Regulatory samples taken @ 12:43 hrs. Influent grabs @ 12:40 hrs. FCl: 2.19 mg/L Analyzer: FCl: 2.22 mg/L Effluent Grabs @ 12:43 hrs. FCl: 1.49 mg/L TCl: 1.76 mg/L Analyzer: FCl: 1.51 mg/L NTU: 0.039 @ 13:08 hrs. placed well pump 3 in auto @ 13:12 informed ROC and placed well pump 3 in manual off for turbidity analyzer vial cleaning Turbidity analyzer vial cleaning: Clean start @ 13:14 hrs. Clean stop @ 13:30 hrs. @ 13:31 placed well pump 3 back in auto Duty inactive Well pump 4 in local Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-26 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for operator assistance with chemical line tie ins for well 4; - Sodium silicate flush and depressurize - Chlorine gas system purge and depressurize - Piping gallery depressurization - Station check Worked with OIC Dan Zhou, for operator assistance tasks @ 08:48 hrs. Informed ROC of well 3 shutdown and chemical line tie ins. Placed well pump 3 in local at PLC and in E-stop. Flushed silicate system with hot water. Depressurized silicate system, as drain valves remain open. Closed chlorine cylinders and placed chlorine regulators in off position. Purged chlorine gas system in local, using booster pump 1 for line 1 and then booster pump 2 for line 2, 5 minutes each. Valved close hypochlorous lines post chlorinator and pre injection to isolate for chemical line tie ins. Isolated well 3 at isolation valve Opened valve connections below tie in on chemical lines to verify depressurization of silicate line and hypochlorous acid line. Verified depressurization of piping gallery at raw water sample tap. Well isolated from distribution system. Witnessed chemical line tie ins. All valves closed for isolation are locked out and tagged out. Data in PWQ workbook Influent grabs @ 11:54 hrs. Influent: FCl: 1.60 mg/L Analyzer: FCl: 1.60 mg/L Effluent Grabs @ 11:55 hrs. FCl: 1.40 mg/L TCl: 1.65 mg/L Analyzer: FCl: 1.41 mg/L NTU: 0.039 Well pump 4 in local off, well pump 3 in local off/ E-stop, silicate pumps 1 and 2 in local/hand, chlorine booster pumps 1 and 2 in local off/E-stop. Systems interlocked and facility shutdown until March 27 Equipment OOS: Well pumps 3,4 and chlorine booster pumps 1 and 2, station offline Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-13 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ workbook Duty active for grabs Influent grabs @ 10:24 hrs. Influent: FCl: 1.44 mg/L Analyzer: FCl: 1.44 mg/L Effluent Grabs @ 10:29 hrs. FCl: 1.54 mg/L TCl: 1.67 mg/L Analyzer: FCl: 1.55 mg/L NTU: 0.030 Well pump 4 in local Duty inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-02 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - JHSC health and safety inspection Data in PWQ workbook Influent grabs @ 13:38 hrs. Influent: FCl: 1.76 mg/L, 1.76 mg/L, 1.75 mg/L *Adjusted influent analyzer to 1.75 mg/L Analyzer: FCl: 1.62 mg/L Effluent Grabs @ 13:47 hrs. FCl: 1.70 mg/L TCl: 2.05 mg/L Analyzer: FCl: 1.73 mg/L NTU: 0.088 NTU pre clean NTU: 0.015 NTU post clean @ 13:55 hrs. placed well pump 3 in manual off to clean turbidity analyzer, water not going to users. Disregard any turbidity alarm. @ 14:13 hrs. returned pump 3 to auto Changed influent analyzer reagents, indicator and buffer Well pump 4 in local (not commissioned yet) Duty Inactive Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks - Operational sampling Data in PWQ workbook Duty active for grabs Influent grabs @ 13:27 hrs. Influent: FCl: 2.44 mg/L Analyzer: FCl: 2.50 mg/L Effluent Grabs @ 13:30 hrs. FCl: 1.49 mg/L TCl: 1.77 mg/L Analyzer: FCl: 1.46 mg/L NTU: 0.016 Well pump 4 in local (not commissioned yet) Well pump 3 Active in Duty 1 Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-09 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou Placed well pump 3 in manual off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034586 | 0 | 0
2026-03 | 2026-03-04 | Ballantrae Well 3 | EAST | Onsite to top up silicate day tank. Start: 80l Stop: 210 L Switch silicate pump duty since #1 is not dosing correctly. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058374 | 0 | 0
2026-03 | 2026-03-11 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou @ 08:25 hrs. Placed well pump 3 in manual off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030856 | 0 | 0
2026-03 | 2026-03-18 | Ballantrae Well 3 | EAST | Under direction of OIC Patrick Fobert On site for; - Station checks - Regulatory sampling, micro (W11672695) Data in PWQ workbook Regulatory samples taken @ 12:53 hrs. Influent grabs @ 12:51 hrs. FCl: 2.18 mg/L Analyzer: FCl: 2.22 mg/L Effluent Grabs @ 12:53 hrs. FCl: 1.44 mg/L TCl: 1.72 mg/L Analyzer: FCl: 1.46 mg/L NTU: 0.042 @ 13:01 hrs. placed well pump 3 in auto Duty inactive Well pump 4 in local (not commissioned yet) Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; regulatory [regulatory] | oos [equipment_failure]; regulatory [regulatory] |  | 1 | 0
2026-03 | 2026-03-24 | Ballantrae Well 3 | EAST | On site to swap ejector #1 on chlorine train #1. Purged chlorine system for work, replaced ejector. Tested chlorine system after swap, and tested well #3 in manual. Station operations normal | FLAG | stage2_low_confidence | 0.015661 | ML: above threshold (no LLM available) — 0.016 |  | 0.015661 | 0 | 0
2026-03 | 2026-03-19 | Ballantrae Well 3 | EAST | Silicate top up (150 to 200L) | FLAG | stage2_low_confidence | 0.0095777 | ML: above threshold (no LLM available) — 0.01 |  | 0.0095777 | 0 | 0
2026-03 | 2026-03-18 | Ballantrae Well 3 | EAST | Under direction of OIC Patrick Fobert @ 12:10 hrs. Placed well pump 3 in manual on for regulatory sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | regulatory [regulatory] | 0.0054056 | 0 | 0
2026-03 | 2026-03-23 | Ballantrae Well 3 | EAST | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ workbook Influent grabs @ 13:51 hrs. Influent: FCl: 2.18 mg/L Analyzer: FCl: 2.22 mg/L Effluent Grabs @ 13:57 hrs. FCl: 1.52 mg/L TCl: 1.86 mg/L Analyzer: FCl: 1.55 mg/L NTU: 0.085 Changed buffer and analyzer reagents for effluent AIT. Well pump 4 in local Duty active Equipment OOS: None Facility OK | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-31 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for BacT sampling W11706508 Collected well 5 raw sample, 12:56 Collected treated water sample, 13:05, and verified free chlorine analyzer, in mg/L FCl - G 1.73; A 1.76 TCl - G 1.94 Collected well 6 raw sample, 13:10 Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035665 | 0 | 0
2026-03 | 2026-03-21 | Ballantrae Well 3 | EAST | On site responding to Influent Lolo chlorine lockout. CMU5 #W11749880 Arrived on site @16:30 and took grab residuals on Influent: Grab: 0.09 mg/L / Analyzer: 0.05 mg/L Set up backflushing hose around the back of the building to that waste man hole and started backflushing @14:43 Well had been running from 23:26 yesterday until 00:53 today. Influent chlorine had been stable from 23:30 to 00:43, when it suddenly started decking until it locked out @00:53. Chlorinator #1 had been running, trends look stable. Tested chlorine train #1 in local, and did not observe any issues. @17:28 stopped backflushing - Analyzer is reading 1.29 mg/L on Influent @17:33 started well #3 in manual to test well operation Chlorine train #1 is left OOS for the rest of the weekend. Will further investigate next week. Leaving well #3 running in manual - requested ROC to place well back to auto after 30 minutes @18:15 Station operation okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-27 | Ballantrae Well 3 | EAST | On site to bring well 3 back online after chemical line work by contractors. Primed and tested both silicate lines. Primed and tested both chlorine solutions lines. Chlorine train 1?s isolation ball valve in chlorinator room is leaking slightly, tried to tighten it, not able to seal. Left chlorine #1 system in local off. Tested chlorine train 2 in local and remote, noticed the vacuum gauge is stuck in high vacuum. Will issue work order to INST. Shelved the chlorinator 2 high vacuum alarm in order to run chlorine #2 system. Backflushed well 3 for a few minutes. Man/start well 3, checked silicate #1 operation, no issues. While checking chlorine #2 performances, noticed a leak at the new elbow. Notified Jason G. (ETO). Placed well 3 Local Off. Isolated both gas cylinders. Purged chlorine line 2 with system water. Contractors are coming back to site tomorrow morning to address cl2 line 2 leak. Well 3 remains OOS for the night. Informed ROC. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-30 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check Recorded observations in the shared PWQ sheet Verified reservoir influent and effluent free chlorine analyzers - see PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.013487 | ML: above threshold (no LLM available) — 0.013 |  | 0.013487 | 0 | 0
2026-03 | 2026-03-09 | Stouffville Reservoir and Wells 5 & 6 | EAST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-11 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for sampling and station check Sampling work orders: Micro samples W11656903 HAA W11707190 Collected well 5 raw, 12:30 Collected well 6 raw, 12:20 Collected STRS48 treated water samples, 12:55 FCl G 1.82; A 1.80 TCl G 2.02 Recorded observations in the shared PWQ sheet Rotated reservoirs for sampling Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.0037484 | 0 | 0
2026-03 | 2026-03-10 | Stouffville Reservoir and Wells 5 & 6 | EAST | Macnamarra fuel inspection | FLAG | stage2_low_confidence | 0.012436 | ML: above threshold (no LLM available) — 0.012 |  | 0.012436 | 0 | 0
2026-03 | 2026-03-13 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and equipment verification Duty is not active - reservoir level is 84% Recorded data in PWQ sheets Verified CL-17 analyzer readings @09:10 to 09:19 (Grab / Analyzer mg/L) Influent FCL: 1.95 / 2.03 Effluent FCL: 1.76 / 1.78 Effluent TCL: 1.93 No adjustments needed Reviewed trends, equipment OOS: none Station operation normal | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-02 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check Verified post injection FCl, 9:45, mg/L G 1.94; A 1.99 Verified effluent free FCl, 10:39, mg/L G 1.66; A 1.70 Effluent TCl grab: 1.87 Recorded observations in the station PWQ sheet Changed chlorine cylinder bank 2 with Dan Zhou, verified regulator function Switched influent sample line to reservoir Performed visual inspection of equipment, chemical system, sample pumps, all okay Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026199 | 0 | 0
2026-03 | 2026-03-10 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for CMU5 W11722310 Hi lift pump 2 fail to stop Attended site with Sean Peoples (Electrical) and worked with Ian Williams (remote, PCS) Sean opened limit switch on P2 FCV and the pump stopped. Test ran the pump for three cycles and found no issues starting and stopping HLP2 back in service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-03 | 2026-03-04 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and sampling W11637348 Collected well 5 raw, 12:45 Collected reservoir treated, 12:58, and verified free chlorine analyzer: FCl G 1.78; A 1.79 mg/L; TCl G 1.93 mg/L Collected well 6 raw, 13:10 Recorded observations and process analyzer verification in the shared PWQ sheet. Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071831 | 0 | 0
2026-03 | 2026-03-25 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site to install halogen system. | FLAG | stage2_low_confidence | 0.01204 | ML: above threshold (no LLM available) — 0.012 |  | 0.01204 | 0 | 0
2026-03 | 2026-03-20 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for facility station check and equipment verifications and to collect well #5 raw resample for YD lab (W11746801) High lift pump #2 running in manual - 52 L/s Wells duty is active - res level is 81% Recorded data in PWQ sheets Verified analyzer readings: @0915-0920 Influent FCL: 1.98 / 1.94 Effluent FCL: 1.80 / 1.82 Effluent TCL: 1.95 Collected well #5 raw sample @09:10 Reviewed trends, equipment ok Placed high lift pump 2 back to auto Station operation normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057672 | 0 | 0
2026-03 | 2026-03-25 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and sampling W11690172 Verified reservoir influent free chlorine analyzer and collected well 5 raw water sample, 11:45, in mg/L FCl - G 2.09; A 2.08 Collected reservoir effluent sample and verified free chlorine analyzer, 12:02, in mg/L FCl - G 1.70; A 1.77 TCl - G 1.94 Collected well 6 raw water sample, 12:12. Replaced influent and effluent free chlorine analyzer reagents Recorded observations in the shared PWQ sheet Ferguson Electric on site working on generator flashing and insulation Electrician Ernesto Hidalgo on site working on emergency halogen shut off system Station and equipment okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-03 | 2026-03-17 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for preventative maintenance Completed Chlorine scrubber inspection Chlorine system inspection Chlorine leak emergency kit inspection Chlorine analyzer cleaning (post injection) Housekeeping Station and equipment okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; leak [infrastructure] | emergency [critical]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-27 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site to install halogen system | FLAG | stage2_low_confidence | 0.011989 | ML: above threshold (no LLM available) — 0.012 |  | 0.011989 | 0 | 0
2026-03 | 2026-03-18 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check and sampling W11672797 Collected treated sample, 13:28, and verified free chlorine analyzer (mg/L) FCl - G 1.76; A 1.76 TCl - G 1.94 Collected well 5 raw, 13:32 Collected well 6 raw, 13:45 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035021 | 0 | 0
2026-03 | 2026-03-26 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site to work on halogen system installation. | FLAG | stage2_low_confidence | 0.012812 | ML: above threshold (no LLM available) — 0.013 |  | 0.012812 | 0 | 0
2026-03 | 2026-03-23 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for station check Recorded observations in the shared PWQ sheet Rotated reservoir sample line and pump Station and equipment okay | FLAG | stage2_low_confidence | 0.011182 | ML: above threshold (no LLM available) — 0.011 |  | 0.011182 | 0 | 0
2026-03 | 2026-03-05 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for preventative maintenance work orders Completed Generator test run JHSC inspection Chlorine analyzer maintenance Turbidity analyzer maintenance Housekeeping Genset: Performed pre and post run inspection Fuel Start 3098 L Stop 3064 L Hours Start 14.25 Stop 16.55 Reviewed genset run statistics - okay Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | work order [maintenance_action] | 0.00082828 | 0 | 0
2026-03 | 2026-03-16 | Stouffville Reservoir and Wells 5 & 6 | EAST | On site for facility station check and equipment verifications Duty is not active for reservoir or high lift - res level is 84% Recorded data in PWQ sheets Reset fault on sample pump #1 - showing overcurrent fault on display Changed chlorine cylinders with Jack P (Left) tested for leaks, none observed Verified analyzer readings with grab residuals (Grab/Analyzer mg/L Influent FCL: 1.85 / 1.89 Effluent FCL: 1.81 / 1.79 Effluent TCL: 1.92 Reviewed trends, equipment ok Station ok | FLAG | stage2_low_confidence | 0.020608 | ML: above threshold (no LLM available) — 0.021 | fault [equipment_failure]; leak [infrastructure] | 0.020608 | 0 | 0
2026-03 | 2026-03-30 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check Verified free chlorine analyzer and recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.013151 | ML: above threshold (no LLM available) — 0.013 |  | 0.013151 | 0 | 0
2026-03 | 2026-03-13 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check and equipment verifications Recorded data in PWQ sheets Ran air compressor in hand to draw down level in pressure tanks a bit Verified analyzer reading - no adjustments needed Reviewed trends, equipment ok Station ok | FLAG | stage2_low_confidence | 0.020027 | ML: above threshold (no LLM available) — 0.02 | sso [critical] | 0.020027 | 0 | 0
2026-03 | 2026-03-02 | Stouffville Highway 48 Booster Pumping Station | EAST | Verified effluent FCl, 10:26, in mg/L G 1.66; A 1.63 TCl grab: 1.79 Checked pressure tanks, inspected pipes, sensors, gauges and analyzers, all okay and meeting expectations. Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050599 | 0 | 0
2026-03 | 2026-03-05 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for preventative maintenance Completed Chlorine analyzer maintenance Turbidity analyzer maintenance Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063622 | 0 | 0
2026-03 | 2026-03-06 | Stouffville Highway 48 Booster Pumping Station | EAST | Attended site for station check Recorded observations and analyzer verification in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.013761 | ML: above threshold (no LLM available) — 0.014 |  | 0.013761 | 0 | 0
2026-03 | 2026-03-20 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for facility station check Readings in PWQ sheets Verified CL-17 analyzer reading Checked site and equipment Station ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067281 | 0 | 0
2026-03 | 2026-03-16 | Stouffville Highway 48 Booster Pumping Station | EAST | On site for station check and equipment verifications Recorded readings in PWQ sheets Verified analyzer readings with grab residuals @09:25 Grab FCL: 1.55 mg/L / Analyzer: 1.53 mg/L Grab TCL: 1.63 mg/L Station and equipment ok | FLAG | stage2_low_confidence | 0.0074077 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074077 | 0 | 0
2026-03 | 2026-03-26 | Stouffville Highway 48 Booster Pumping Station | EAST | Attended site for station check Verified free chlorine analyzer, 14:53, mg/L Effluent FCl - G 1.68; A 1.75 Effluent TCl - G 1.92 Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070467 | 0 | 0
2026-03 | 2026-03-02 | King City Wells 3 & 4 | WEST | -on site to complete station check -site out of service -site secure -no issues found | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-23 | Stouffville Highway 48 Booster Pumping Station | EAST | Attended site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | FLAG | stage2_low_confidence | 0.012228 | ML: above threshold (no LLM available) — 0.012 |  | 0.012228 | 0 | 0
2026-03 | 2026-03-09 | King City Wells 3 & 4 | WEST | -on site to complete station check -site out of service -site secure -no issues found -completed JHSC Health and Safety Inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-23 | King City Wells 3 & 4 | WEST | On site to check station. Site offline, facility secure. | FLAG | stage2_low_confidence | 0.013322 | ML: above threshold (no LLM available) — 0.013 |  | 0.013322 | 0 | 0
2026-03 | 2026-03-17 | King City Wells 3 & 4 | WEST | On site to inspect facility, no issues on site. | FLAG | stage2_low_confidence | 0.012797 | ML: above threshold (no LLM available) — 0.013 |  | 0.012797 | 0 | 0
2026-03 | 2026-03-04 | Kleinburg Wells 3 and 4 | WEST | -on site to complete station check and collect samples -sample work order # W11637596 -site offline and isolated from distribution system 09:47 - started well #3 in local running to waste at 25.5 l/s 09:47 - started well #4 in local running to waste at 26.5 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:57 - Analyzer readings: Free Chlorine = 0.01 mg/L Total Chlorine = 1.91 mg/L 09:57 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.86 mg/L 10:24 - collected weekly well #3 raw water micro. sample 10:24 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | FLAG | stage2_low_confidence | 0.0089004 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action] | 0.0089004 | 0 | 0
2026-03 | 2026-03-31 | Kleinburg Wells 3 and 4 | WEST | -on site to complete station check and collect samples -sample work order # W11705756 -site offline and isolated from distribution system 09:30 - started well #3 in local running to waste at 25.6 l/s 09:30 - started well #4 in local running to waste at 26.7 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:34 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.92 mg/L 09:34 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.92 mg/L 10:02- collected weekly well #3 raw water micro. sample 10:02 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | FLAG | stage2_low_confidence | 0.0088308 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action] | 0.0088308 | 0 | 0
2026-03 | 2026-03-10 | Kleinburg Wells 3 and 4 | WEST | -on site to complete work orders -informed ROC of work -completed Diesel Generator Test Run -pre inspection ok 09:01 - transfer to generator power -ran KLPSWL pump #3 on generator power Start hours = 417.3 Stop hours = 418.6 Run time = 1.3 hours Start fuel = 1928 L Stop fuel = 1876 L Fuel used = 52 L -completed Deep Well Exhaust Valve, Maintenance -completed Pressure Relief Valve, Inspection -completed Turbidimeter Maintenance -cleaned and verified turbidimeter -completed Chlorine Analyzer, Maintenance -checked grit sand and electrolyte -flushed sample lines -zero calibrated influent and effluent FCL analyzers -verified analyzers after maintenance 09:52 - influent analyzer = 0.01 mg/L grab = 0.03 mg/L 09:54 - effluent analyzer = 0.00 mg/L grab = 0.02 mg/L 09:56 - Treated Analyzer readings: Free Chlorine = 0.01 mg/L Total Chlorine = 1.94 mg/L 09:56 - Treated Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.96 mg/L -completed Ventilation System - Exhaust Fans 10:09 - transfer back to utility power -no issues with generator test run -completed JHSC Health and Safety Inspection, Kleinburg Well 3/4 and Whisper Lane -completed Chlorine Cylinder Emergency Repair Kit Inspection -completed Manual Valve, Exercise -completed Chlorine Scrubber, Check -completed Chlorine Leak Detector, Test -completed Chemical System Inspection - Silicate -completed Ammonia System, Inspection -completed Chemical System Inspection - Chlorine -no issues, site back to normal operation | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action]; repair [maintenance_action]; leak [infrastructure] | emergency [critical]; work order [maintenance_action]; repair [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | Kleinburg Wells 3 and 4 | WEST | -on site to complete station check and collect samples -site offline and isolated from distribution system 08:37 - started well #3 in local running to waste at 25.5 l/s 08:37 - started well #4 in local running to waste at 26.7 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 08:42 - Analyzer readings: Free Chlorine = 0.01 mg/L Total Chlorine = 1.91 mg/L 08:42 - Grabs: Free Chlorine = 0.01 mg/L Total Chlorine = 1.91 mg/L 09:12 - collected weekly well #3 raw water micro. sample - W/O# W11657170 09:12 - collected weekly well #4 raw water micro. sample - W/O# W11657170 -put both wells back into local off -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060986 | 0 | 0
2026-03 | 2026-03-25 | Kleinburg Wells 3 and 4 | WEST | -on site to complete station check and collect samples -site offline and isolated from distribution system -sample work order # W11690439 09:38 - started well #3 in local running to waste at 25.6 l/s 09:38 - started well #4 in local running to waste at 26.6 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:45 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.90 mg/L 09:45 - Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 1.92 mg/L 10:16 - collected weekly well #3 raw water micro. sample 10:16 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | FLAG | stage2_low_confidence | 0.0089004 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action] | 0.0089004 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Elevated Tank | WEST | - on site to complete contingency entry | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-27 | Kleinburg Wells 3 and 4 | WEST | -on site to complete station check -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:41 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 2.10 mg/L 09:41 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.14 mg/L -no issues found | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029313 | 0 | 0
2026-03 | 2026-03-18 | Kleinburg Wells 3 and 4 | WEST | -on site to complete station check and collect samples -sample work order # W11672975 -site offline and isolated from distribution system 09:10 - started well #3 in local running to waste at 25.4 l/s 09:10 - started well #4 in local running to waste at 26.6 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:19 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.87 mg/L 09:19 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.83 mg/L 09:41 - collected weekly well #3 raw water micro. sample 09:41 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | FLAG | stage2_low_confidence | 0.0089004 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action] | 0.0089004 | 0 | 0
2026-03 | 2026-03-04 | Schomberg Elevated Tank | WEST | On site to collect weekly bact sample (W11637544). Verified online common inlet/outlet chlorine analyzer via hach field kit. Collected sample for in house lab analyses. Entered readings into PWQ sheet. Common chlorine grab residual @ 10:10 Free: 0.03 mg/L Total: 3.45 mg/L Mono: 2.91 mg/L Analyzer: 3.49 mg/L Checked analyzer reagents-ok. Station operation normal, no issues on site. | FLAG | stage2_low_confidence | 0.0093919 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093919 | 0 | 0
2026-03 | 2026-03-02 | Schomberg Elevated Tank | WEST | Onsite for station check Reviewed SCADA and trends Visual inspection of instrumentation and equipment Recorded station readings into pwq data sheet Common inlet/outlet -time 1436hrs Free grab 0.03 mg/l Total grab 3.48 mg/l analyzer 3.51 mg/l Post injection- time: 1441 hrs Free grab =0.05 mg/l Total grab =3.60 mg/l analyzer =3.56 mg/l | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0038582 | 0 | 0
2026-03 | 2026-03-11 | Schomberg Elevated Tank | WEST | Onsite to collect weekly bact sample (W11657095). Verified online common inlet/outlet chlorine analyzer via hach field kit. @12:18 Free grab: 0.05 mg/L Total: 3.62 mg/L Analyzer: 3.56 mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069592 | 0 | 0
2026-03 | 2026-03-10 | Schomberg Elevated Tank | WEST | -on site to complete following work order -generator run - topped up generator - switched to emergency power -JHSC inspection: all ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action] | emergency [critical]; work order [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-06 | Schomberg Elevated Tank | WEST | On-site for station check Reviewed scada and trends, duty active, ET @ 32% and filling @ 2 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1206 hrs Outlet Grabs: Analyzer reading TCL = 3.60 mg/l TCL = 3.61mg/l FCL = 0.05 mg/l FCL = mg/l Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 3% speed Dose scada: 3:4mL/min Hypo system pressure 600 kpa Activated duty for post chlorine injection grabs Chlorine Grab @ 1258 hrs Post Grabs: Analyzer reading TCL = 3.48 mg/l TCL = 3.48mg/l FCL = 0.04 mg/l FCL = mg/l Placed Hypo pump2 in manual off for the weekend due to fail to start issues Further troubleshoot required | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0031921 | 0 | 0
2026-03 | 2026-03-09 | Schomberg Elevated Tank | WEST | All trends checked and ok, all equipment checked and ok All measurements are in mg/l Common inlet outlet - 11:30 Total grab 3.45 vs analyzer 3.50 Free 0.04 Mono 2.99 Post injection - 11:40 Total grab 4.35 vs analyzer 4.36 Free 0.02 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0027666 | 0 | 0
2026-03 | 2026-03-24 | Schomberg Elevated Tank | WEST | On site to collect weekly bact sample (W11690364) from outlet sample tap. Common inlet/outlet Free: 0.02 mg/L grab Total: 3.22 mg/L grab vs analyzer 3.17 mg/l Post injection Total: 3.61 mg/l grab vs 3.67 mg/l analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052003 | 0 | 0
2026-03 | 2026-03-18 | Schomberg Elevated Tank | WEST | On site to collect weekly bact sample (W11672923) from outlet sample tap. Tested chlorine residuals via hach field kit. Free: 0.04 mg/L Total: 3.64 mg/L Changed common inlet/outlet analyzer reagents. Entered readings into PWQ sheet. | FLAG | stage2_low_confidence | 0.011547 | ML: above threshold (no LLM available) — 0.012 |  | 0.011547 | 0 | 0
2026-03 | 2026-03-19 | Schomberg Elevated Tank | WEST | SHETCS- Hypo Pump 1 failed to start, hypo pump 2 uncmd start. Called Jacob M. He is onsite working on them | FLAG | stage2_low_confidence | 0.011034 | ML: above threshold (no LLM available) — 0.011 | failed [equipment_failure] | 0.011034 | 0 | 0
2026-03 | 2026-03-27 | Schomberg Elevated Tank | WEST | At site for Station check All equipment looks good and trends checked. All measurements are in mg/l Common inlet 11:10 Total: 3.59 grab vs 3.50 analyzer Free: 0.07 grab Mono: 2.98 Post injection Total: 4.40 vs 4.28 analyzer Free: 0.09 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0019266 | 0 | 0
2026-03 | 2026-03-19 | Schomberg Elevated Tank | WEST | Onsite to complete work orders Completed hypo pump inspection Ran pumps to sight glass P1 135 ml/min P2 150 ml/min Placed hypo pump 2 in duty | FLAG | stage2_low_confidence | 0.0092155 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action] | 0.0092155 | 0 | 0
2026-03 | 2026-03-16 | Schomberg Elevated Tank | WEST | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -pre injection 08:50: 3.33mg/l grab: 3.34mg/l -free cl grab: 0.04mg/l -post injection 09:00: 3.66mg/l grab: 3.64mg/l -reagents all ok -equipment all ok | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048876 | 0 | 0
2026-03 | 2026-03-10 | Schomberg Elevated Tank | WEST | -on site to complete following work orders -manual valve exercise: all ok -drain valve exercise: all ok -heat trace inspection: all ok -chlorine analyzer maintenance- cleaned -took pre injection grab 11:00 -analyzer: 3.53mg/l grab: 3.50mg/l -took post injection 11:15 -analyzer: 3.50mg/l grab: 3.50mg/l -reagents all ok -low temp alarm test: -altitude valve inspection: all ok | FLAG | stage2_low_confidence | 0.010027 | ML: above threshold (no LLM available) — 0.01 | work order [maintenance_action]; alarm [control_system] | 0.010027 | 0 | 0
2026-03 | 2026-03-23 | Schomberg Elevated Tank | WEST | On site to inspect facility. Collected sample for in house lab analyses. Verified common inlet/outlet analyzer via hach field kit. Changed post injection analyzer reagents. Common inlet/outlet analyzer: 3.52 mg/L Grab total: 3.58 mg/L Grab free: 0.03 mg/L | FLAG | stage2_low_confidence | 0.012253 | ML: above threshold (no LLM available) — 0.012 |  | 0.012253 | 0 | 0
2026-03 | 2026-03-10 | Linear Water System | LINEAR | VNMCYS: Onsite to verify FIT installation Informed ROC Created CSE permit Verified mag flow meter installed correctly. Checked wiring. Potted. Installed clamp-on ultrasonic FIT and confirmed flow direction. At the time it was reverse flow and matched mag meter Closed CSE permit Informed ROC Left site | FLAG | stage2_low_confidence | 0.012415 | ML: above threshold (no LLM available) — 0.012 |  | 0.012415 | 0 | 0
2026-03 | 2026-03-02 | Linear Water System | LINEAR | T0530-07 Worked with North Rock to change AV in chamber T0530-07. It was completed and WM is back to normal. Total Cl2: 1.55mg/L Free Cl2: 0.02mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065929 | 0 | 0
2026-03 | 2026-03-04 | Linear Water System | LINEAR | Worked with North Rock to install a new 100 mm air valve in chamber 69-10. Grab chlorine residual test as follows Free- 0.05mg/l Total- 1.26mg/l All isolated valves are open and the system is back to normal operation. | FLAG | stage2_low_confidence | 0.013133 | ML: above threshold (no LLM available) — 0.013 |  | 0.013133 | 0 | 0
2026-03 | 2026-03-06 | Linear Water System | LINEAR | Worked with North Rock replaced two air valves in chamber T9632-01 reopened isolation valves and cl2 residual is total cl2 ; 1.75 mg/L and free cl2; 0.03 mg/L. | FLAG | stage2_low_confidence | 0.017409 | ML: above threshold (no LLM available) — 0.017 |  | 0.017409 | 0 | 0
2026-03 | 2026-03-17 | Linear Water System | LINEAR | Worked with North Rock to install a new AV in T0528-10. Grab chlorine residual test as follows Free- 0.02mg/l Total- 1.57mg/l All isolated valves are open and the system is back to normal operation. | FLAG | stage2_low_confidence | 0.011996 | ML: above threshold (no LLM available) — 0.012 |  | 0.011996 | 0 | 0
2026-03 | 2026-03-11 | Linear Water System | LINEAR | Worked with North Rock to install a new air valve in chamber T0530-03. Grab chlorine residual test as follows Free- 0.03mg/l Total- 1.68mg/l All isolated valves are open and the system is back to normal operation. | FLAG | stage2_low_confidence | 0.012868 | ML: above threshold (no LLM available) — 0.013 |  | 0.012868 | 0 | 0
2026-03 | 2026-03-03 | Linear Water System | LINEAR | Worked with North Rock to replace air valves in chamber T0528-06 for the air valve mods project. Grab chlorine test results as follows Free- 0.0.2mg/l Total- 1.24 mg/l All isolated valves are open and the system is back to normal operation. | FLAG | stage2_low_confidence | 0.012177 | ML: above threshold (no LLM available) — 0.012 |  | 0.012177 | 0 | 0
2026-03 | 2026-03-20 | Linear Water System | LINEAR | Worked with North Rock to install AV?s in 3 chambers for contract #2. Grab chlorine residual test as follows Chamber 2 Free- 0.04mg/l Total- 1.53mg/l ChamberLS12 Free- 0.05mg/l Total- 1.55mg/l Chamber LS10 Free- 0.05mg/l Total- 1.58mg/l All isolated valves are open and the system is back to normal operation. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055683 | 0 | 0
2026-03 | 2026-03-30 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, raked rag bin, bar screen oil topped up, cleaned rags off conveyors and floor. -Pump 4 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-31 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | on site in response to high incoming flow and 5 pumps running. Throttled down Newmarket SPS, turned off Greenlane | FLAG | stage2_low_confidence | 0.0092005 | ML: above threshold (no LLM available) — 0.009 |  | 0.0092005 | 0 | 0
2026-03 | 2026-03-31 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -Remotely monitoring site during period of high flows. Periodically partially diverting to EQ tanks. Throttling flows down at Newmarket SPS to help slow incoming flows and get NMMC Manhole 2 Level below HiHi Alarms set point. | FLAG | stage2_low_confidence | 0.013357 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.013357 | 0 | 0
2026-03 | 2026-03-06 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -pump floor inspection/cleaning -cleaned screen room/rotated bins as necessary -dump pad heat trace inspection -station okay | FLAG | stage2_low_confidence | 0.010409 | ML: above threshold (no LLM available) — 0.01 | scada [control_system] | 0.010409 | 0 | 0
2026-03 | 2026-03-03 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | LOTO Drain pump 1 piping Lift pump and put new gasket between piping and pump. Reinstall pump and flood Pump has leakage alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | flood [critical]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 0
2026-03 | 2026-03-05 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Check Harry Walker for wires for pump 4. None on site. Complete pump PM?s on pumps 1,2,3,5,&6. Added 50 grams of grease to lower bearings while pump running. Checked seal leakage chamber. Topped up coolant in cooling jackets as required, detailed in work orders. | FLAG | stage2_low_confidence | 0.030831 | ML: above threshold (no LLM available) — 0.031 | work order [maintenance_action]; leak [infrastructure]; leakage [infrastructure] | 0.030831 | 0 | 0
2026-03 | 2026-03-02 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to install pump one motorized valve programming did not match pump six faults indicated when testing will return tomorrow to troubleshoot | FLAG | stage2_low_confidence | 0.035287 | ML: above threshold (no LLM available) — 0.035 | fault [equipment_failure] | 0.035287 | 0 | 0
2026-03 | 2026-03-02 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -pump 1 and 4 are OOS, 4 pumps available -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-03 | 2026-03-09 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned screen room and rotated bins -station okay | FLAG | stage2_low_confidence | 0.010707 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010707 | 0 | 0
2026-03 | 2026-03-10 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -on site to clean up site before IAM tour tomorrow | FLAG | stage2_low_confidence | 0.013055 | ML: above threshold (no LLM available) — 0.013 |  | 0.013055 | 0 | 0
2026-03 | 2026-03-04 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -rotated bin in screen room -pumps 1 and 4 manual off, duty 7, maintenance working on them -on site for monthly work orders -Air Compressor Inspection -Air Dryer Inspection -JHSC Inspection -bins out for pickup, cleaned screen room -pump 1 back to auto duty 1, running with no issues -5 pumps available in auto, pump 4 OOS -backflushed line 2 at dump pad, cleared alarm, back to available -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] | sso [critical]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-11 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Adjusted pump duty 3,4, and 5 start/stop setpoint for early duty activation in response to high flow. Original set point: D3(4.90/5.70) D4(5.80/6.40) D5(6.60/7.10) Changed setpoint: D3(4.80/5.60) D4(5.70/6.30) D5(6.40/7.00) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050384 | 0 | 0
2026-03 | 2026-03-12 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to troubleshoot line 3 overtorque alarm. Back flushed the line to clear blockage and cleared the alarm Put line 3 back in service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; blockage [infrastructure] | alarm [control_system]; blockage [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -high flows at AUSS, 5 pumps active, wet well slowly coming down -put ISS East FM valve back to remote in case ISS pumps need to run -cleaned screen room, rotated bin as necessary -air compressor inspection -dump pad inspection/cleaning -EQ OCF inspection -station okay -giving a tour to IAM department around 14:00 today | FLAG | stage2_low_confidence | 0.013 | ML: above threshold (no LLM available) — 0.013 | sso [critical]; scada [control_system] | 0.013 | 0 | 0
2026-03 | 2026-03-09 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -left site to assist Kevin Shaji at Newmarket PS to unclog Pump 4 | FLAG | stage2_low_confidence | 0.017977 | ML: above threshold (no LLM available) — 0.018 | clog [infrastructure] | 0.017977 | 0 | 0
2026-03 | 2026-03-13 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -cleaned screen room and rotated bin -station okay | FLAG | stage2_low_confidence | 0.010654 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010654 | 0 | 0
2026-03 | 2026-03-03 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -on site for monthly work orders -Aurora SPS Consolidated Wetwell and Outfall Inspection -Monthly Surge Tank Inspection -Aurora EQ Tipping Bucket Test -outfall is okay, creek is well below duckbill -pump 1 was tested from the request of maintenance, leakage alarm came in, pump 1 is manual off, duty 7 -pump 4 is OOS -4 pumps available -Housekeeping of site, cleaned up garbage on all levels -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 1
2026-03 | 2026-03-25 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -at 09:00 met CPD and the contractors who are doing the gravity sewer clean out south of Bloomington, the contractors put their locks on the already locked out valves before they started their work -on site for station check -reviewed SCADA -inspected site -entered data into SharePoint -inspected air compressors -cleaned screen room, rotated bins as necessary -station okay -met contractor at 5:15 to get their locks off the LOTO valves | FLAG | stage2_low_confidence | 0.024307 | ML: above threshold (no LLM available) — 0.024 | sso [critical]; scada [control_system] | 0.024307 | 0 | 0
2026-03 | 2026-03-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Cut and replaced gasket on fuel primer pump for generator 3. Work on basement cleanup | FLAG | stage2_low_confidence | 0.0086315 | ML: above threshold (no LLM available) — 0.009 |  | 0.0086315 | 0 | 0
2026-03 | 2026-03-26 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -on site to pump out ISS actuated valve chamber, which has the two actuated valves for the two ISS pumps, the chamber has a leak in the roof from a crack which let's ground water in, a sump pump should be installed in this chamber to prevent future floods -AUSSSR line 2 overtorque, flushed line, reset alarms, line 2 back in service -put East Forcemain back online, removed LOTO of East FM discharge valve, ISS East discharge valve, East surge tank valves, all pump east forcemain valves back to remote/auto, East FM back to online in setpoints -station okay, contractors are on site still | FLAG | stage2_low_confidence | 0.20651 | ML: above threshold (no LLM available) — 0.207 | flood [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.20651 | 0 | 0
2026-03 | 2026-03-18 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On sit with Total Lift for inspections | FLAG | stage2_low_confidence | 0.013063 | ML: above threshold (no LLM available) — 0.013 |  | 0.013063 | 0 | 0
2026-03 | 2026-03-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to test run generator 3 after CMS fixed the defective fuel filter primer. Ran tested in manual without load, it was observed that the fuel filter primer that was installed is leaking a bit like one drop per second. Put generator 3 back in out of service and informed CMS (Terry C. and Bill VB.) | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; leak [infrastructure]; leaking [infrastructure] | out of service [equipment_failure]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-16 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -inspected overflow sampling kit -cleaned screen room, raked out bin -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; scada [control_system]; overflow [infrastructure] | overflow [critical]; scada [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-20 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -cleaned screen room, rotated bin as necessary -inspected generator 3, back to auto/available -station okay | FLAG | stage2_low_confidence | 0.0087457 | ML: above threshold (no LLM available) — 0.009 | scada [control_system] | 0.0087457 | 0 | 0
2026-03 | 2026-03-18 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Pick up and replace broken fuel primer pump for generator 3 | FLAG | stage2_low_confidence | 0.01108 | ML: above threshold (no LLM available) — 0.011 |  | 0.01108 | 0 | 0
2026-03 | 2026-03-30 | Newmarket Green Lane Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | FLAG | stage2_low_confidence | 0.010721 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010721 | 0 | 0
2026-03 | 2026-03-14 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to investigate alarms- Generator 1 Warning//Engine Battery Low Volts. Upon arrival noticed acid odours and fumes coming out of battery cells for generator 1. Requested ROC to connect to an electrician. As per the electrician request, battery charger is turned off and generator 1 is turned off. Electrician on the way to fix the issue with battery. Daniel Boate replaced the 2 old batteries with new ones. Run the generator to test the new batteries and no issues were found on startup. All generator 1 related alarms cleared on scada. | FLAG | stage2_low_confidence | 0.11701 | ML: above threshold (no LLM available) — 0.117 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.11701 | 0 | 0
2026-03 | 2026-03-18 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to complete work orders. -Alectra on site for hydro meter replacement. Discovered meter due for replacement was for solar power, so no disruption to station power is needed. -0855 - Transferred station to generator power. -Upon transfer to generator power, Generator 3 fuel filter primer cap blew out of the filter causing diesel fuel to spill onto ground. Immediately stopped Generator 3 and used absorbent pads to contain and clean up fuel spill. -0956 - Transferred site back to utility power. -Monthly diesel generator test run completed, readings entered into SharePoint. -Generator 1: Start: 629.3hrs, Stop: 630.4hrs, Run time: 1.1hrs. -Generator 2: Start: 621.5hrs, Stop: 622.6hrs, Run time: 1.1hrs. -Generator 3: Start: 825.3hrs, Stop 825.3hrs. -Generator 3 OOS until repairs can be made. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, changed out rag bin, bar screen oil topped up. -Bar screen rag bin removal completed, bins out for pick up. -Pump 4 OOS, Generator 3 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; sso [critical]; oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; absorbent pads [safety] | spill [critical]; sso [critical]; oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; absorbent pads [safety] |  | 1 | 1
2026-03 | 2026-03-27 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -received email/call at 09:44 from Daniel Kim regarding an odour complaint that came in north of AUSS -began investigating odour complaint thoroughly for 2-3 hours, completed Part A of Odour Complaint Form -all odour complaint findings can be found under Complaint ID#: 222 -facility is operating normally, chemical dosing systems to reduce H2S are operating normally, all rag bins are stored inside with doors sealed, no disruptions to pumping system | FLAG | stage2_low_confidence | 0.046434 | ML: above threshold (no LLM available) — 0.046 | scada [control_system]; h2s [safety] | 0.046434 | 0 | 0
2026-03 | 2026-03-23 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -rotated bin in screen room, cleaned screen room -reset pump 1 for discharge valve fault -pump 4 remains OOS, 5 pumps available -locked out and tagged out East Forcemain for gravity sewer cleaning south of Bloomington: all 6 pumps east discharge valves are in local stop, east surge tanks valve are closed and depowered, East forcemain common discharge valve is local closed, and depowered, ISS east discharge valve is local closed, in local stop -setpoints on SCADA show East is not in service, west forcemain is manually selected as in service -notified ROC and CEWW of East Forcemain OOS -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; scada [control_system] | fault [equipment_failure]; oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-03 | 2026-03-02 | Newmarket Green Lane Pumping Station | WW-CEAST | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. JHSC Health and Safety Inspection completed. | FLAG | stage2_low_confidence | 0.012805 | ML: above threshold (no LLM available) — 0.013 |  | 0.012805 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Green Lane Pumping Station | WW-CEAST | @ 8:30am - turned all pumps off in manual to throttle down flow going to Aurora SPS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054253 | 0 | 0
2026-03 | 2026-03-13 | Newmarket Green Lane Pumping Station | WW-CEAST | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. | FLAG | stage2_low_confidence | 0.012468 | ML: above threshold (no LLM available) — 0.012 |  | 0.012468 | 0 | 0
2026-03 | 2026-03-06 | Newmarket Green Lane Pumping Station | WW-CEAST | Station check complete and the readings have been entered into the sharepoint | FLAG | stage2_low_confidence | 0.015844 | ML: above threshold (no LLM available) — 0.016 |  | 0.015844 | 0 | 0
2026-03 | 2026-03-11 | Newmarket Green Lane Pumping Station | WW-CEAST | Put both pumps in local to prevent backup mode to start the pumps | FLAG | stage1_keyword | 0.95 | Critical keyword match: backup [infrastructure] | backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-18 | Newmarket Green Lane Pumping Station | WW-CEAST | Completed workorders. Wet well High level alarm test. Received and confirmed by ROC RS pump inspection. Pump #1- 40% = 175.8 L/s. Pump #2- 40% = 272.5 L/s. | FLAG | stage2_low_confidence | 0.0092813 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0092813 | 0 | 0
2026-03 | 2026-03-16 | Newmarket Green Lane Pumping Station | WW-CEAST | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. overflow kit inspection completed | FLAG | stage2_low_confidence | 0.029906 | ML: above threshold (no LLM available) — 0.03 | overflow [critical]; overflow [infrastructure] | 0.029906 | 0 | 0
2026-03 | 2026-03-11 | Newmarket Green Lane Pumping Station | WW-CEAST | Remotely put pumps OOS/Manual in response to high flow event. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-09 | Newmarket Green Lane Pumping Station | WW-CEAST | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. | FLAG | stage2_low_confidence | 0.012468 | ML: above threshold (no LLM available) — 0.012 |  | 0.012468 | 0 | 0
2026-03 | 2026-03-29 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site for lab analysis and sludge handling. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Batch wasted 8m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -Clarifier 1 OOS, WAS Pump 2 OOS, RAS Pump 3 OOS, UV Bank 1A OOS, OCU OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-30 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today is Partly Cloudy and 10 Celsius -On site to complete work order W11699719, W11698764, W116761554, W11699274, W11699499, W11699512. -Completed station check. -Entered station readings into SharePoint. -Completed Sludge Processing. -Bar Screen Bin, Removal and Replacement. -Post Aeration Alum mixing chamber and RAS/WAS inlet channel inspection/cleanout. -Added two bags of soda ash to each aeration tank. -Clarifier 1 still OOS and, presently filling with effluent water in preparation to put it back in service. -Alum delivery/Receiving started at 1.16 m filled to 3.79 m. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-30 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Batch wasted 5m3. Added 2 bags of soda ash into each aeration tank. | FLAG | stage2_low_confidence | 0.010433 | ML: above threshold (no LLM available) — 0.01 |  | 0.010433 | 0 | 0
2026-03 | 2026-03-31 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site to complete work order. Lab Analysis (See results on SharePoint) and Sludge Processing. STT decanted, afterwards, remaining sludge dumped into the SHT. Based on the SCADA trends there is no flow coming into the WRRF from the Mt Albert PS between 3:30am up to 9:35am, due to the power failure happened at the Mt Albert PS. Lagoon level at around 11:00am is at 102 inches. Added two bags of Soda Ash into each Aeration Tanks. Batch wasted 10m3 from clarifier 2. Clarifier 1 still out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; out of service [equipment_failure]; work order [maintenance_action]; scada [control_system] | failure [equipment_failure]; out of service [equipment_failure]; work order [maintenance_action]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-05 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -on site for lab analysis and sludge handling -reviewed SCADA -inspected site -entered data into sharepoint -started decanting sludge thickening tank -wasted sludge in thickening tank to sludge holding tank -added 4 bags of soda ash to aeration tanks -lab completed -sludge handling completed -wasted 10 m3 of sludge from clarifiers to thickening tank -station okay | FLAG | stage2_low_confidence | 0.0089255 | ML: above threshold (no LLM available) — 0.009 | scada [control_system] | 0.0089255 | 0 | 0
2026-03 | 2026-03-02 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Phil and I here to fix the hose on the de-cant pump. Brought the pump up and disconnected the hose and cut about a foot off the end and re-attached it back onto the de-cant pump. Lowered pump down and set the level up so its pumping clear liquid. Flow coming out of the pump is much better. Lots of hose left if we need to cut more off. | FLAG | stage2_low_confidence | 0.05286 | ML: above threshold (no LLM available) — 0.053 |  | 0.05286 | 0 | 0
2026-03 | 2026-03-11 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed Lab Analysis (See results on SharePoint) and Sludge Processing. STT decanted, afterwards remaining sludge dumped into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Clarifier 1 still draining into the lagoon. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Also, collected weekly sewage samples under YD #W11656931. | FLAG | stage2_low_confidence | 0.021603 | ML: above threshold (no LLM available) — 0.022 |  | 0.021603 | 0 | 0
2026-03 | 2026-03-07 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Here to continue the draining of Clarifier 1 - put RAZ pump 3 in manual on at 50% and also completed the Lab sheet for Sunday (small lab). I had to slow down the flow on RAZ pump 3 due to UV train 1 coming on/off quit frequently due to the higher flows. Entered the results from the Lab into Sharepoint and put the station back to normal ops at the end of the day. Ammonia was a little Hi but the rest of the Lab was OK. | FLAG | stage2_low_confidence | 0.060325 | ML: above threshold (no LLM available) — 0.06 |  | 0.060325 | 0 | 0
2026-03 | 2026-03-12 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint). STT decanted, afterwards remaining sludge dumped into the SHT. STT hosed down after decanting. Added two bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Consolidated Headworks Building Inspection Grit Vortex Travelling Screen Dewatering Press Screening Press | FLAG | stage2_low_confidence | 0.025809 | ML: above threshold (no LLM available) — 0.026 | work order [maintenance_action] | 0.025809 | 0 | 0
2026-03 | 2026-03-12 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Partly cloudy and -1 Celsius. -On site to complete work order W11661150, W11660965, W11660939. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. - Post Filtration/UV channel hose down. -RAS/WAS inlet channel inspection/cleanout. -Wasted 4m3 from clarifier #1. | FLAG | stage2_low_confidence | 0.021905 | ML: above threshold (no LLM available) — 0.022 | work order [maintenance_action] | 0.021905 | 0 | 0
2026-03 | 2026-03-05 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Verified alum dosing and sand filter operation. -Cleaned out grease and solids from Clarifier 1 inner ring. -Traveling screen and OCU remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-10 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Partly Cloudy and 9 Celsius -On site to complete work order W11651437, W11651087, W11651073, W11651059, W11650205. -Completed station check. -Entered station readings into SharePoint. - RAS Pumps 1,2, and 3 Inspection. - WAS Pumps 1and 2 Inspection. - Scum Pumps 1and 2 Inspection. - Sump Pumps Maintenance. | FLAG | stage2_low_confidence | 0.018414 | ML: above threshold (no LLM available) — 0.018 | work order [maintenance_action] | 0.018414 | 0 | 0
2026-03 | 2026-03-10 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Removed south clarifier, gearbox and motor | FLAG | stage2_low_confidence | 0.013452 | ML: above threshold (no LLM available) — 0.013 |  | 0.013452 | 0 | 0
2026-03 | 2026-03-02 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing STT decanted after decant pump hose fixed by Philip R. and Terry R. Dumped remaining sludge into SHT. Station Check (See details on SharePoint). Added two bags of Soda Ash into each Aeration Tanks. Checked Headworks, raked rags from the manual bar screen. Checked DO Probes, removed rags dangling from the probes. Checked Alum dosing injection points at prefilter and post aeration. Batch wasted 10m3. Ran RAS Pumps 1 and 3 to 100% to get desired flows of around 13 L/s. Post Aeration Alum Mixing Chamber Cleaned Out Removed rags from the inlet/outlet sluice gates of Aeration Tanks. | FLAG | stage2_low_confidence | 0.043848 | ML: above threshold (no LLM available) — 0.044 | work order [maintenance_action] | 0.043848 | 0 | 0
2026-03 | 2026-03-01 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site for sludge handling and lab analysis. -Added two bags of soda ash to each aeration tank. -Unable to decant STT. Hose has multiple holes right above connection to decant pump and is producing no flow. Emptied approximately 2m out of STT to make room for auto wasting tonight. -Raked manual bar screen. -Completed lab analysis and entered results into SharePoint. -Ran RAS pumps at 100% speed for several minutes. -Verified sand filter operation and alum dosing. -Cleaned solids off top of post aeration alum chamber. -Verified clarifier heater are both still running. -OCU and traveling screen remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Added two bags each of Soda Ash into each Aeration Tanks Removed rags from the sluice gates of Aeration Tanks Post Filtration/UV channel hose down. Clarifier #1 taken OOS due to gearbox issue. Emptying clarifier #1 now. Bar screen put back to service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-04 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing Decanting STT started. Station Check (See details on SharePoint) Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration, ok. Also, collected weekly and monthly sewage samples under YD #s W11637306, W11637092, W11637362 and W11637028. Out around 11:00am, to collect sewage samples at Mt Albert PS. Back at 12:30pm, to continue completing work orders. Decanting STT done, afterwards remaining sludge dumped into the SHT. Batch wasted 10 m3. Ran RAS Pumps 1 and 3 at 100% speed to get desired flows of around 13 L/s at 0% auto speed setpoint. They are running at 12% auto speed before that with around 13 L/s flows. Added two bags of Soda Ash into each Aeration Tanks, one in the morning and one in the afternoon. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Raked rags from the manual bar screen. As per Bill VB (CMS TL), mechanical bar screen gear box is defective, need new one. | FLAG | stage2_low_confidence | 0.12844 | ML: above threshold (no LLM available) — 0.128 | work order [maintenance_action] | 0.12844 | 0 | 0
2026-03 | 2026-03-15 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed in-house lab Analysis (See details on SharePoint) Station Check (See details on SharePoint). Decanting STT into the Headworks. Transferred the sludge and processing. Added two bags each of Soda Ash into each Aeration Tanks | FLAG | stage2_low_confidence | 0.015888 | ML: above threshold (no LLM available) — 0.016 |  | 0.015888 | 0 | 0
2026-03 | 2026-03-03 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to complete work orders. -Added two bags of soda ash to each aeration tank. -Raked manual bar screen. -Cleaned out RAS inlet chamber and post aeration alum chamber. Cleaned rags off aeration tank inlet gates and DO probes. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Monthly diesel generator test run completed, readings entered into SharePoint. -1013 - Transferred station to generator power. -1122 - Station transferred back to utility power. -Generator start hours: 492.3, stop hours: 493.5, run time: 1.2hrs. -Switched grit bins following pick up. -Clarifier scum system cleaning completed. Cleaned out clarifier scum troughs, hosed down walls of scum tank and ran Scum Pump 1 in local to pump out tank following cleaning. -Traveling screen and OCU remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-03 | 2026-03-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Installed barscreen drive motor Electricians wired motor Tested okay. | FLAG | stage2_low_confidence | 0.01055 | ML: above threshold (no LLM available) — 0.011 |  | 0.01055 | 0 | 0
2026-03 | 2026-03-08 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put two bags of soda ash into the aeration tanks and set two up for later,, started the de-cant pump as well as RAZ pump 3 to continue emptying clarifier 1. Completed the Lab work and entered results into Sharepoint. Ammonia still Hi but the rest of the Lab looks fine. added the other two bags of soda ash and put the station back to normal operation. Clarifier 1 is about 3/4 empty now. | FLAG | stage2_low_confidence | 0.051167 | ML: above threshold (no LLM available) — 0.051 |  | 0.051167 | 0 | 0
2026-03 | 2026-03-11 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Heavy rian and 3 Celsius -On site to complete work order W11655956, W11651680, W11627876. -Completed station check. -Entered station readings into SharePoint. -JHSC Health and safety inspection. -Alum chemical system flush. | FLAG | stage2_low_confidence | 0.017863 | ML: above threshold (no LLM available) — 0.018 | work order [maintenance_action] | 0.017863 | 0 | 0
2026-03 | 2026-03-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Check south clarifier and found drive motor gear assembly needs replacement. Requested quote for new assembly. | FLAG | stage2_low_confidence | 0.015353 | ML: above threshold (no LLM available) — 0.015 |  | 0.015353 | 0 | 0
2026-03 | 2026-03-01 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to respond to Clarifier 2 Fault Alarm, reported by ROC. -Found Clarifier 2 with a Torque Alarm on MCC. -Manually backed up clarifier 2 arm, cleared faults, and ran in auto. Repeated this several times, each time Clarifier 2 would run a little bit longer before the Torque Alarm came back in. Inspected clarifier gearbox and found that heater was running, but gearbox was full of chunks of a frozen water/oil mixture. Drained as much water as possible from gearbox and added in new oil. Turned up temperature on heater slightly and used propane torch to help thaw out gearbox. Torque reading on Clarifier 2 has dropped from approximately 45 to 25 and is continuing to slowly decrease. Left heater running, but repositioned against opposite wall. -Clarifier 2 is back in auto and running. | FLAG | stage2_low_confidence | 0.29243 | ML: above threshold (no LLM available) — 0.292 | fault [equipment_failure]; alarm [control_system] | 0.29243 | 0 | 0
2026-03 | 2026-03-09 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed Station Check (See details on SharePoint). STT decanted, afterwards dumped remaining sludge into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Checked Headworks, ok. Checked DO Probes, removed rags dangling from the probes. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Also, at around 10:30am, 4Refuel delivered diesel fuel, 800.4 L. Tanks previous level: 58.6cm/471L and 56.9cm/455L Tanks level after delivery: 102.0cm/859L and 100.9cm/849L. | FLAG | stage2_low_confidence | 0.022343 | ML: above threshold (no LLM available) — 0.022 |  | 0.022343 | 0 | 0
2026-03 | 2026-03-10 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Batch wasted 5m3 from clarifier #2. filter reject drain line flush completed. Added 2 bags of soda ash into each aeration tank. Created WO# W11722223 to fix water scour line leak for grit vortex 1. | FLAG | stage2_low_confidence | 0.021886 | ML: above threshold (no LLM available) — 0.022 | leak [infrastructure] | 0.021886 | 0 | 0
2026-03 | 2026-03-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | put two bags of soda ash into the aeration tanks and set two up for later. Started grabbing samples for the Lab and Daniel had switched WO to Kevin,, went through the station and sand filters working great and started de-cant pump. Clarifier 1 arm stopped turning, got a hold of Bill (maintenance) and he's on his way. Cleaned out the post aeration tank as well as the inlet gates while waiting. There was no Hazardous waste to dispose of and went through the weekly alarm management for EOC and YDOC and there were no changes to either site. Started emptying clarifier #1 due to gear box in motor is broken - Daniel showed up and walked us through switching everything over. Continued draining for two hours and i'll be in on the weekend to complete. Bill and Terry - maintenance got the bar screen working again so we closed off the by-pass and now flow is going through the bar screen. Clarifier 1 is down but the rest of the station is running fine. | FLAG | stage2_low_confidence | 0.57583 | ML: above threshold (no LLM available) — 0.576 | alarm [control_system]; hazard [safety] | 0.57583 | 0 | 1
2026-03 | 2026-03-03 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing STT decanted, afterwards remaining sludge dumped into the SHT. Ran RAS Pumps 1 and 3 at 100% speed to get desired flows of around 13 L/s at 0% auto speed setpoint. They are running at 17% auto speed before that with around 14 L/s flows. Sand Filter Filter-Reject Drain Line Flushed Dissolved Oxygen Meter Verification Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration, ok. | FLAG | stage2_low_confidence | 0.066072 | ML: above threshold (no LLM available) — 0.066 | sso [critical]; work order [maintenance_action] | 0.066072 | 0 | 0
2026-03 | 2026-03-13 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint). STT decanted, afterwards remaining sludge dumped into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Weekly alarm management - only clarifier 1 no RAS pump running is the alarm due to clarifier 1 out of service. Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system] | out of service [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-13 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Overcast and -2 Celsius. -On site to complete work order W11663911, W11660952, W11651121. W11730157. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. - Air Compressors 1-2, Cleaning & Inspection. - Post Aeration Alum mixing chamber cleanout. -Wasted 3m3 from clarifier #1. - Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | FLAG | stage2_low_confidence | 0.054791 | ML: above threshold (no LLM available) — 0.055 | sso [critical]; work order [maintenance_action]; repair [maintenance_action] | 0.054791 | 0 | 0
2026-03 | 2026-03-24 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site for leak at vortex solenoid outlet piping. Operators drained vortex. Backed off piping, cleaned threads, and applied new thread tape. Reinstalled piping and tightened union. Had operations run water scour to open solenoid. No leaks detected. Removed isolation gates to allow flow back to vortex. Rechecked for leaks okay. Complete. | FLAG | stage2_low_confidence | 0.017445 | ML: above threshold (no LLM available) — 0.017 | leak [infrastructure] | 0.017445 | 0 | 0
2026-03 | 2026-03-21 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site for Station Check, Lab Analysis and Sludge Processing. Completed lab analysis (See results on SharePoint) Decanted STT. Dumped remaining sludge into the SHT. Added 2 bags of Soda Ash into each Aeration Tanks. Checked DO Probes. Removed rags dangling on the probes. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration, ok. | FLAG | stage2_low_confidence | 0.018159 | ML: above threshold (no LLM available) — 0.018 |  | 0.018159 | 0 | 0
2026-03 | 2026-03-17 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Mostly cloudy and -10 Celsius. -On site to complete work order W11669544, W11669735, W11740565, W11664220. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. - Sand Filter Filter-Reject Drain Line Flush. -Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. - Training, IMS Emergency Procedure Quiz | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action]; repair [maintenance_action] | emergency [critical]; work order [maintenance_action]; repair [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-19 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site with Total Lift for annual inspections | FLAG | stage2_low_confidence | 0.012727 | ML: above threshold (no LLM available) — 0.013 |  | 0.012727 | 0 | 0
2026-03 | 2026-03-23 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Went through alarm management for the WRRF this morning,, all alarms that are shelved are still currently OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-02-27 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put two bags of soda ash into the aeration tank and set two up for later,, started the de-cant pump as well. Cleaned the washroom in the sand filter room (this time the appliances-not the floor) and then took the traveling bar screen apart so maintenance could have a look. Cleaned out the back and a big wad on the top before the brush, washed the inside down with the hose to get it as cleaned out as possible. Pulled the de-cant pump up after emptying the thickening tank and cleaned out the bottom of the pump. Went through the station - sand filters and clarifiers all working well. Went through the alarm management the only problem we have here is the Odour Control and it is shelved and still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to respond to Alum Pump Containment Flood Alarm, reported by ROC. -Upon arrival to site, found alum pump containment area filled with water, likely from previous effluent line break. Inspected alum pumps and chemical lines, as well as nearby water line and found no sign of a leak. Alum trends also appear normal. Pumped out water from containment area, but am unable to reset Alum Pump Containment Flood Alarm on SCADA. Containment area is currently dry with no signs of a leak. Will have to investigate flood alarm float issue further tomorrow. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system]; leak [infrastructure]; containment [safety] | flood [critical]; scada [control_system]; alarm [control_system]; leak [infrastructure]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-20 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. STT decanted. Dumped remaining sludge into the SHT afterwards. Orlando B. (Sludge hauler) called, he cannot make it today due to weather related issue, he is behind with other facilities. Completed Lab Analysis (See results on SharePoint) Station Check (See details on SharePoint) Added two bags of Soda Ash into each Aeration Tanks. Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration, ok. Removed rags from the inlet/outlet sluice gates of aeration tanks. Batch wasted 10m3 from Clarifier 2. At 2:00pm, Alum dosage increased from 15 mg/L to 20 mg/L at the prefilter. Found effluent pumps in off position at the panel. Put back in auto. | FLAG | stage2_low_confidence | 0.049857 | ML: above threshold (no LLM available) — 0.05 | work order [maintenance_action] | 0.049857 | 0 | 0
2026-03 | 2026-03-19 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put in 2 bags of soda ash and set 2 up for later,, Kevin started de-cant pump and then I worked with Kevin on his Lab work to speed it up and get a lot more organized. Went through the station, UV bank 1 is OOS - sand filters working great. Checked the hoist in the aeration room and the sand filter room - all good. Cleaned out the post aeration tank and the inlet channel gates, Washed down the UV channel and shut down the effluent pumps for the night to make sure we have no breaks again. Hopefully this helped Kevin out with his Lab work, UV 1 is OOS along with clarifier 1 the rest of the station is running fine. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-22 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site for the Weekend Sludge Handling/Processing. STT decanted. Dumped remaining sludge into the SHT afterwards. Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration. Added two bags of Soda Ash into each Aeration Tanks. Checked Headworks. Cleaned/hosed down screen room. At 9:57am, Dewatering Screw, Grit System 1 and 2 Faulted. Cleared/reset alarms at the panel. All back in auto and in service. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Batch wasted 10 m3 on Clarifier 2. Clarifier 1 still out of service due to gear box issue. Also, completed Lab Analysis (See results on SharePoint). | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Overcast and 0 Celsius. -On site to complete work order W11682416, W11682185, W11681950, W11681937, W11681610, W11681098. -Completed station check and lab analysis. -Entered station readings and lab analysis into SharePoint. -Completed Sludge Processing. -Bar Screen Bin, Removal and Replacement. -Post Aeration Alum mixing chamber and RAS/WAS inlet channel inspection/cleanout. -Added two bags of soda ash to each aeration tank. | FLAG | stage2_low_confidence | 0.033339 | ML: above threshold (no LLM available) — 0.033 | work order [maintenance_action] | 0.033339 | 0 | 0
2026-03 | 2026-03-17 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put 2 bags of soda ash in and set 2 up for later,, started de-cant pump. Went through the blowers , had to top up 3. Checked the Lagoon from on top of the clarifier cat walk - all looks good, no breaks | FLAG | stage2_low_confidence | 0.021844 | ML: above threshold (no LLM available) — 0.022 |  | 0.021844 | 0 | 0
2026-03 | 2026-03-17 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Replace battery in tow motor and verified unit is charging. | FLAG | stage2_low_confidence | 0.014472 | ML: above threshold (no LLM available) — 0.014 |  | 0.014472 | 0 | 0
2026-03 | 2026-03-16 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Mostly cloudy and 11 Celsius. -On site to complete work order W11667140, W11667069, W11666578. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. -Bar Screen Bin, Removal and Replacement. | FLAG | stage2_low_confidence | 0.022523 | ML: above threshold (no LLM available) — 0.023 | work order [maintenance_action] | 0.022523 | 0 | 0
2026-03 | 2026-03-23 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put 4 bags of soda ash in and started de-cant pump,, Daniel and I isolated the inlet at the headworks and are diverting flow to the lagoon (@ approx. 08:25 ) Put 3 knife gates in place to re-direct flow to the lagoon. Accuworxs here and are pumping down post aeration tank, Retrieved the grating at approx. 14:00 hrs and then put the station back to normal ops by removing gates from the headworks. Station back to normal ops - clarifier 1 and UV bank 1A are still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-19 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed in-house lab Analysis (See details on SharePoint) Station Check (See details on SharePoint). Decanting STT into the Headworks. Transferred the sludge and processing.. Added two bags each of Soda Ash into each Aeration Tanks Post Filtration/UV channel hose down. | FLAG | stage2_low_confidence | 0.015916 | ML: above threshold (no LLM available) — 0.016 |  | 0.015916 | 0 | 0
2026-03 | 2026-03-23 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site with GFL for adhoc post aeration tank clean out to retrieve the grating that fell in last week. Started diverting to lagoon @ 8:25 am, pumping station flow totalizer @ 382m3. Dropped in 2 slide gates to isolate inlet chamber. Slide gate not perfectly water tight, about 10% going pass the gate. @14:00, Accuworx was able to drawdown the chamber to near bottom. Ops performed CSE to get the grating out. @14:15, all gates inserted in the headworks has been removed, valve to clarifier 2 has been re-opened. Both RAS put back in service | FLAG | stage2_low_confidence | 0.027495 | ML: above threshold (no LLM available) — 0.027 |  | 0.027495 | 0 | 0
2026-03 | 2026-03-16 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site to complete work orders. Station Check (See details on SharePoint) At around 09:50am, Barry and I found the effluent water pipe leaking at the union connection in the process building (Filter Room) near the entrance door. Put effluent pumps in manual/off. Sump pump in the basement was able to keep up with the leak. Work request created for CMS. Also, UV bank 1B has a major fault status. tried to run in manual but there is no lights on the nodules. Alarm can be cleared/reset but it keeps on coming back. Work request created for CMS. Added two bags of Soda Ash into each Aeration Tanks. Post aeration alum mixing chamber clean out. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration. Decanted STT. Dumped remaining sludge into the SHT afterwards. | FLAG | stage2_low_confidence | 0.36637 | ML: above threshold (no LLM available) — 0.366 | fault [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] | 0.36637 | 0 | 0
2026-03 | 2026-03-24 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site to complete work orders. Vortex Grit System 1 isolated and water pumped out in preparation for the repair of leaking water scour line. Vortex Grit System 1 back in service after repair (See Terry C.) eLogbook entry above. Flushed Sand Filter-Filter Reject Drain Line Partially did housekeeping. | FLAG | stage2_low_confidence | 0.044172 | ML: above threshold (no LLM available) — 0.044 | work order [maintenance_action]; repair [maintenance_action]; leak [infrastructure]; leaking [infrastructure] | 0.044172 | 0 | 0
2026-03 | 2026-03-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Partly cloudy and 8 Celsius. -On site to complete work order W11682416, W11692183, W11692096, W11756498. -Completed lab analysis. -Entered lab analysis readings into SharePoint. -Completed Sludge Processing. -Post Filtration/UV channel hose down. - Admin area cleaning. -Added two bags of soda ash to each aeration tank. -Clarifier 1 and UV bank 1A are still OOS. -Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] | oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-24 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Check on generator rpm and voltage fluctuations Ran generator without load for approximately 30 minutes RPM stayed at 1805-1806 Voltage stayed at 599-601 V Recommend inspecting during next full transfer. No issues at this time. | FLAG | stage2_low_confidence | 0.0080707 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080707 | 0 | 0
2026-03 | 2026-03-18 | Mount Albert Water Resource Recovery Facility | WW-CEAST | arrived on site to respond to UV bank 1A major fault alarm. Upon arrival found the UV system running normally but there was an unhealthy lamp status on the lead UV bank 1A. Acknowledged and cleared the alarms on the UV screen. Cleared all alarms on SCADA. | FLAG | stage2_low_confidence | 0.053481 | ML: above threshold (no LLM available) — 0.053 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.053481 | 0 | 0
2026-03 | 2026-03-24 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Clear and -3 Celsius. -On site to complete work order W11682416, W11684111, W11682556, W11685349, W11753100. -Completed station check and lab analysis. -Entered station readings and lab analysis into SharePoint. -Completed Sludge Processing. - H&S Vehicle Inspection, Vehicle 2057. - Pick-up Fall Arrest Equipment. -Added two bags of soda ash to each aeration tank. | FLAG | stage2_low_confidence | 0.020466 | ML: above threshold (no LLM available) — 0.02 | work order [maintenance_action] | 0.020466 | 0 | 0
2026-03 | 2026-03-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Installed clarifier drive motor and gearbox Electricians wired up on site after installation of new terminal block in motor. Advised operator to put a blue lock on the local shut off and test operation to verify correct rotation once clarifier is finished being cleaned. | FLAG | stage2_low_confidence | 0.025144 | ML: above threshold (no LLM available) — 0.025 |  | 0.025144 | 0 | 0
2026-03 | 2026-03-18 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Responded to UV fail alarm found UV bank A and bank B were full of water. There was water infiltration in the UV control panel as well. Cleaned and dried out. All panels was able to get enough components between UVA and UVB to get UVB working. New parts are on order exhaust fan 206 has failed as well. Reported to the team lead to have a work order created. Device locked out. | FLAG | stage2_low_confidence | 0.12483 | ML: above threshold (no LLM available) — 0.125 | failed [equipment_failure]; work order [maintenance_action]; work order created [maintenance_action]; alarm [control_system] | 0.12483 | 0 | 0
2026-03 | 2026-03-25 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Partly cloudy and -3 Celsius. -On site to complete work order W11682416, W11690597, W11690200, W11689416. -Completed station check and lab analysis. -Entered station readings and lab analysis into SharePoint. -Completed Sludge Processing. - Sewage Sampling. -Added two bags of soda ash to each aeration tank. | FLAG | stage2_low_confidence | 0.022386 | ML: above threshold (no LLM available) — 0.022 | work order [maintenance_action] | 0.022386 | 0 | 0
2026-03 | 2026-03-31 | Mount Albert Pumping Station | WW-CEAST | -on site to assist Phil Romito with sampling | FLAG | stage2_low_confidence | 0.012647 | ML: above threshold (no LLM available) — 0.013 |  | 0.012647 | 0 | 0
2026-03 | 2026-02-27 | Mount Albert Pumping Station | WW-CEAST | Took station readings and entered into Sharepoint,, reviewed trends - all good. Station running under normal ops - no issues were found. | FLAG | stage2_low_confidence | 0.020643 | ML: above threshold (no LLM available) — 0.021 |  | 0.020643 | 0 | 0
2026-03 | 2026-03-13 | Mount Albert Pumping Station | WW-CEAST | On site for Station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Station operations normal. | FLAG | stage2_low_confidence | 0.012544 | ML: above threshold (no LLM available) — 0.013 |  | 0.012544 | 0 | 0
2026-03 | 2026-03-11 | Mount Albert Pumping Station | WW-CEAST | Weather today Overcast and 2 Celsius -On site to complete work order W11656931. -Collected monthly and weekly sewage samples and then, delivered to 145 HWP. -Rinsed samples container. -Reset composite sampler for next week sewage samples collection. | FLAG | stage2_low_confidence | 0.022597 | ML: above threshold (no LLM available) — 0.023 | work order [maintenance_action] | 0.022597 | 0 | 0
2026-03 | 2026-03-02 | Mount Albert Pumping Station | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. JHSC Health and Safety Inspection Hazardous Waste Collection and Removal | FLAG | stage2_low_confidence | 0.032478 | ML: above threshold (no LLM available) — 0.032 | work order [maintenance_action]; hazard [safety] | 0.032478 | 0 | 0
2026-03 | 2026-03-05 | Mount Albert Pumping Station | WW-CEAST | -On site for semi annual diesel generator maintenance, including monthly test run. -Total Power on site for semi annual maintenance. -0859 - Transferred station to generator power. -1005 - Transferred station back to utility power. -Generator Start hours: 619.5, Stop hours: 620.7, run time: 1.2hrs. -Generator test run completed, readings entered into SharePoint. | FLAG | stage2_low_confidence | 0.01455 | ML: above threshold (no LLM available) — 0.015 |  | 0.01455 | 0 | 0
2026-03 | 2026-03-20 | Mount Albert Pumping Station | WW-CEAST | On site completed Station Check (See details on SharePoint) Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Station operations normal. | FLAG | stage2_low_confidence | 0.012878 | ML: above threshold (no LLM available) — 0.013 |  | 0.012878 | 0 | 0
2026-03 | 2026-03-16 | Mount Albert Pumping Station | WW-CEAST | On site completed work orders. Upon arrival found SCADA with generator not in auto alarm happened last Friday, March 13th, 2026, at 11:33am. Cleared/reset said alarm and check generator, ok. Station Check (See details on SharePoint) Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Station operations normal. Overflow Kit Inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; overflow [infrastructure] | overflow [critical]; work order [maintenance_action]; scada [control_system]; alarm [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today Partly cloudy and 11 Celsius. -On site to complete work order W11648657, W11648577, W11707125, W11648041, W11648341, W11648328, W11714174. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. -Bar Screen Bin, Removal and Replacement. -Post Aeration Alum mixing chamber and RAS/WAS inlet channel inspection/cleanout. -Wasted 25m3 from clarifier #1. -Alum Delivery/Receiving stated at 0.89m and filled to 3.52m. | FLAG | stage2_low_confidence | 0.037022 | ML: above threshold (no LLM available) — 0.037 | work order [maintenance_action] | 0.037022 | 0 | 0
2026-03 | 2026-03-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to complete work orders. -GFL/Accuworx on site for Clarifier 1 cleaning. -Two bags of soda ash added to each aeration tank. -Cleaned out RAS inlet chamber and post aeration alum mixing chamber. -Mechanics and electricians have completed repair work on Clarifier 1. Clarifier 1 locked out at local disconnect with station lock until clarifier cleaning is completed. -Worked on UV room cleaning. Removed old/broken items. Cleaned floors. -UV Bank 1A OOS, Clarifier 1 OOS, RAS Pump 3 OOS, WAS Pump 2 OOS, OCU OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] | oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] |  | 1 | 1
2026-03 | 2026-03-18 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site to complete work orders. STT decanted and sludge dumped into the SHT afterwards. As per notification of work order completion received today, effluent pipe leak has been fixed by CMS. Effluent pumps put back in auto and back in service. Lab Analysis (See results on SharePoint) and Sludge Processing. At around 9:45am, turned off both UV banks and flows diverted to the lagoon due to damaged wirings on the UV banks systems and the Trojan panel. Electricians on site troubleshooting it. Station Check (See details on SharePoint). Added two bags of Soda Ash into each Aeration Tanks. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration. Also, collected weekly sewage samples under YD# W11672811. Terry R. delivered to 145 HWP. At around 11:26am, Post Aeration Alum dosage increased from 195 mg/L to 200 mg/L. Prefilter remains the same at 15 mg/L. At around 12:15pm, UV Bank 1B has been fixed by electricians and put back in service. Cleared/reset alarms. At 13:00pm, flows diverted back to the plant. Approximate volume of flows diverted is 220 m3. | FLAG | stage2_low_confidence | 0.40787 | ML: above threshold (no LLM available) — 0.408 | work order [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.40787 | 0 | 0
2026-03 | 2026-03-27 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Weather today a few clouds and -8 Celsius. -On site to complete work order W11682416, W11696996, W11696424, W11697180. -Completed station check and lab analysis. -Entered station readings and lab analysis into SharePoint. -Completed Sludge Processing. -Weekly Alarm Management. -Added two bags of soda ash to each aeration tank. -Clarifier 1 and UV bank 1A are still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | Mount Albert Pumping Station | WW-CEAST | Weather today is Partly Cloudy and 10 Celsius -On site to complete work order W11698440. -Completed station check. -Entered station readings into SharePoint. -Both pumps are available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well. -Station operations normal. | FLAG | stage2_low_confidence | 0.017021 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action] | 0.017021 | 0 | 0
2026-03 | 2026-03-31 | Mount Albert Pumping Station | WW-CEAST | -On site to respond to communications failure alarm reported by ROC. PCS on-call has also been notified and is on route to site. -0405 - Upon arrival to site, swipe card reader not working, local SCADA OIT panel is blank and not working, Pumps both displaying No Communication faults on panels. Wet well level is at 4.08m. Tried resetting pump faults on local panel, but pumps will not run in remote or local. Wet well backup mode is in Auto, but pumps not running. -Called on-call electrician, tried cycling power to pumps, but still not working. Tried disconnecting power for 5-10min, but pumps still not working when turned back on. On-call electrician on route to site. -0431 - Contacted ROC to initiate emergency vac truck procedure and have trucks dispatched to site. -Tried transferring site to generator power, suspecting possible phase loss on site. Unable to get generator to turn on, e-key not working on any locks on site. -Briefly left site to bump e-key at MTA WRRF. When back on site, e-key still not working. Cut lock to generator building. Generator screen is blank and unresponsive. Generator will not run in remote or manual. -0512 - Wessuc confirmed they have vac truck and tanker on route to site. -Electricians and PCS arrived at site and found multiple damaged pieces of equipment due to a suspected lightning strike on the building. They immediately began work to restore functionality of damaged equipment. -0631 - Wessuc informed of delays and that they were still approximately 1.5hrs away. -0645 - Informed SAC of ongoing spill. Spoke with environmental officer Edhilvia Campos and was assigned event# 1QG1QRG. -0655 - Informed York Region local health unit of ongoing spill. Spoke with health officer David Huang. -0700 - Notified LSCRA of ongoing spill. -0815 - Wessuc arrived on site and began setting up hoses to pump down wet well. Began pumping down wet well at approximately 0830. -0830 - Collected spill samples with Chris Rodie, CoC# W11769441. -0925 - Electricians able to get one pump running on site and began pumping down wet well to forcemain along with Wessuc pumping wet well to vac truck. -0957 - Wet well at 3.99m, below the overflow level. Spill has ended. -Kevin Shaji arrived at site to complete weekly sample collection. -When Wessuc had completed their emergency wet well pumping activities, accompanied vac truck to site of spill, which was a local East Gwillimbury manhole between the southeast corner of the Foodland parking lot and the railroad tracks. Wessuc cleaned solids and liquid from surrounding area, as well as removed excess solids from local sewer. While on site, visited by local Public Heath Inspector Darja Montsenko, who also observed spill location during cleanup and afterwards. -Instrumentation team on site to replace damaged flowmeter and level sensor. -Electricians and PCS team able to get both station pumps repaired and operational in auto. -Temporary generator set up on site and tested in manual and in auto, with a full station transfer test. -Composite sampler reset for 0700 April 7, 2026. Sample jug cleaned. -Security system and swipe card reader on site not working. Informed supervisor of issue and work request created. -Station is back running normally. Temporary generator set up on site. Both pumps available and in local. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; spill [critical]; emergency [critical]; lightning strike [critical]; fault [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; not working [equipment_failure]; repair [maintenance_action]; environmental officer [regulatory]; health unit [regulatory]; spill sample [regulatory]; scada [control_system]; alarm [control_system]; no communication [control_system]; overflow [infrastructure]; backup [infrastructure]; pump fault [infrastructure] | overflow [critical]; spill [critical]; emergency [critical]; lightning strike [critical]; fault [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; not working [equipment_failure]; repair [maintenance_action]; environmental officer [regulatory]; health unit [regulatory]; spill sample [regulatory]; scada [control_system]; alarm [control_system]; no communication [control_system]; overflow [infrastructure]; backup [infrastructure]; pump fault [infrastructure] |  | 1 | 1
2026-03 | 2026-03-31 | Mount Albert Pumping Station | WW-CEAST | Attending site to replace wetwell level transmitter and flowmeter (W11769917). Devices were damaged due to electrical storm. Replaced, configured and tested wetwell level transmitter with Art. Parth and Rick replaced and configured discharge flowmeter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-04 | Mount Albert Pumping Station | WW-CEAST | On site collected monthly and weekly sewage samples and then, delivered to 145 HWP. Rinsed samples container. Reset composite sampler for next week sewage samples collection. | FLAG | stage2_low_confidence | 0.012237 | ML: above threshold (no LLM available) — 0.012 |  | 0.012237 | 0 | 0
2026-03 | 2026-03-09 | Mount Albert Pumping Station | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint). Both pumps available in auto. Standby power generator available in auto. Checked dry well, ok. Also, at around 11:00am, 4Refuel delivered diesel fuel, 400.2L. Previous level 12.2cm/914L Current level 17.6cm/1319L. Bypass sampling kit inspection Eye wash cleaning and solution inspection. Consolidated Dry Well and Hoist System Inspection Auto Dialer Alarm Test - alarm received and confirmed by ROC. Dry Well Flood Alarm Test - alarm received and confirmed by ROC. Sump Pit Inspection Hoist System Inspection No High/Low Temp Alarm Test in this facility. RS Pump Grease/Inspection Check Valve Inspection RS Pump Motor/Inspection Pump 1 - @ 50% speed, 43L: @ 100% speed, 63L Pump 2 - @ 50% speed, 37L: @ 100% speed, 58L | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; flood [critical]; work order [maintenance_action]; alarm [control_system] | bypass [critical]; flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-06 | Mount Albert Pumping Station | WW-CEAST | Took station readings and entered into Sharepoint - reviewed trends - all looks good. Station running under normal ops - no issues were found. | FLAG | stage2_low_confidence | 0.021237 | ML: above threshold (no LLM available) — 0.021 |  | 0.021237 | 0 | 0
2026-03 | 2026-03-27 | Mount Albert Pumping Station | WW-CEAST | Weather today is Partly Cloudy and -9 Celsius -On site to complete work order W11696163. -Completed station check. -Entered station readings into SharePoint. -Raw Sewage sampler check. -Both pumps are available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well, ok. -Station operations normal. | FLAG | stage2_low_confidence | 0.016375 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action] | 0.016375 | 0 | 0
2026-03 | 2026-03-23 | Mount Albert Pumping Station | WW-CEAST | Weather today Overcast and 0 Celsius -On site to complete work order W11668817, W11680778. -Completed station check. -Entered station readings into SharePoint. -Raw Sewage sampler check. -Both pumps are available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well, ok. -Station operations normal. | FLAG | stage2_low_confidence | 0.016546 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action] | 0.016546 | 0 | 0
2026-03 | 2026-03-26 | Mount Albert Pumping Station | WW-CEAST | Weather today a few clouds and 2 degrees Celsius -On site to complete work order W11690200. -Collected monthly and weekly sewage samples and then, delivered to 145 HWP. -Rinsed samples container. -Reset composite sampler for next week?s sewage samples collection. | FLAG | stage2_low_confidence | 0.024069 | ML: above threshold (no LLM available) — 0.024 | work order [maintenance_action] | 0.024069 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | -Remotely throttling flows going to Aurora SPS in response to NMMC Manhole 2 Level HiHi Alarms. -Ran two to three pumps together at reduced speeds. -Partially diverting flows to EQ tanks while keeping Screen Upstream levels below HiHi levels. | FLAG | stage2_low_confidence | 0.010049 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010049 | 0 | 0
2026-03 | 2026-03-11 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site to monitor station in response to high flow. Max 2 pumps running onsite with flow output of approx 880 l/s, maintaining ww level around 5m. Changed both barscreen run/rest setpoint from 6m/2m to 8m/1m to manage screen 2 upstream level | FLAG | stage2_low_confidence | 0.011629 | ML: above threshold (no LLM available) — 0.012 |  | 0.011629 | 0 | 0
2026-03 | 2026-03-03 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site to fix broken water line in screen room beside bay door. Also notice barscreen number 1 loud growl from top sprocket bearing. Investigated greased and ran quiet and smooth. | FLAG | stage2_low_confidence | 0.0080333 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080333 | 0 | 0
2026-03 | 2026-03-11 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). Standby power generator available in auto. Checked dry well, ok. checked screen room. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Bar Screen 1 making a growling noise. Greased Bar screen 1 bearings and now the noise is gone. Air compressors inspection and cleaning completed. In response to high flow, Max 2 pumps running onsite with flow output of approx 680 l/s, overflowing into the EQ tanks at 3.15pm. At around 3:30pm, on site monitored SCADA for the whole Central-East WW due to the weather. Too much incoming flows. Monitored SCADA for flows due to weather till 7.20pm. | FLAG | stage2_low_confidence | 0.2128 | ML: above threshold (no LLM available) — 0.213 | overflow [critical]; sso [critical]; noise [equipment_failure]; scada [control_system]; overflow [infrastructure] | 0.2128 | 0 | 0
2026-03 | 2026-03-06 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station check complete and the readings have been entered into the sharepoint. Pushed empty bin back into the screen room. | FLAG | stage2_low_confidence | 0.013643 | ML: above threshold (no LLM available) — 0.014 |  | 0.013643 | 0 | 0
2026-03 | 2026-03-02 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Raked rag bins. | FLAG | stage2_low_confidence | 0.013417 | ML: above threshold (no LLM available) — 0.013 |  | 0.013417 | 0 | 0
2026-03 | 2026-03-05 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site to complete consolidated monthly dry well pump floor inspection. Auto Dialer Alarm Test - alarm received and confirmed by ROC. Dry Well Flood Alarm Test - received and confirmed by ROC. Sump Pit Inspection Air Compressor Inspection Check Valve Inspection RS Pump and Motor Inspection Pump 1 - @ 0% speed 234 L/s, 129 kPa, 136 A, 617 V, 39 Hz; @ 25% speed 303 L/s, 170 kPa, 170 A, 617 V, 44 Hz; @ 35% speed 376 L/s, 162 kPa, 191 A, 617 V, 46 Hz Pump 2 - @ 0% speed 217 L/s, 132 kPa, 123 A, 384 V, 797 RPM, 40 Hz; @ 25% speed 308 L/s, 135 kPa, 152 A, 431 V, 896 RPM, 45 Hz; @ 100% speed 540 L/s, 172 kPa, 246 A, 574 V, 1193 RPM, 60 Hz Pump 3 - @ 0% speed 226 L/s, 132 kPa, 134 A, 372 V, 769 RPM, 39 Hz; @ 25% speed 294 L/s, 160 kPa, 173 A, 425 V, 878 RPM, 44 Hz; @ 35% speed 335 L/s, 158 kPa, 194 A, 446 V, 921 RPM, 46 Hz. Pump 4 - @ 0% speed 128 L/s, 142 kPa, 109 A, 615 V, 39 Hz; @ 25% speed 178 L/s, 163 kPa, 143 A, 618 V, 44 Hz; @ 35% speed 223 L/s, 149 kPa, 159 A, 616 V, 46 Hz. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; alarm [control_system] | sso [critical]; flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site with Total Lift for inspections | FLAG | stage2_low_confidence | 0.012314 | ML: above threshold (no LLM available) — 0.012 |  | 0.012314 | 0 | 0
2026-03 | 2026-03-27 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Flushed the drain screen and drain hose. Tipping bucket operational check completed. | FLAG | stage2_low_confidence | 0.015454 | ML: above threshold (no LLM available) — 0.015 |  | 0.015454 | 0 | 0
2026-03 | 2026-03-26 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site completed consolidated Wet Well Inspection: Wet Well High Level Alarm Test - received and confirmed by ROC. Sluice Gate Valve/Actuator Exercise Wet Well Valve Exercise Wet Well Inspection and Cleaning Bar Screen Cleaning/Lubrication Screw Conveyor Cleaning/Lubrication Consolidated monthly Surge Tank Inspection Surge Tank and System Inspection Surge Tank Drain Valve Inspection Transmission Lines Flushing Surge Tank Valve and Actuator Exercise and Inspection | FLAG | stage2_low_confidence | 0.013966 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system] | 0.013966 | 0 | 0
2026-03 | 2026-03-16 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. flushed the drain screen and drain hose. Overflow kit inspection. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure] | overflow [critical]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-19 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site to perform pm on air compressors. Changed oil and checked air filters. Inspected bar screens found barscreen #2 out of alignment when travelling over top sprockets. Found top drive sprocket key and key way worn. Removed and ordered parts. Waiting for parts to install. | FLAG | stage2_low_confidence | 0.01994 | ML: above threshold (no LLM available) — 0.02 | sso [critical] | 0.01994 | 0 | 0
2026-03 | 2026-03-20 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Flushed the drain screen and drain hose. | FLAG | stage2_low_confidence | 0.015076 | ML: above threshold (no LLM available) — 0.015 |  | 0.015076 | 0 | 0
2026-03 | 2026-03-25 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Air compressors inspection and cleaning completed. | FLAG | stage2_low_confidence | 0.026354 | ML: above threshold (no LLM available) — 0.026 | sso [critical] | 0.026354 | 0 | 0
2026-03 | 2026-03-18 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Air compressors inspection and cleaning completed. | FLAG | stage2_low_confidence | 0.029116 | ML: above threshold (no LLM available) — 0.029 | sso [critical] | 0.029116 | 0 | 0
2026-03 | 2026-03-23 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. flushed the drain screen and drain hose. | FLAG | stage2_low_confidence | 0.015076 | ML: above threshold (no LLM available) — 0.015 |  | 0.015076 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | @8:30am - Made some changes in response to high flow event. put pump 2 in duty 3 and increased duty 1 vfd min speed from 15% to 50% to minimize duty 2 start cleared ultrasonic interlock on pump 3 pump 1 vfd fault outstanding from last night, will be investigated on upcoming station checks. @12:32 - Put duty 1 vfd min speed back to 15%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure] | 0.0055551 | 0 | 0
2026-03 | 2026-03-30 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | FLAG | stage2_low_confidence | 0.010721 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010721 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | -Remotely made changes to respond to alarms coming in during period of high flows. -Placed pump 2 in duty 3. Pump 4 in duty 1, Pump 3 in duty 2. -Changed controlling LIT from LIT1 to LIT4. -Lowered duty 1 start set point from 2.25m to 2.20m -Increased duty 1 minimum speed set point from 15% to 25% to help avoid multiple duty 2 starts. | FLAG | stage2_low_confidence | 0.011022 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011022 | 0 | 0
2026-03 | 2026-03-13 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Station running normal. Consolidated Dry Well & Hoist System Inspection. Hoist System Inspection. Check valve inspection. Dry well flood alarm test. received and confirmed by ROC. Sump pit inspection. Air relief valve inspection. High low temp alarm test. received and confirmed by ROC. Autodialer test. alarm received and confirmed by ROC. RS pump motor / inspection. Pumps 1-4 RS pump motor / inspection. Pump 1 -16% - 82.9 L/s Pump 2 constant speed ? 193.9 L/s Pump 3 - 16% - 76.9 L/s Pump 4 - 16% - 82.7 L/s | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system] | flood [critical]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-02 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal. JHSC Health and Safety Inspection completed. Hazardous Waste Collection and Removal Odour control system, inspection and cleaning. Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped running without problem. Gen Start time: 273.22, Stop time: 274.37, Run time: 1:15hrs. Cleared/reset all alarms. Generator back in auto and available. | FLAG | stage2_low_confidence | 0.021611 | ML: above threshold (no LLM available) — 0.022 | scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] | 0.021611 | 0 | 0
2026-03 | 2026-03-09 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal | FLAG | stage2_low_confidence | 0.013971 | ML: above threshold (no LLM available) — 0.014 | scada [control_system] | 0.013971 | 0 | 0
2026-03 | 2026-03-12 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | On site to complete work orders. Manual valve exercise completed. RS pump discharge valve and Actuator, inspection and exercise. comprehensive housekeeping completed | FLAG | stage2_low_confidence | 0.022813 | ML: above threshold (no LLM available) — 0.023 | work order [maintenance_action] | 0.022813 | 0 | 0
2026-03 | 2026-03-10 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | On site to grease pump motors and drive shafts | FLAG | stage2_low_confidence | 0.012837 | ML: above threshold (no LLM available) — 0.013 |  | 0.012837 | 0 | 0
2026-03 | 2026-03-16 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal Seal water system maintenance completed. Overflow kit, inspection completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; scada [control_system]; overflow [infrastructure] | overflow [critical]; scada [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-27 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal. | FLAG | stage2_low_confidence | 0.014034 | ML: above threshold (no LLM available) — 0.014 | scada [control_system] | 0.014034 | 0 | 0
2026-03 | 2026-03-25 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | On site for vibration readings. All pumps left in auto | FLAG | stage2_low_confidence | 0.024233 | ML: above threshold (no LLM available) — 0.024 | vibration [equipment_failure] | 0.024233 | 0 | 0
2026-03 | 2026-03-23 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -OCU exhaust piping for wet well has blown apart, created a WO for CMS and notified CEWW Team - W117533481 -station okay | FLAG | stage2_low_confidence | 0.011482 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.011482 | 0 | 0
2026-03 | 2026-03-30 | SEC Boxgove Corrosion Control Facility | WW-CEAST | On site to complete work orders. Station Check (See details on SharePoint) Peristaltic Pump Inspection | FLAG | stage2_low_confidence | 0.020569 | ML: above threshold (no LLM available) — 0.021 | work order [maintenance_action] | 0.020569 | 0 | 0
2026-03 | 2026-03-30 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -cleaned screen room, rotated bin in screen room as necessary -station okay | FLAG | stage2_low_confidence | 0.011976 | ML: above threshold (no LLM available) — 0.012 | scada [control_system] | 0.011976 | 0 | 0
2026-03 | 2026-03-31 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | @8:25 - Placed pumps 1 and 3 OOS in manual off to leave 2 other pumps running in auto and in manual speed of 30% to slow down flow to Aurora SPS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-13 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. flushed the drain screen and drain hose. | FLAG | stage2_low_confidence | 0.015076 | ML: above threshold (no LLM available) — 0.015 |  | 0.015076 | 0 | 0
2026-03 | 2026-03-04 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Monthly diesel generator test run completed, readings entered into SharePoint. 9.50am - Transferred site to generator power. 10.55am - Transferred site back to utility power. Generator Start time: 288.7, Stop time: 290.0, Run time: 1:3hrs. JHSC Health and Safety Inspection completed. Hazardous Waste Collection and Removal Air compressors inspection and cleaning completed. Completed station housekeeping. | FLAG | stage2_low_confidence | 0.045648 | ML: above threshold (no LLM available) — 0.046 | sso [critical]; hazard [safety] | 0.045648 | 0 | 0
2026-03 | 2026-03-09 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Unclogged RS Pump #4 with Chris R. | FLAG | stage2_low_confidence | 0.015207 | ML: above threshold (no LLM available) — 0.015 | clog [infrastructure]; clogged [infrastructure] | 0.015207 | 0 | 0
2026-03 | 2026-03-31 | SEC Boxgove Corrosion Control Facility | WW-CEAST | -on site to complete work orders -Tank 1 has water in it, tank 2 has 0.5 meters of 50% H2O2 -using Tank 1 to keep chemical pumps running for warranty period -topping up Tank 1 with water -Chemical Tank Maintenance -Sump Pump Test -Ventilation System Inspection -Housekeeping -station okay | FLAG | stage2_low_confidence | 0.012456 | ML: above threshold (no LLM available) — 0.012 | work order [maintenance_action] | 0.012456 | 0 | 0
2026-03 | 2026-03-02 | SEC Boxgove Corrosion Control Facility | WW-CEAST | Took station readings and entered into Sharepoint ,, completed H & S inspection as well. Checked paristaltic pumps,, 1 of the pumps is down but 2 are working fine. Station running under normal ops - dosing water. | FLAG | stage2_low_confidence | 0.022396 | ML: above threshold (no LLM available) — 0.022 |  | 0.022396 | 0 | 0
2026-03 | 2026-03-05 | SEC Boxgove Corrosion Control Facility | WW-CEAST | On site to meet with SPD for back pressure/pressure relief adjustment for chemical pumps. Back pressure has been changed from 40 psi to 10 psi. Pressure relief have been changed from 60 psi to 30 psi | FLAG | stage2_low_confidence | 0.013791 | ML: above threshold (no LLM available) — 0.014 |  | 0.013791 | 0 | 0
2026-03 | 2026-03-09 | SEC Boxgove Corrosion Control Facility | WW-CEAST | Took station readings and entered into Sharepoint,, went through the station - no leaks in tanks, all looks good. Checked sump pits - OK. Station running under normal ops - no issues were found. | FLAG | stage2_low_confidence | 0.04074 | ML: above threshold (no LLM available) — 0.041 | leak [infrastructure] | 0.04074 | 0 | 0
2026-03 | 2026-03-16 | SEC Boxgove Corrosion Control Facility | WW-CEAST | Station check complete and the readings have been entered into the sharepoint. Revised 2026 sharepoint page via POA as it did not reflect recent chemical feed system upgrade. | FLAG | stage2_low_confidence | 0.010982 | ML: above threshold (no LLM available) — 0.011 |  | 0.010982 | 0 | 0
2026-03 | 2026-03-27 | SEC Boxgove Corrosion Control Facility | WW-CEAST | Took station readings and entered into Sharepoint - added water to tank 1 and went through the shelved alarms and nothing has changed. Cleaned the washroom and also swept out the HVAC room. Station running under normal ops - no new issues were found. | FLAG | stage2_low_confidence | 0.034187 | ML: above threshold (no LLM available) — 0.034 | alarm [control_system]; alarms [control_system] | 0.034187 | 0 | 0
2026-03 | 2026-03-09 | SEC Markham Odour Control Facility | WW-CEAST | Took station readings and entered into Sharepoint ,, greased the fan bearings and topped up the nutrient tanks. Tested the 3 actuators for the water supply in local - all good and they are back in remote, activated the sump pump and also tested the alarm - both work fine and sump pit is clear of debris. The HVAC is currently off - I believe due to winter temps. Could not check media spray as it takes two people to complete the task. Checked the Y strainers while topping up nutrient tanks - they all look good only the 2nd bio scrubber has a recirc pump running. Fan 3 is OOS but the rest of the staztion is running fine. Cleared all the alarms that I could. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | SEC Markham Odour Control Facility | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint) Currently, fan 1 and fan 2 running in auto as duty 1 and 2, respectively. Standby power generator available in auto. Water supply pumps are full of oil. Put fan 3 in e-stop/local out of service, CMS currently on-site checking knife gate that has faulted. Nutrient Tank Batch Mixing Nutrient tanks are full of water. Odour Control Fans Impeller Bearing Lubrication | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure]; impeller [equipment_failure]; work order [maintenance_action] | fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure]; impeller [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-03 | SEC Markham Odour Control Facility | WW-CEAST | Here to meet up with contractor ( got a phone call) and we are going to run the Diesel and do the maintainance check. Checked the fluids out on the Diesel - all good, Batteries need to be replaced as well as the Fan belts ( Company will submit a evaluation ) Shut the Fans down and transferred power over to Diesel - no issues. While Diesel was running completed H & S inspection - no issues were found. Took Diesel readings and entered into Sharepoint - Company found that the Diesel was operating fine. Shut the fans back down and switched back to main power - no issues during transfer ,, cleared the alarms and informed ROC I was all finished here. Fan 3 is still OOS but 1 & 2 are fine. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-27 | SEC Markham Odour Control Facility | WW-CEAST | Took station readings and entered into Sharepoint,, checked all 3 nutrient tanks as well as the oil level on the water pumps - all good. Greased the bearings on Fans 1 & 2 - 3 is OOS and also cleaned up the washroom/ office area and swept out the MCC room. Station running under normal ops - Fan 3 is OOS. Also went through the shelved alarms and nothing has changed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-16 | SEC Markham Odour Control Facility | WW-CEAST | Station check complete and the readings have been entered into the sharepoint. Created CMU3 for INST to repair O2 sensors @ shaft 9/ocf damper station/fan room Cleared fan room O2 alarm and turned off high ventilation. Heaters in the fan/mech room still not working as intended and producing room temp air, notified SUP to follow up with PS Fan 3 OOS due to the suction knife gate fault, CMU has been previously submitted to CMS | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; not working [equipment_failure]; repair [maintenance_action]; alarm [control_system] | fault [equipment_failure]; oos [equipment_failure]; not working [equipment_failure]; repair [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | SEC Markham Odour Control Facility | WW-CEAST | -On site for immersion heater inspections. -Inspected immersion heaters, pumped down humid chambers to test low level alarms and ensure heaters turned off with low levels. -Equipment Room 3 immersion heater has been locked out by the electrical team and is OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | SEC Markham Odour Control Facility | WW-CEAST | Onsite to troubleshoot carbon unit O2 sensor and fan room outlet O2 sensor Informed ROC Replaced sensor and calibrated Cleared associated alarms ODOR _GO25 is still in alarm on local gas panel. Cannot locate this device on scada or at facility Informed ROC and left site | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system] | sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | SEC Markham Odour Control Facility | WW-CEAST | Went through alarm management for the SEOC and YDOC - all alarms shelved are still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-11 | SEC Fairport Air Handling Facility (Shaft 4) | WW-CEAST | Took station readings and entered into Sharepoint,, reviewed trends - all good. Completed H & S inspection as well as Diesel Test run and entered readings into Sharepoint. Verified Heat trace is on and operational. Exercised all the actuators with the Fans as well as a partial exercise of the knife gate valves. All alarms cleared except O2 sensor(WO has been created) and station is running under normal ops. | FLAG | stage2_low_confidence | 0.070091 | ML: above threshold (no LLM available) — 0.07 | alarm [control_system]; alarms [control_system] | 0.070091 | 0 | 0
2026-03 | 2026-03-05 | SEC Markham Odour Control Facility | WW-CEAST | Here to clean the mist eliminators , opened the panel door and hosed down the mist eliminators - a bit messy. cleaned up the floor and washed everything down the drain. Station running under normal ops - Fan 3 is OOS. | FLAG | stage2_low_confidence | 0.049901 | ML: above threshold (no LLM available) — 0.05 | oos [equipment_failure] | 0.049901 | 0 | 0
2026-03 | 2026-03-02 | SEC Markham Odour Control Facility | WW-CEAST | Entered station readings into Sharepoint ,, greased blowers 1 & 2 - blower 3 is OOS,, topped up nutrient tanks and also checked the oil level on the water pumps. Walked through the station and everything looks good also went into the Diesel room - no leaks around the Diesel and everything is in auto. Also checked the blower Fans 1 & 2 - belts look fine and are running straight. Station is running under normal ops - blower 3 is OOS. | FLAG | stage2_low_confidence | 0.197 | ML: above threshold (no LLM available) — 0.197 | oos [equipment_failure]; leak [infrastructure] | 0.197 | 0 | 0
2026-03 | 2026-03-04 | SEC Fairport Air Handling Facility (Shaft 4) | WW-CEAST | Took station readings and entered into Sharepoint,, reviewed trends - all good. Cleared alarms from last night and station is running under normal ops - no issues were found. ( gas monitor sensor is out but WO has been created) | FLAG | stage2_low_confidence | 0.038598 | ML: above threshold (no LLM available) — 0.039 | alarm [control_system]; alarms [control_system] | 0.038598 | 0 | 0
2026-03 | 2026-03-18 | SEC Fairport Air Handling Facility (Shaft 4) | WW-CEAST | Took station readings and entered into Sharepoint, reviewed trends - all good. Swept out main office and cleaned up washroom. Station running under normal ops - no issues found. | FLAG | stage2_low_confidence | 0.024922 | ML: above threshold (no LLM available) — 0.025 |  | 0.024922 | 0 | 0
2026-03 | 2026-03-24 | SEC Fairport Air Handling Facility (Shaft 4) | WW-CEAST | Onsite to troubleshoot fan room O2 sensor. Informed ROC Found O2 gas detector reading 10% Replaced sensor and calibrated Cleared associated alarms Informed ROC, armed building and left site | FLAG | stage2_low_confidence | 0.016148 | ML: above threshold (no LLM available) — 0.016 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.016148 | 0 | 0
2026-03 | 2026-03-25 | SEC Fairport Air Handling Facility (Shaft 4) | WW-CEAST | Took station readings and entered into Sharepoint,, reviewed trends and checked the Diesel room - all good. Station running under normal ops - no issues were found. | FLAG | stage2_low_confidence | 0.023517 | ML: above threshold (no LLM available) — 0.024 |  | 0.023517 | 0 | 0
2026-03 | 2026-03-25 | SEC Fairport Air Handling Facility (Shaft 4) | WW-CEAST | On site for vibration readings. Had the ROC rotate duty?s | FLAG | stage2_low_confidence | 0.024564 | ML: above threshold (no LLM available) — 0.025 | vibration [equipment_failure] | 0.024564 | 0 | 0
2026-03 | 2026-03-11 | SEC Altona Air Handling Facility (Shaft 6/7) | WW-CEAST | Took station readings and entered into Sharepoint and reviewed trends - all good. Checked Heat Trace system - all working fine. Station running under normal ops - no issues were found. | FLAG | stage2_low_confidence | 0.025765 | ML: above threshold (no LLM available) — 0.026 |  | 0.025765 | 0 | 0
2026-03 | 2026-03-04 | SEC Altona Air Handling Facility (Shaft 6/7) | WW-CEAST | Checked fluids on Diesel and then transferred power over for the Diesel test run,, entered station readings into Sharepoint and reviewed trends - all looks good. Exercised actuators by switching fan Duty once power was transferred (shut fans down before transferring power). Partially exercised knife gates before and after switching fan Duty. Completed H & S check - all good. | FLAG | stage2_low_confidence | 0.06254 | ML: above threshold (no LLM available) — 0.063 |  | 0.06254 | 0 | 0
2026-03 | 2026-03-25 | SEC Altona Air Handling Facility (Shaft 6/7) | WW-CEAST | Met up with the water delivery and we could not fill the tank as there was a valve closed but the E-Key does not work on that door so water delivery will have to be re-scheduled. Took station readings and entered into Sharepoint, reviewed trends - all good. Also swept out the main room, MCC room. Station running under normal ops - no issues were found. | FLAG | stage2_low_confidence | 0.056124 | ML: above threshold (no LLM available) — 0.056 |  | 0.056124 | 0 | 0
2026-03 | 2026-03-30 | Bayview & Steeles Air Management Facility | WW-CEAST | Station check complete. confirmed condensation draining as intended. No unusual odor detected onsite during visit Heater element - 71.8 Hydro - 288964 kwh VFD Chiller - no display on-site | FLAG | stage2_low_confidence | 0.0089793 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089793 | 0 | 0
2026-03 | 2026-03-18 | SEC Altona Air Handling Facility (Shaft 6/7) | WW-CEAST | Took station readings and entered into Sharepoint - reviewed trends, all good. Verified hoist operation and also checked the filters on the HVAC but its off due to winter temps. Station running under normal ops - no issues were found. | FLAG | stage2_low_confidence | 0.032479 | ML: above threshold (no LLM available) — 0.032 |  | 0.032479 | 0 | 0
2026-03 | 2026-03-02 | Bayview & Steeles Air Management Facility | WW-CEAST | -On site to complete work orders. -Station check completed. -Heater element: 95.4F. -Hydro meter: 283523kWh. -Fan is running, no odours detected while on site. -Monthly JHSC H&S inspection completed. -Odour control scrubber inspection completed. | FLAG | stage2_low_confidence | 0.014472 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action] | 0.014472 | 0 | 0
2026-03 | 2026-03-09 | Bayview & Steeles Air Management Facility | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Heater element: 82.2F. -Hydro meter: 284777kWh. -Mist eliminator filters, clean and replace completed. All mist eliminator filters changed out with clean spares. -0937 - Turned off fan for mist eliminator maintenance. -0953 - Fan turned back on after changing out mist eliminator filters. -Inspected fan belts and greased fan shaft while on site. | FLAG | stage2_low_confidence | 0.025336 | ML: above threshold (no LLM available) — 0.025 | work order [maintenance_action] | 0.025336 | 0 | 0
2026-03 | 2026-03-23 | Bayview & Steeles Air Management Facility | WW-CEAST | On site for station check. Heater Element - 89.1 F Hydro Meter Reading - 287516 Kwh VFD Chiller - No temp reading. Fan and motor running. No bad odour at time of visit. Station operation normal. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064961 | 0 | 0
2026-03 | 2026-03-16 | Bayview & Steeles Air Management Facility | WW-CEAST | -On site to perform a station check. -Heater element: 86.0F. -Hydro meter: 286147kWh. -Fan running, no odours detected on site. | FLAG | stage2_low_confidence | 0.0081757 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081757 | 0 | 0
2026-03 | 2026-03-30 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | On site for electric meter replacement to be done by Toronto Hydro. Address on their work order is 8A Pickering Townline, which is YDOC 2001 Scarborough Pickering Townline. They arrived on site at around 8:00am, however, I'm not yet on site so they went to another appointment. When I called them, they said they will be back around 12:00pm. At 12:00 Noon, Toronto Hydro arrived on site. They replaced the electric meter of the Boundary Meter Facility, not YDOC. | FLAG | stage2_low_confidence | 0.04191 | ML: above threshold (no LLM available) — 0.042 | work order [maintenance_action] | 0.04191 | 0 | 0
2026-03 | 2026-03-04 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | Took station readings and entered into Sharepoint ,, reviewed trends and went through the station. Nutrient tanks are good. Fan 1 is still OOS but rest of the station is running under normal ops. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-05 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | Here to clean the mist eliminators,, Fan 2 is the only one running so I left that one but I took 1 out - no to bad, hosed it down as best I could and replaced it. Station running under normal ops - fan 1 is OOS but the rest is running fine. | FLAG | stage2_low_confidence | 0.057125 | ML: above threshold (no LLM available) — 0.057 | oos [equipment_failure] | 0.057125 | 0 | 0
2026-03 | 2026-03-03 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | Here to complete WO's,, checked fluid levels on the Diesel, green light on the batteries and started my Diesel test run. while Diesel was running I completed the H & S check - no issues were found. Entered readings from the Diesel run into Sharepoint. Had to bring the contractor back after SEOC - I had no idea this was going on today, He took down the readings from the Diesel run and also checked out the Diesel. Station back to normal ops - Fan 1 is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-11 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | Took station readings and entered into Sharepoint,, reviewed trends and Fan 1 is OOS. Checked nutrient tanks - all good. Station running with 1 fan(2) . | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | Took station readings and entered into Sharepoint,, reviewed trends - all good. Fan 1 is OOS and nutrient tanks have been topped up. cleared all alarms (new). Station running with Fan 2 only. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-25 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | Took station readings and entered into Sharepoint,, reviewed trends and also checked the nutrient tanks. Checked the strainers on the recirc pumps and cleaned them both out. Did a blower inspection on Fan 2 and greased it, Fan 1 is OOS, walked around the cat walk and checked media sprayers on line 2 - there are a few not working. Also swept up the main floor and around the Generator. Fan 1 is OOS but Fan 2 is working fine. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; not working [equipment_failure] | oos [equipment_failure]; not working [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-26 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | Check battery type 4D Belt is due for replacement. | FLAG | stage2_low_confidence | 0.008841 | ML: above threshold (no LLM available) — 0.009 |  | 0.008841 | 0 | 0
2026-03 | 2026-03-25 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | On site for vibration readings | FLAG | stage2_low_confidence | 0.021603 | ML: above threshold (no LLM available) — 0.022 | vibration [equipment_failure] | 0.021603 | 0 | 0
2026-03 | 2026-03-11 | Central-East Wastewater Linear System | WW-CEAST | -Passive scrubber inspections/maintenance completed for the following locations: -Major Mackenzie and Leslie -Warden and Enterprise -Milne Park -Tuclor Lane -Woodbine and 16th | FLAG | stage2_low_confidence | 0.007579 | ML: above threshold (no LLM available) — 0.008 |  | 0.007579 | 0 | 0
2026-03 | 2026-03-12 | Central-East Wastewater Linear System | WW-CEAST | -On site to perform Aurora East Forcemain Chamber inspections. -Completed inspections, multiple chambers full of water, will have to revisit chambers at a later date to pump out groundwater. | FLAG | stage2_low_confidence | 0.020864 | ML: above threshold (no LLM available) — 0.021 |  | 0.020864 | 0 | 0
2026-03 | 2026-03-25 | Central-East Wastewater Linear System | WW-CEAST | -inspected Jefferson Forest and Yonge passive scrubber -media was replaced, site okay | FLAG | stage2_low_confidence | 0.013578 | ML: above threshold (no LLM available) — 0.014 |  | 0.013578 | 0 | 0
2026-03 | 2026-03-25 | Central-East Wastewater Linear System | WW-CEAST | On site for Leslie PS forcemain inspection of the following chambers. 71-01 (chamber pumped out) LSMFT-01 (chamber pumped out) LSMFT-02 (Chamber full of water but cannot be pumped out due to no access for the truck/equipment) 71-03 71-04W 71-04E (chamber pumped out) 43-02 LSMFT-03 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067133 | 0 | 0
2026-03 | 2026-03-26 | Central-East Wastewater Linear System | WW-CEAST | On site to continue working on the Leslie PS chamber inspections. 71-02 (Chamber cannot find - near chamber no. LSFMT-02) 94-01 (Chamber cannot find) 43-01 (chamber pumped out) 43-03 (Chamber cannot find) LSFMT-04 (Chamber cannot find) 43-04 (Outfall - did not inspect) | FLAG | stage2_low_confidence | 0.0091418 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091418 | 0 | 0
2026-03 | 2026-03-19 | Central-East Wastewater Linear System | WW-CEAST | On site for chamber inspection of Aurora West Forcemain and Henderson Twin Forcemains. 28-CH01 - Yonge/Henderson 28-CH02 - Yonge/Industrial Pkwy S 28-CH03 - Industrial Pkwy S/Yonge | FLAG | stage2_low_confidence | 0.010454 | ML: above threshold (no LLM available) — 0.01 |  | 0.010454 | 0 | 0
2026-03 | 2026-03-25 | Central-East Wastewater Linear System | WW-CEAST | -completed chamber checks for Aurora East FM inspections -pumped out half of the chambers which were flooded, still require a days work to pump out the rest | FLAG | stage2_low_confidence | 0.030076 | ML: above threshold (no LLM available) — 0.03 | flood [critical] | 0.030076 | 0 | 0
2026-03 | 2026-03-31 | Vaughan Black Creek Pumping Station | WW-WEST | onsite for station check - no new issues. reviewed trends and added data into sharepoint. pump run test: pump 1 - 553.1L/s at 300kPa pump 2 - 450.4L/s at 268lPa at 100% pump 3 - 133.0L/s at 214lPa at 100% pump 4 - 467.1L/s at 261kPa at 100% pump 5 - OOS (known issue) All pumps placed back into auto and back into duty rotation. pushed barscreen bin outside for pick up. completed comprehensive housekeeping - cleaned bathroom and entrance. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-10 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check - no new issues reviewed trends and added data to SharePoint. Oil dispenser for bar screen not pumping. Tried to fix with no success. Will need to order new one. | FLAG | stage2_low_confidence | 0.018263 | ML: above threshold (no LLM available) — 0.018 |  | 0.018263 | 0 | 0
2026-03 | 2026-03-09 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for PMs with Marcus. Completed dry well consolidated inspection. Wetwell and barscreen consolidated inspection and air relief valve flushing. Created work order for pump 4 check valve not closing. | FLAG | stage2_low_confidence | 0.026288 | ML: above threshold (no LLM available) — 0.026 | work order [maintenance_action] | 0.026288 | 0 | 0
2026-03 | 2026-03-13 | Vaughan Black Creek Pumping Station | WW-WEST | Station checks, SharePoint readings and review of continuous monitoring data Level screen room bin and clean floor. Pump test runs on pump 1 & 4. - ok- Pump 3 running on entry and 2/5 OOS. | FLAG | stage2_low_confidence | 0.017943 | ML: above threshold (no LLM available) — 0.018 | oos [equipment_failure] | 0.017943 | 0 | 0
2026-03 | 2026-03-11 | Vaughan Black Creek Pumping Station | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Placed Pumps #1, 3 and 4 in Manual Off. Transferred Station to Generator Power with No Issues. Acknowledged and Cleared Associated Alarms. Returned Pumps #1, 3 and 4 to Auto. Duties #1 and 2 Activated Automatically. Completed Heat Exchanger Radiator Inspection. Visible Internal and External Piping OK. Unable to Assess Rooftop Radiator Unit due to Ladder Access H&S Concerns. Placed Pumps #1, 3 and 4 in Manual Off. Activated Pump #1 in Manual for Wet Well Drawdown. Drawdown Complete, Returned Pump #1 to Manual Off. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. Returned Pumps #1, 3 and 4 to Auto. Completed JHSC and Hazardous Waste Inspections with No Issues. Cleared Associated Alarm. | FLAG | stage2_low_confidence | 0.043711 | ML: above threshold (no LLM available) — 0.044 | sso [critical]; alarm [control_system]; alarms [control_system]; hazard [safety] | 0.043711 | 0 | 0
2026-03 | 2026-03-12 | Vaughan Black Creek Pumping Station | WW-WEST | On site to look at pump 4 check valve stuck open. Removed end caps on shaft cleaned out debris greased and re installed. Check valve now moving free. | FLAG | stage2_low_confidence | 0.024945 | ML: above threshold (no LLM available) — 0.025 | valve stuck [infrastructure] | 0.024945 | 0 | 0
2026-03 | 2026-03-06 | Vaughan Black Creek Pumping Station | WW-WEST | LOTO Complete PM?s on all pumps Greased driveshafts and pumps. Complete | FLAG | stage2_low_confidence | 0.0088643 | ML: above threshold (no LLM available) — 0.009 |  | 0.0088643 | 0 | 0
2026-03 | 2026-03-06 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check. Pump run test and seal water test pm. Station check ok - no new issues. Reviewed trends and added data into SharePoint. Pushed empty bin back in and topped up oil on bar screen. Pump run test : Pump1 - 601.7L/s at 281kPa Pump 2 - 469.9L/s at 100% at 257kPa Pump 3 - 133.3L/s at 100% at 214kPa Pump4 - 470.1L/s at 100% at 267kPA Pump 5 -OOS Completed seal water test PM no new issues. Checked seal water screens - all clear. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-09 | Vaughan Black Creek Pumping Station | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Manually Rotated Scrubber Blower Duties. Blower #2 in Duty #1, Pump #1 in Duty #2. Completed Bar-screen and Wet Well Inspections. Tested Wet Well Overflow Alarms. Confirmed Reception by the ROC. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Consolidated Dry Well Inspections. Tested Hi/Lo Temperature and Dry Well Flood Alarms. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. Pump #2 Failed to Start on Several Attempts, Using Multiple Methods, Such as Manual Start and Auto Duty Start. Suspected Discharge Valve Communication Error. Created Follow Up WO for PCS ?> W11719088. Pump #2 Manual Off and OOS Until Issue Rectified. Completed FM Air Valve Flushing and Inspections with No Issues. Returned to Service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; sso [critical]; flood [critical]; failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; communication error [control_system]; overflow [infrastructure] | overflow [critical]; sso [critical]; flood [critical]; failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system]; communication error [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-26 | Vaughan Black Creek Pumping Station | WW-WEST | On site to troubleshoot pump 2 failing to start. With assistance from ROC, was able to observe pump 2 starting and running for two auto cycles. There were no issues to be seen. | FLAG | stage2_low_confidence | 0.017865 | ML: above threshold (no LLM available) — 0.018 |  | 0.017865 | 0 | 0
2026-03 | 2026-03-20 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check and weekly pump run test. No new issues. Reviewed trends and added data into SharePoint. Pump run test: Pump1 - 571.5L/s at 303kPa Pump 2 - OOS Pump 3 - 131.3L/s at 215kPa Pump4 - 473.8L/s at 269kPa Pump 5 -OOS After running pump 4 and placing it in manual off - discharge valve closed alarm came in. Reset and cleared alarm. Checked discharge and check valve all normal. Will continue to monitor. Returned all in service pumps back to auto. Pumps 2 and 5 left in manual off. Known issues with work orders created. Bar screen running and operating normally. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Bar screen room okay- replaced broken oil pump and topped up bar screen oil. Inspected spill kit - all sample bottles ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical] | spill [critical] |  | 1 | 0
2026-03 | 2026-03-23 | Vaughan Black Creek Pumping Station | WW-WEST | Completed wetwell manual valve exercise. All valves exercised and sprayed down floors. Everything operating as normal | FLAG | stage2_low_confidence | 0.013074 | ML: above threshold (no LLM available) — 0.013 |  | 0.013074 | 0 | 0
2026-03 | 2026-03-17 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and entered data into SharePoint Pumps #2 and #5 still OOS - known issues with WO made Ran pump 4 to try to replicate the disch. Valve closed alarm from yesterday - alarm did not come in and pump ran normally. Checked contact on the valve and it appeared normal. Bin pushed out for pick up. Barscreen room ok. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | Vaughan Black Creek Pumping Station | WW-WEST | On site to investigate bar screen fault alarm. No visual indicators of problem. Pressed reset button. Screen started and ran fine. Ran in hand for a few cycles and monitored. Found no problems. Returned to auto and reset alarms. | FLAG | stage2_low_confidence | 0.021033 | ML: above threshold (no LLM available) — 0.021 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.021033 | 0 | 0
2026-03 | 2026-03-23 | Vaughan Black Creek Pumping Station | WW-WEST | In to Complete Scheduled WO. | FLAG | stage2_low_confidence | 0.012569 | ML: above threshold (no LLM available) — 0.013 |  | 0.012569 | 0 | 0
2026-03 | 2026-03-03 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check and PMs Station check completed - reviewed trends and added data into SharePoint. Pump 4 check valve not closing. Cycled pump on to try to clear unsuccessful in getting check valve to close. Will continue to monitor and create work order if needed. Bar screen bin placed outside for pick up. Inspected odour control scrubber unit. Put unit into LOTO - Greased and checked belts. All okay. Mist eliminator at 2inches of water. Removed filter to clean and replaced with spare clean filter. Returned unit to on. Unit now at 1.6inches of water. | FLAG | stage2_low_confidence | 0.032864 | ML: above threshold (no LLM available) — 0.033 | work order [maintenance_action] | 0.032864 | 0 | 0
2026-03 | 2026-03-16 | Vaughan Black Creek Pumping Station | WW-WEST | Remotely Rotated Scrubber Blower Duties. Blower #1 in Duty #1, Pump #2 in Duty #2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054242 | 0 | 0
2026-03 | 2026-03-19 | Vaughan Black Creek Pumping Station | WW-WEST | On site to check dialer. Low battery alarm. Got replacement battery and installed. Ok now. | FLAG | stage2_low_confidence | 0.017358 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system] | 0.017358 | 0 | 0
2026-03 | 2026-03-27 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check - no new issues. Pump 2 fixed and back into duty rotation. Reviewed trends and added data into SharePoint. Barscreen okay - no issues | FLAG | stage2_low_confidence | 0.010138 | ML: above threshold (no LLM available) — 0.01 |  | 0.010138 | 0 | 0
2026-03 | 2026-03-31 | Vaughan Humber Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Bins pushed outside for pick up | FLAG | stage2_low_confidence | 0.013486 | ML: above threshold (no LLM available) — 0.013 |  | 0.013486 | 0 | 0
2026-03 | 2026-03-29 | Vaughan Humber Pumping Station | WW-WEST | Onsite to level barscreen bins | FLAG | stage2_low_confidence | 0.012652 | ML: above threshold (no LLM available) — 0.013 |  | 0.012652 | 0 | 0
2026-03 | 2026-03-13 | Vaughan Humber Pumping Station | WW-WEST | Onsite for station check and to meet Total Lift for sky jack and pallet truck inspection. Station check ok, no new issues. Reviewed trends and added data into SharePoint. Bar screen okay - rag bins leveled Empty rag bins pushed back in. Total Lift onsite at 10am Offsite at 10:20am - total power going to get new batteries for pallet truck. Back onsite at 11:11am to wait for Total Lift to return. Total Lift back onsite at 11:45am. Pallet truck batteries replaced and on charge. Skyjack batteries water refilled and inspections completed by Total Lift at 12:30pm Signed and reviewed all papers. | FLAG | stage2_low_confidence | 0.014907 | ML: above threshold (no LLM available) — 0.015 |  | 0.014907 | 0 | 0
2026-03 | 2026-03-15 | Vaughan Humber Pumping Station | WW-WEST | In to Complete Scheduled WO. Reviewed SCADA and Trends. No Issues Found. Levelled and Adjusted Bins. Inspected and Tidied HWs. Bar-screen Oil Hoppers OK. | FLAG | stage2_low_confidence | 0.01384 | ML: above threshold (no LLM available) — 0.014 | scada [control_system] | 0.01384 | 0 | 0
2026-03 | 2026-03-07 | Vaughan Humber Pumping Station | WW-WEST | On site to check and level screen room bins. | FLAG | stage2_low_confidence | 0.01282 | ML: above threshold (no LLM available) — 0.013 |  | 0.01282 | 0 | 0
2026-03 | 2026-03-03 | Vaughan Humber Pumping Station | WW-WEST | In to Receive Odour Control Unit Components for New Construction WVSS. | FLAG | stage2_low_confidence | 0.015247 | ML: above threshold (no LLM available) — 0.015 |  | 0.015247 | 0 | 0
2026-03 | 2026-03-03 | Vaughan Humber Pumping Station | WW-WEST | Onsite to assist with new odour control parts delivery. Completed station check - no new issues reviewed trends and added data into SharePoint. Bins pushed out for pick up. | FLAG | stage2_low_confidence | 0.011895 | ML: above threshold (no LLM available) — 0.012 |  | 0.011895 | 0 | 0
2026-03 | 2026-03-02 | Vaughan Humber Pumping Station | WW-WEST | Onsite for PMs. Called ROC to inform of generator run test and work being done. Pumped down wet well and placed all pumps in manual before transferring power to generator at 9:03am. Transferred smoothly pumps placed back in auto. Recorded generator run data into SharePoint. Inspected heat exchanger - operating normally Generator run test completed at 10:10am and power transferred back to hydro smoothly. Completed JHSC inspection and checked site for hazardous waste. Inspected hoist system - operates normally. Inspected force main valve chamber and triggered the valve chamber flood alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; hazard [safety] | flood [critical]; alarm [control_system]; hazard [safety] |  | 1 | 0
2026-03 | 2026-03-06 | Vaughan Humber Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Leveled bins and pushed empty bins back inside. | FLAG | stage2_low_confidence | 0.014488 | ML: above threshold (no LLM available) — 0.014 |  | 0.014488 | 0 | 0
2026-03 | 2026-03-18 | Vaughan Humber Pumping Station | WW-WEST | Onsite for dry well and wet well consolidated work orders with Marcus Completed housekeeping work order - cleaned bathroom and swept main room | FLAG | stage2_low_confidence | 0.026154 | ML: above threshold (no LLM available) — 0.026 | work order [maintenance_action] | 0.026154 | 0 | 0
2026-03 | 2026-03-24 | Vaughan Humber Pumping Station | WW-WEST | Onsite for station check. No new issues. Reviewed trends and added data into SharePoint. Inspected spill kit - no issues. Bins out for pick up | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical] | spill [critical] |  | 1 | 0
2026-03 | 2026-03-18 | Vaughan Humber Pumping Station | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Completed Consolidated Dry Well Inspections and Maintenance. Greased Pumps and Driveshafts. Tested Associated Alarms and Confirmed Reception by the ROC. Cleared Associated Alarms. Completed Consolidated Wet Well Inspections and Maintenance. Greased Bar-screen Sprockets. Tested Associated Alarms and Confirmed Reception by the ROC. Cleared Associated Alarms. | FLAG | stage2_low_confidence | 0.066573 | ML: above threshold (no LLM available) — 0.067 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.066573 | 0 | 0
2026-03 | 2026-03-17 | Vaughan Humber Pumping Station | WW-WEST | On site for annual inspection of scissor lift and pallet lift. | FLAG | stage2_low_confidence | 0.021865 | ML: above threshold (no LLM available) — 0.022 | sso [critical] | 0.021865 | 0 | 0
2026-03 | 2026-03-20 | Vaughan Humber Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Bar screen room okay - leveled rag bins | FLAG | stage2_low_confidence | 0.014122 | ML: above threshold (no LLM available) — 0.014 |  | 0.014122 | 0 | 0
2026-03 | 2026-03-17 | Vaughan Humber Pumping Station | WW-WEST | In to Complete Scheduled WOs and Assist Maint. with Bar-screen #2 Repair Work. Bar-screen #2 Rake Re-Aligned and Tested with No Issues. Returned Bar-screen Inlet Gate to Manual Open. Cleared Associated Alarm. Adjusted Bar-screen #1 Run Time Interval: 6 ?> 12.5 mins. Removed and Replaced HWs Bins for Pick Up. Tidied and Inspected HWs. Topped Up Bar-screen Oil Hoppers. No New Issues Found. Reviewed SCADA and Trends. No Issues Found. | FLAG | stage2_low_confidence | 0.048097 | ML: above threshold (no LLM available) — 0.048 | sso [critical]; repair [maintenance_action]; scada [control_system]; alarm [control_system] | 0.048097 | 0 | 0
2026-03 | 2026-03-24 | Vaughan Humber Pumping Station | WW-WEST | On site to meet with Total Lift to have the 10 year engineering certify on scissor lift. | FLAG | stage2_low_confidence | 0.018852 | ML: above threshold (no LLM available) — 0.019 | sso [critical] | 0.018852 | 0 | 0
2026-03 | 2026-03-22 | Vaughan Humber Pumping Station | WW-WEST | Checked and levelled screen room rag bins. | FLAG | stage2_low_confidence | 0.01359 | ML: above threshold (no LLM available) — 0.014 |  | 0.01359 | 0 | 0
2026-03 | 2026-03-16 | Vaughan Humber Pumping Station | WW-WEST | In to Investigate Bar-screen #2 Fault Communicated by the ROC. Found Bar-screen Torque Overload Fault due to Rake Misalignment. Placed Bar-screen in Local Off/OOS and Isolated Inlet Valve. Bar-screen #2 Not in Auto Alarm to Remain Outstanding. Adjusted Bar-screen #1 Run Time Interval: 12.5 ?> 6 mins. Created Follow-Up WO for Maint. ?> W11737270. Will Communicate with Appropriate Staff for Remedy at Next Earliest Convenience. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; follow-up [maintenance_action]; alarm [control_system] | fault [equipment_failure]; oos [equipment_failure]; follow-up [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-10 | Vaughan Humber Pumping Station | WW-WEST | Onsite for station check - no new issues. reviewed trends and added data into SharePoint Bins pushed out for pick up. | FLAG | stage2_low_confidence | 0.013263 | ML: above threshold (no LLM available) — 0.013 |  | 0.013263 | 0 | 0
2026-03 | 2026-03-27 | Vaughan Humber Pumping Station | WW-WEST | Onsite for station check - no new issues reviewed trends and added data into SharePoint. Pushed fixed rag bin back inside. Topped up oil on bar screen | FLAG | stage2_low_confidence | 0.015537 | ML: above threshold (no LLM available) — 0.016 |  | 0.015537 | 0 | 0
2026-03 | 2026-03-17 | Vaughan Humber Pumping Station | WW-WEST | Repaired barscreen 2 Completed PM?s on both barscreens Barscreen 1 needs a chain oiler brush. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | repair [maintenance_action] | 0.0069966 | 0 | 0
2026-03 | 2026-03-24 | Vaughan Humber Pumping Station | WW-WEST | Check backflow setup for new building | FLAG | stage2_low_confidence | 0.013109 | ML: above threshold (no LLM available) — 0.013 |  | 0.013109 | 0 | 0
2026-03 | 2026-03-24 | Vaughan Humber Pumping Station | WW-WEST | On site with Lance Johnson. Sealed holes around screen room roll up door where rats have been getting access. Used spray foam, dirt, stones and bricks. | FLAG | stage2_low_confidence | 0.02096 | ML: above threshold (no LLM available) — 0.021 |  | 0.02096 | 0 | 0
2026-03 | 2026-03-29 | Kleinburg Water Resource Recovery Facility | WW-WEST | remotely enabled batch wasting mode at 6am Onsite at 8:30am manually wasted 30m3 total from 8:30am to 9am. RAS resumed after wasting completed. added 14 bags of soda ash to hopper | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006529 | 0 | 0
2026-03 | 2026-03-30 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated STT 1 & transferred to SHT -Started batch wasting process at 09:30 to waste from 10:00 - 12:25 for 36.97m^3, Train 1(14.97m^3) & Train 2(22.00m^3). Wasted more from tank 2 to help balance out solids. -Completed lab analysis & station check, no abnormalities found -Turned RAS pumps 1&3 into manual off -Turned RAS pumps 2&4 into auto -Turned WAS pumps 1 &2 into manual off -Added 11 bags of soda ash into hopper -Completed scum tank cleaning, used skimmers in local. Set skimmers back into remote. -Completed aeration tank/channel outlet weir cleaning -Completed aeration condensation line bleed out, no liquid or solids were present -Raked bar screen & dewatering press -Cleaned rags off of distribution chamber inlet valve stem & aeration inlet valve stems -Switched outlet weir effluent hose to tank 1 due to outlet weir foam build up -Hosed down and cleaned sand filters | FLAG | stage2_low_confidence | 0.041894 | ML: above threshold (no LLM available) — 0.042 |  | 0.041894 | 0 | 0
2026-03 | 2026-03-31 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Collected weekly compliance samples -Started batch wasting process at 09:45 to waste from 11:00-13:15 for 36.13m^3 into STT 1. Train 1(15.03m^3) & Train 2(21.10m^3), wasted more from train 2 to balance out solids. -Completed lab analysis station check , no issues found -Generator 2 being worked on by contractors -Added 9 bags of soda ash into hopper -Raked bar screen & dewatering press -Cleared rags from distribution inlet valve stem -Checked aeration inlet valve stems, no rags present -Switched effluent hose to aeration tank 2 outlet weir -Diesel generator 2 ran by contractors for 3.9 hrs -Diesel generator 1 being ran until approximately 16:30 -Completed biorem odour control unit inspection, no issues found -Turned WAS pumps 1&2 into manual off | FLAG | stage2_low_confidence | 0.041536 | ML: above threshold (no LLM available) — 0.042 | compliance [regulatory] | 0.041536 | 0 | 0
2026-03 | 2026-03-30 | Kleinburg Water Resource Recovery Facility | WW-WEST | Onsite for influent flow meter chamber inspection. Called ROC to inform of work being done. inspection completed - no issues found. No need to pump out. Activated plant 2 influent chamber float alarm - reset alarm. Reset thick'd sludge pmp 2 pres. switch hi alm with Harie - alarm now cleared. Set raw sampler to be ready for sample collection tommorow. | FLAG | stage2_low_confidence | 0.0092528 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0092528 | 0 | 0
2026-03 | 2026-03-11 | Kleinburg Water Resource Recovery Facility | WW-WEST | Switch aeration alum pumps to manual speed @ 46%. Filter inlet alum pump speed to 30% manual. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039682 | 0 | 0
2026-03 | 2026-03-03 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Supernated thickening tank 1 and transferred to holding tank -Completed lab analysis and station check , no issues found -Wasting process from 09:00-13:00, wasted 13.50m^3 from train 1 & 13.58m^3 from train 2 for a total of 27.08m^3 -Completed scum tank cleaning -Completed Biorem Odour Control Unit inspection , no issues found -Trend gap in SCADA data is present due to PAC issues from 11:27 -12:20 | FLAG | stage2_low_confidence | 0.02196 | ML: above threshold (no LLM available) — 0.022 | scada [control_system] | 0.02196 | 0 | 0
2026-03 | 2026-03-10 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed lab analysis & station check , no issues found -Started batch wasting process at 09:00 , wasting from 10:00-12:00 for 25.01m^3 -Added 10 bags of soda ash into hopper -Turned WAS pumps 1&2 to manuel off -All 3 scum pumps are in manuel due to high flows -Checked Raw Sewage & Final Composite Effluent Samplers , no issues found -Checked headworks heat traces , no issues found -Inspected Bioremediation Odour Control Unit , no issues found -WAS_MV2 valve is hand cranked fully closed | FLAG | stage2_low_confidence | 0.016168 | ML: above threshold (no LLM available) — 0.016 |  | 0.016168 | 0 | 0
2026-03 | 2026-03-15 | Kleinburg Water Resource Recovery Facility | WW-WEST | Remotely Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:50. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047811 | 0 | 0
2026-03 | 2026-03-12 | Kleinburg Water Resource Recovery Facility | WW-WEST | Remotely changed alum pumps 1, 3, 4 speed to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046513 | 0 | 0
2026-03 | 2026-03-11 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Collected weekly compliance samples -Started batch wasting process 10:00, wasting from 11:00-13:00 for 30.02m^3 -WAS_MV2 is now operational -Completed online DO probe maintenance -Completed sand filter hose down and performance check -Hosed down clarifier weirs | FLAG | stage2_low_confidence | 0.014569 | ML: above threshold (no LLM available) — 0.015 | compliance [regulatory] | 0.014569 | 0 | 0
2026-03 | 2026-03-12 | Kleinburg Water Resource Recovery Facility | WW-WEST | Completed labs and entered data in ace sheets. Added 9 bags soda ash to hopper. Enabled wasting timer at 9:57. Set auto wasting to waste 15 m3 from each train in 6 cycles between 11:00 and 13:00. Reset high temp alarm on sludge blower motor. Set scum pumps to auto. Cleared high level alarm on scum tank. Completed station check. No issues found. Corrected sand filter 2, cell one so its pulling sand again. | FLAG | stage2_low_confidence | 0.01173 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.01173 | 0 | 0
2026-03 | 2026-03-05 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Young Jung(OIC). -Completed lab analysis & station check , no issues found -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 26.01m^3 -Added 8 bags of soda ash into hopper -Received 400 bags of soda ash from 10:40-11:10 -Completed circular plant clarifier maintenance , did not run clarifier as bottom of the tank is frozen -Completed rectangular plant clarifier maintenance , no issues found except for having to adjust the shear pin slightly on clarifier 1 to avoid false over torque alarm -Completed scum tank 3 valve/actuator exercise -Thickening tank 2 LIT level trend does not correspond with the increases in level expected from the wasting process. The affected timeline is 11:00-14:39 , PCS will be notified and a CMU 4 will be created | FLAG | stage2_low_confidence | 0.066186 | ML: above threshold (no LLM available) — 0.066 | alarm [control_system] | 0.066186 | 0 | 0
2026-03 | 2026-03-07 | Kleinburg Water Resource Recovery Facility | WW-WEST | Remotely enabled batch wasting mode at 21:20 On site added 8 x 25kg bags of soda ash to auto dispenser hopper. Begin wasting and will continue WAS process remotely. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069132 | 0 | 0
2026-03 | 2026-03-03 | Kleinburg Water Resource Recovery Facility | WW-WEST | Completed the diesel generator runs Completed the jhsc inspection WAS_MV2 faulted and could not be reset W11702216 was created to address this | FLAG | stage2_low_confidence | 0.021583 | ML: above threshold (no LLM available) — 0.022 | fault [equipment_failure]; faulted [equipment_failure] | 0.021583 | 0 | 0
2026-03 | 2026-03-04 | Kleinburg Water Resource Recovery Facility | WW-WEST | Manually exercised aeration butterfly valves. Manually exercised distribution chamber butterfly valves. Inspected soda ash gear reducer. Changed oil and inspected vortex blowers. Changed oil and inspected diversion tank blowers. Inspected circular plant blowers. Completed 2 month maintenance on air compressors. | FLAG | stage2_low_confidence | 0.019115 | ML: above threshold (no LLM available) — 0.019 | sso [critical] | 0.019115 | 0 | 0
2026-03 | 2026-03-01 | Kleinburg Water Resource Recovery Facility | WW-WEST | - Received a call from ROC at 2:55 about a PAC3 communication failure alarm that occurred at 2:06. PCS on call was already notified and could not resolve issue remotely. Requested PCS on call, Yash Savaliya be dispatched to site - Looked through intelex procedure and followed protocol - Arrived on site at 3:33 and PCS on call arrived at roughly 3:38. Dialer alarm shows RTU failure in the headworks scada panel room. - No communication (PAC3) for sludge/scum loading, and sludge, and WAS pumps interlocked due to the failure. Aeration temperature value, aeration DO readings and aeration solids value are all affected since 1:51 until 2:47. Plant 2 influent readings is affected from 1:51 until 3:46 (gap in trend from 2:46 until 3:46) - PCS on call made repairs. Changed blown out fuse and reset breakers affecting FIT. Reset historian heartbeat alarm. Gap in trend from 4:19:37 until 4:19:47 - Reset alarms, pac4 to pac3 communication failure, pac3 communication alarm, KBSPSH pac communication failure, historian heartbeat alarm all cleared - Quickly addressed the issue and no local controls was needed to operate the plant - Once confirming proper operation. Left site at 4:23 | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; communication failure [control_system]; no communication [control_system] | failure [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; communication failure [control_system]; no communication [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed lab analysis & station check , no issues found -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 26.02m^3 -Added 12 bags of soda ash into hopper -Rotated RAS pumps, P1 for train 1 & P3 for train 2 -Completed scum tank cleaning -Supernated STT 1 and transferred to SHT -Turned WAS pumps 1&2 to manuel off -WAS_MV2 is hand cranked fully open | FLAG | stage2_low_confidence | 0.011045 | ML: above threshold (no LLM available) — 0.011 |  | 0.011045 | 0 | 0
2026-03 | 2026-03-10 | Kleinburg Water Resource Recovery Facility | WW-WEST | Remotely Responded to Scum Tank Level HiHi Alarm. Paced Scum Pumps #1 and 2 in Manual Off for the Duration of On-going High Flows Entering the Plant. Notified ROC and On-call Staff Member. | FLAG | stage2_low_confidence | 0.0095261 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0095261 | 0 | 0
2026-03 | 2026-03-06 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Completed lab analysis & station check , no issues found -Started batch wasting process at 09:00 , wasting from 10:00-12:00 for 26.02m^3 -Added 11 bags of soda ash into hopped -WAS_MV2 is hand cranked closed -Turned WAS pumps 1&2 into manuel off -Supernated thickening tank 2 and transferred to holding tank -Completed plant 2 WAS pumps 1-2 and check valve inspections , no issues found -Cleared bar screen and dewatering press of debris -Programmed final effluent composite sampler to start on March.8/2026 | FLAG | stage2_low_confidence | 0.017488 | ML: above threshold (no LLM available) — 0.017 |  | 0.017488 | 0 | 0
2026-03 | 2026-03-13 | Kleinburg Water Resource Recovery Facility | WW-WEST | Received load of alum. Reviewed and confirmed certificate of analysis. Filled tank from 0.76m to 3.45m. Inspected sludge, rectangular plant aeration, diversion and vortex blowers. No issues with any of the above. | FLAG | stage2_low_confidence | 0.013011 | ML: above threshold (no LLM available) — 0.013 |  | 0.013011 | 0 | 0
2026-03 | 2026-03-15 | Kleinburg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Topped Up Soda Ash Hopper ?> 16 Bags. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 15 m3 from Each Clarifier. Rotated Active Sludge Thickening Tank. WAS Valve #2 Manual Closed, WAS Valve #1 Manual Open. | FLAG | stage2_low_confidence | 0.010442 | ML: above threshold (no LLM available) — 0.01 |  | 0.010442 | 0 | 0
2026-03 | 2026-03-11 | Kleinburg Water Resource Recovery Facility | WW-WEST | Exercised ras and was valves for rectangular and circular plant. Inspected rectangular plant ras pumps. Inspected circular plant blowers. Inspected circular plant ras and was pumps. | FLAG | stage2_low_confidence | 0.014884 | ML: above threshold (no LLM available) — 0.015 |  | 0.014884 | 0 | 0
2026-03 | 2026-03-02 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Marcus Remonde(OIC). -Supernated thickening tank 2 and transferred to holding tank -Completed lab analysis and station check , no issues found. MLVSS was omitted , as oven temperature was too hot and melted samples -Added 12 bags of soda ash into the hopper -Started batch wasting process at 09:00 , wasting 30.02m^3 from 10:00 - 12:00 -Put WAS pumps 1&2 into manuel off -Completed RSHW BLO1 & BLO2 inspections , no issues found -Bled aeration condensation line.No condensate or liquid came out , only air was present -Completed aeration outlet weir rag cleaning -Cleaned bar screen/dewatering area | FLAG | stage2_low_confidence | 0.024269 | ML: above threshold (no LLM available) — 0.024 |  | 0.024269 | 0 | 0
2026-03 | 2026-03-16 | Kleinburg Water Resource Recovery Facility | WW-WEST | Hosed aeration tank outlets and weirs. | FLAG | stage2_low_confidence | 0.013326 | ML: above threshold (no LLM available) — 0.013 |  | 0.013326 | 0 | 0
2026-03 | 2026-03-27 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 30.03m^3. Train 1(15.07m^3) & Train 2(14.95m^3). -Wasted an additional 5.08m^3 from train 2 as solids are higher in aeration tank 2 -Put WAS pumps 1&2 into manuel off -Supernated STT 1 & transferred to SHT -Completed lab analysis and found that clarifier 1&2 has a slight spike of ammonia, 0.197mg/L & 0.177mg/L respectively. Final Effluent parameters are good. -Transferred sludge from STT 2 to SHT without supernating to make sure weekend wasting has space. Initial STT 2 level - 2.20m & Final STT 2 level-1.88m after transferring to SHT without supernating -Completed station check , no issues found -Removed rags from aeration inlet & distribution chamber inlet valve stems -Raked bar screen & dewatering press -Added 10 bags of soda ash into hopper -Turned off Effluent hose that was running in headworks building by the soda ash hopper | FLAG | stage2_low_confidence | 0.080384 | ML: above threshold (no LLM available) — 0.08 |  | 0.080384 | 0 | 0
2026-03 | 2026-03-16 | Kleinburg Water Resource Recovery Facility | WW-WEST | Onsite for daily PMs Decanted sludge thickening tank 2 and transferred remaining sludge to holding. Placed WAS pumps into Auto - Enabled batch wasting mode at 8:45am and set auto waste to waste 30m3 (15m3 each tank) from 10am to 12pm. WAS pumps placed back into manual upon wasting completion and RAS pumps placed back into operation. Rotated RAS pumps in operation from RAS pumps 1 and 3 to RAS pumps 2 and 4. Added 7 bags of soda ash to hopper. Ran helical skimmers in manual and Manually pumped down scum tank to clean scum tank. Scum pump placed back into auto and skimmers also placed back into auto upon completion. Barscreen cleared of rags and confirmed operation. Distribution valve cleared of rags. Completed daily lab and Completed station check - no new issues added data into SharePoint | FLAG | stage2_low_confidence | 0.015704 | ML: above threshold (no LLM available) — 0.016 |  | 0.015704 | 0 | 0
2026-03 | 2026-03-16 | Kleinburg Water Resource Recovery Facility | WW-WEST | On site to assist contractor Total Power with diesel generator 1 maintenance and load test. Informed ROC of generator work. Completed work on generator 1. | FLAG | stage2_low_confidence | 0.01598 | ML: above threshold (no LLM available) — 0.016 |  | 0.01598 | 0 | 0
2026-03 | 2026-03-17 | Kleinburg Water Resource Recovery Facility | WW-WEST | Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:53. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Autowasting wasted 13 m3 from train 1 and 17 m3 from train 2. Added 10 bags to soda ash hopper. Inspected odour control machine. Adjusted pressure regulating valve to get 30 psi on the irrigation line pressure. Completed housekeeping in blower building. Cleaned aeration channel and bled condensation. | FLAG | stage2_low_confidence | 0.016365 | ML: above threshold (no LLM available) — 0.016 |  | 0.016365 | 0 | 0
2026-03 | 2026-03-18 | Kleinburg Water Resource Recovery Facility | WW-WEST | Collected weekly compliance samples. Lowered supernate tube on sludge tank 1. | FLAG | stage2_low_confidence | 0.015328 | ML: above threshold (no LLM available) — 0.015 | compliance [regulatory] | 0.015328 | 0 | 0
2026-03 | 2026-03-19 | Kleinburg Water Resource Recovery Facility | WW-WEST | On site with total lift for annual inspecttions | FLAG | stage2_low_confidence | 0.012772 | ML: above threshold (no LLM available) — 0.013 |  | 0.012772 | 0 | 0
2026-03 | 2026-03-23 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Turned RAS pumps 2&4 into manuel off -Turned RAS pumps 1&3 into auto -Started batch wasting process at 09:00 , wasting from 10:00-12:00 for 30.02m^3 -Completed lab analysis & station check , no issues found -Turned WAS pumps 1&2 into manuel off -Supernated STT 1 and transferred to SHT -Added 9 bags of soda ash into hopper -Raked bar screen and dewatering press -Completed scum tank cleaning -Completed aeration outlet weir cleaning -Bled out aeration condensation line , no condensate was found | FLAG | stage2_low_confidence | 0.011653 | ML: above threshold (no LLM available) — 0.012 |  | 0.011653 | 0 | 0
2026-03 | 2026-03-17 | Kleinburg Water Resource Recovery Facility | WW-WEST | On site to assist contractor Total Power with Diesel Generator #2 PM. | FLAG | stage2_low_confidence | 0.010782 | ML: above threshold (no LLM available) — 0.011 |  | 0.010782 | 0 | 0
2026-03 | 2026-03-26 | Kleinburg Water Resource Recovery Facility | WW-WEST | Shut off Bertha/Generator 2 for contractors. Completed labs and entered data in ACE sheets. Completed station check. No issues found. Added 9 bags to soda ash hopper. Enabled was timer at 8:51. Set auto-wasting for 30 m3 total between 11:00 and 13:00 in 6 cycles. Wasted a bonus 5 m3 from train 2. Shut effluent water to headworks off for maintenance work order. Wasted an extra 5 m3 from tank 2 at 13:05. Verified correct dip switch positions for uv channel 1 bank 2, rack 2. They are in the correct positions. Turned water back on in headworks after pipe repaired. Turned generator 2 back to auto. | FLAG | stage2_low_confidence | 0.027243 | ML: above threshold (no LLM available) — 0.027 | work order [maintenance_action]; repair [maintenance_action] | 0.027243 | 0 | 0
2026-03 | 2026-03-20 | Kleinburg Water Resource Recovery Facility | WW-WEST | Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:11. Set autowasting for 10 m3 per train in 2 cycles each between 10:00 and 11:00. Added 10 bags to soda ash hopper. Cleaned out UV channel. | FLAG | stage2_low_confidence | 0.0091437 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091437 | 0 | 0
2026-03 | 2026-03-16 | Kleinburg Water Resource Recovery Facility | WW-WEST | Did housekeeping. | FLAG | stage2_low_confidence | 0.011904 | ML: above threshold (no LLM available) — 0.012 |  | 0.011904 | 0 | 0
2026-03 | 2026-03-22 | Kleinburg Water Resource Recovery Facility | WW-WEST | Added 17 bags to soda ash hopper. Raked inside bar screen. Picked rags from valve stems. Confirmed auto-wasting under way. | FLAG | stage2_low_confidence | 0.0086425 | ML: above threshold (no LLM available) — 0.009 |  | 0.0086425 | 0 | 0
2026-03 | 2026-03-25 | Kleinburg Water Resource Recovery Facility | WW-WEST | Cleaned and verified DO probes. | FLAG | stage2_low_confidence | 0.012755 | ML: above threshold (no LLM available) — 0.013 |  | 0.012755 | 0 | 0
2026-03 | 2026-03-22 | Kleinburg Water Resource Recovery Facility | WW-WEST | Enabled 200 min was timer. Set autowasting for 30 m3 total between 10:00 and 12:00. Set was pumps to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035101 | 0 | 0
2026-03 | 2026-03-19 | Kleinburg Water Resource Recovery Facility | WW-WEST | Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 08:55. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Added 9 bags to soda ash hopper. | FLAG | stage2_low_confidence | 0.0097581 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097581 | 0 | 0
2026-03 | 2026-03-19 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Turned WAS pumps 1&2 into manuel off -Completed aeration building housekeeping -Completed odour control building & sludge blower room housekeeping | FLAG | stage2_low_confidence | 0.011458 | ML: above threshold (no LLM available) — 0.011 |  | 0.011458 | 0 | 0
2026-03 | 2026-03-25 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Collected weekly compliance samples -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 30.01 m^3. Train 1 (15.04m^3) & Train 2 (14.97m^3) -Added 9 bags of soda ash into hopper -Completed lab analysis & station check , no issues found -Turned WAS pumps 1&2 into manuel off -Raked bar screen & dewatering press -Swept sludge handling building | FLAG | stage2_low_confidence | 0.019408 | ML: above threshold (no LLM available) — 0.019 | compliance [regulatory] | 0.019408 | 0 | 0
2026-03 | 2026-03-24 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Started batch wasting process at 08:40 , wasting from 10:00-12:00 for 26.05 m^3. Train 1 (12.98m^3) & Train 2 (13.07m^3) -Added 8 bags of soda ash into hopper -Completed lab analysis & station check , no issues found -Turned WAS pumps 1&2 into manuel off -Raked bar screen & dewatering press -Cleaned rags off of aeration inlet valve stems & distribution tank valve stem -Swept & mopped circular plant MCC room & washroom -Completed biorem odour control unit inspection , no issues found -Completed filter bypass float alarm test , no issues found and verified with ROC that alarm came through | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system] | bypass [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | Kleinburg Water Resource Recovery Facility | WW-WEST | On site to assist contractor Total Power with diesel generator #2 load test. Completed | FLAG | stage2_low_confidence | 0.011667 | ML: above threshold (no LLM available) — 0.012 |  | 0.011667 | 0 | 0
2026-03 | 2026-03-18 | Kleinburg Water Resource Recovery Facility | WW-WEST | Supernated STT and released to SHT. Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:49. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Autowasting volumes are correct with waste pumps in auto speed. Added 8 bags to soda ash hopper. Completed housekeeping work order for headworks building. Completed DO probe maintenance. Created work order (W11744156) for service water pipe in need of re-securing to wall in headworks. | FLAG | stage2_low_confidence | 0.026213 | ML: above threshold (no LLM available) — 0.026 | work order [maintenance_action] | 0.026213 | 0 | 1
2026-03 | 2026-03-16 | Kleinburg Water Resource Recovery Facility | WW-WEST | Checked in with David Dougherty and diesel mechanics. Cleaned and hosed aeration outlets. | FLAG | stage2_low_confidence | 0.013893 | ML: above threshold (no LLM available) — 0.014 |  | 0.013893 | 0 | 0
2026-03 | 2026-03-31 | King City Pumping Station | WW-WEST | Onsite for station check - no new issues, reviewed trends and added data into sharepoint. flushed barscreen and auger, bar screen room okay. | FLAG | stage2_low_confidence | 0.01479 | ML: above threshold (no LLM available) — 0.015 |  | 0.01479 | 0 | 0
2026-03 | 2026-03-04 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Collected weekly compliance samples -Completed lab analysis and station check , ammonium was spiked for two composite final effluent samples for 0.181 mg/L & 0.192 mg/L . Final grab was tested for ammonium verification for 0.174 mg/L. -Aeration tank 2 inlet was clogged up with rags, upon removal of rags tank 2 DO has dropped back to regular levels. -Wasting was not done to regulate solids due to ammonium spike , clogged up aeration tank 2 inlet and DO spike. -Completed tertiary and headworks sump inspections , verified pumps, tipped floats and verified with ROC of alarms. -No hazardous waste present for collection and removal -Added 8 bags of soda ash into hopper -Completed online DO probe maintenance | FLAG | stage2_low_confidence | 0.25706 | ML: above threshold (no LLM available) — 0.257 | compliance [regulatory]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure]; hazard [safety] | 0.25706 | 0 | 0
2026-03 | 2026-03-02 | Kleinburg Water Resource Recovery Facility | WW-WEST | In to Investigate UV Channel #1 Low Intensity Alarm and Potential Burnt Out Bulb. Placed Channel Inlet Valve in Local Off and UV Bank A in Local On for Testing Purposes. No Issues Found. UVI Sensor for Channel #2, Bank A Not Functioning Properly. Rotated Bank Lead/Lag Priority. Bank B in Lead Position. Outstanding Intensity Alarms Cleared. Will Conduct Investigation of UVI Sensor at Next Earliest Convenience. | FLAG | stage2_low_confidence | 0.055619 | ML: above threshold (no LLM available) — 0.056 | burnt out [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.055619 | 0 | 0
2026-03 | 2026-03-11 | Kleinburg Water Resource Recovery Facility | WW-WEST | On site with Technician from Rotork to try and repair WAS FV2 actuator. Actuator is repaired. Back in remote operation. | FLAG | stage2_low_confidence | 0.024297 | ML: above threshold (no LLM available) — 0.024 | repair [maintenance_action] | 0.024297 | 0 | 0
2026-03 | 2026-03-07 | Kleinburg Water Resource Recovery Facility | WW-WEST | Wasted 12.5m3 per side for a total of 25m3. Reset batch wasting mode. RAS pumps back into auto and running. Scum tank in hi level - notify ROC to disregard as sludge holding tank is too high to pump scum. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004513 | 0 | 0
2026-03 | 2026-03-09 | Kleinburg Water Resource Recovery Facility | WW-WEST | In to Provide Assistance with FE and Raw Composite Sampler Inspections and Programming. Returned All to Service. | FLAG | stage2_low_confidence | 0.018507 | ML: above threshold (no LLM available) — 0.019 |  | 0.018507 | 0 | 0
2026-03 | 2026-03-13 | Kleinburg Water Resource Recovery Facility | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Supernated STT 1 and transferred to SHT -Completed consolidated headworks inspection -Added 10 bags of soda ash into hopper -Started batch wasting process at 10:00 , wasting from 11:00 - 13:00 for 26.01 m^3 into STT 2 -Turned WAS pumps 1&2 into manuel off | FLAG | stage2_low_confidence | 0.011044 | ML: above threshold (no LLM available) — 0.011 |  | 0.011044 | 0 | 0
2026-03 | 2026-03-19 | Kleinburg Water Resource Recovery Facility | WW-WEST | Returned ?Bertha? to auto. | FLAG | stage2_low_confidence | 0.012429 | ML: above threshold (no LLM available) — 0.012 |  | 0.012429 | 0 | 0
2026-03 | 2026-03-13 | King City Pumping Station | WW-WEST | Station checks, SharePoint readings and review of continuous monitoring data. Cycled and cleaned screen room equipment. Site walkthrough. | FLAG | stage2_low_confidence | 0.010064 | ML: above threshold (no LLM available) — 0.01 |  | 0.010064 | 0 | 0
2026-03 | 2026-03-11 | King City Pumping Station | WW-WEST | Check leaking backflow preventer leaking | FLAG | stage2_low_confidence | 0.020853 | ML: above threshold (no LLM available) — 0.021 | leak [infrastructure]; leaking [infrastructure] | 0.020853 | 0 | 0
2026-03 | 2026-03-10 | King City Pumping Station | WW-WEST | Onsite for station check- no new issues. Reviewed trends and added data into SharePoint. Barscreen okay - flushed and checked oil levels. Checked overflow sample kit. - no issues. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure] | overflow [critical]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-02 | King City Pumping Station | WW-WEST | On site to let King Township in to replace water meter. Successfully replaced the water meter with no issues | FLAG | stage2_low_confidence | 0.017049 | ML: above threshold (no LLM available) — 0.017 |  | 0.017049 | 0 | 0
2026-03 | 2026-03-05 | King City Pumping Station | WW-WEST | Onsite to assist with wet well cleaning and assisted with work orders. | FLAG | stage2_low_confidence | 0.025506 | ML: above threshold (no LLM available) — 0.026 | work order [maintenance_action] | 0.025506 | 0 | 0
2026-03 | 2026-03-03 | King City Pumping Station | WW-WEST | Onsite for station check - reviewed trends and added data into SharePoint. Found service water backflow preventer leaking. Created work order. | FLAG | stage2_low_confidence | 0.042176 | ML: above threshold (no LLM available) — 0.042 | work order [maintenance_action]; leak [infrastructure]; leaking [infrastructure] | 0.042176 | 0 | 0
2026-03 | 2026-03-19 | King City Pumping Station | WW-WEST | Onsite to push Barscreen rag bin out. Bin out and ready for pick up | FLAG | stage2_low_confidence | 0.010596 | ML: above threshold (no LLM available) — 0.011 |  | 0.010596 | 0 | 0
2026-03 | 2026-03-20 | King City Pumping Station | WW-WEST | Onsite for for station check - no new issues. Reviewed trends and added data into SharePoint. Barscreen okay - flushed and pushed empty bin back in | FLAG | stage2_low_confidence | 0.015206 | ML: above threshold (no LLM available) — 0.015 |  | 0.015206 | 0 | 0
2026-03 | 2026-03-20 | King City Pumping Station | WW-WEST | On site for pump vibration test. Rotated 2 and 3. Pump1 is OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; vibration [equipment_failure] | oos [equipment_failure]; vibration [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-16 | King City Pumping Station | WW-WEST | Remotely Responded to Pump #3 Fault Communicated by the ROC. Rotated RS Pump Duties. RS Pump #3 Manual Off, Duty #4/OOS. RS Pump #1 in Auto, Duty #2. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure] | fault [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-27 | King City Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data to SharePoint. Flushed and checked Barscreen - no issues oil levels good | FLAG | stage2_low_confidence | 0.014957 | ML: above threshold (no LLM available) — 0.015 |  | 0.014957 | 0 | 0
2026-03 | 2026-03-16 | King City Pumping Station | WW-WEST | Reset pump 3 fault. Tested. Works well. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-23 | King City Pumping Station | WW-WEST | On site for annual generator PM and load test | FLAG | stage2_low_confidence | 0.012716 | ML: above threshold (no LLM available) — 0.013 |  | 0.012716 | 0 | 0
2026-03 | 2026-03-17 | King City Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Barscreen flushed and oil levels ok. | FLAG | stage2_low_confidence | 0.013741 | ML: above threshold (no LLM available) — 0.014 |  | 0.013741 | 0 | 0
2026-03 | 2026-03-30 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | On site to check the raw composite sampling schedule. all okay and good for sampling tomorrow | FLAG | stage2_low_confidence | 0.01588 | ML: above threshold (no LLM available) — 0.016 |  | 0.01588 | 0 | 0
2026-03 | 2026-03-03 | King City Pumping Station | WW-WEST | Onsite for station check - no new issues reviewed trends and entered data into SharePoint. | FLAG | stage2_low_confidence | 0.01671 | ML: above threshold (no LLM available) — 0.017 |  | 0.01671 | 0 | 0
2026-03 | 2026-03-11 | King City Pumping Station | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Placed Pumps #1 and 3 in Manual On for Wet Well Level Drawdown. Drawdown Complete, Placed Pumps in Manual Off. Transferred Station to Generator Power with No Issues. Acknowledged and Cleared Associated Alarms. Returned Pump #1 to Auto, Duty #2. Placed Pumps #3 in Manual On for Wet Well Level Drawdown. Drawdown Complete, Placed Pump in Manual Off. Completed JHSC Inspection with No Issues. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. | FLAG | stage2_low_confidence | 0.028903 | ML: above threshold (no LLM available) — 0.029 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.028903 | 0 | 0
2026-03 | 2026-03-05 | King City Pumping Station | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Contractor On-site for Wet Well Cleaning. Completed Drawdown and Isolation Procedures as Necessary. Completed Hi/Lo Temp., Dry Well Flood and Diesel Containment Flood Alarm Tests. Confirmed Reception by the ROC. Returned to Service and Cleared Associated Alarms. Completed Dry Well Manual Valve Exercises, Overhead Hoist and Sump System Inspections with No Issues. Returned to Service. Wet Well Cleaning Complete. Returned Station to Service. Cleared Associated Alarms. Completed Consolidated Screen Room Inspections and Maintenance with No Issues. Returned to Service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; alarm [control_system]; alarms [control_system]; containment [safety] | sso [critical]; flood [critical]; alarm [control_system]; alarms [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-06 | King City Pumping Station | WW-WEST | Onsite for station check - no new issues, reviewed trends and added data into SharePoint. Rotated duty pumps. Barscreen room good - flushed bar screen screw | FLAG | stage2_low_confidence | 0.011059 | ML: above threshold (no LLM available) — 0.011 |  | 0.011059 | 0 | 0
2026-03 | 2026-03-25 | King City Pumping Station | WW-WEST | Reset pump 3, which tripped breaker when power transferred to generator. Loss of power due to planned power outage. Reviewed generator parameters. All okay at this time. Set pump 3 to auto/duty 4/oos and pump 2 auto/duty 2. Pump 1 running in duty 1. Reset SCADA alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | King City Pumping Station | WW-WEST | In to Complete Scheduled WOs. Rotated Pump Duties. Pump #2 Manual Off, Duty #4/OOS. RS Pump #1 in Auto, Duty #2. Reviewed SCADA and Trends. No Issues Found. Levelled Bin. Inspected and Tidied HWs. Topped Up Bar-screen Oil Hopper. No Issues Found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Onsite for pump 1 and pump 2 ultrasonic backup mode alarms. Wetwell hi hi level alarm and wetwell overflow alarm due to hi level. Wetwell in backup mode and high levels due to rain event. Upon arrival onsite both pumps 2 and 3 running in backup mode with wetwell at 4.20m. Wet well level slowly coming back down as rain event finishes. Wetwell did not exceed 4.30m. No overflow occurred. Checked wetwell manually to confirm. Placed pump 1 and pump 3 in manual to try to rotate pumps to place pump 1 in duty and pump 3 in off. Due to an energy limit in the coding and being in backup mode pump 1 failed to start and pump 3 failed to stop. Will continue to monitor as wetwell level comes back down | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; failed [equipment_failure]; alarm [control_system]; alarms [control_system]; overflow [infrastructure]; backup [infrastructure] | overflow [critical]; failed [equipment_failure]; alarm [control_system]; alarms [control_system]; overflow [infrastructure]; backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-31 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | - Checked station and recorded readings on SharePoint. No new issues - Collected weekly regulatory samples | FLAG | stage2_low_confidence | 0.022218 | ML: above threshold (no LLM available) — 0.022 | regulatory [regulatory] | 0.022218 | 0 | 0
2026-03 | 2026-03-31 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Dropped off Kleinburg WRRF weekly compliance samples -Created contingency entry due to EZmax mobile error. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) | compliance [regulatory] |  | 0 | 1
2026-03 | 2026-03-04 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Dropped off Kleinburg weekly compliance samples | FLAG | stage2_low_confidence | 0.020652 | ML: above threshold (no LLM available) — 0.021 | compliance [regulatory] | 0.020652 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Relieve Young Jung from site. Wessuc completed sewer cleaning and camera inspection. Change pump duty 1 and 2 start and stop set points to their original and normal operating ranges. Duty 1: start @ 1.4m, Stop @0.90m Duty 2: start @ 1.7m, Stop @ 1.10m Enabled low level lockout and review local scada. All pumps returned to auto speed. | FLAG | stage2_low_confidence | 0.011789 | ML: above threshold (no LLM available) — 0.012 | scada [control_system] | 0.011789 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Collected regulatory samples | FLAG | stage2_low_confidence | 0.01928 | ML: above threshold (no LLM available) — 0.019 | regulatory [regulatory] | 0.01928 | 0 | 0
2026-03 | 2026-03-13 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | In to Complete Scheduled WOs. Reviewed SCADA and Trends. No Issues Found. Completed Overflow Kit Inspection and Refill. No Issues Found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; scada [control_system]; overflow [infrastructure] | overflow [critical]; scada [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-06 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Once Wessuc was done with sewer line cleaning and wet well cleaning. Placed pumps 1 and 2 to auto speed. Placed pump 3 back into pump rotation as duty 3. Changed pump duty rotation from all stop to timed. Changed wet well duty 1 start from 1 m to 1.4 m. Duty 1 stop from 0.75 m to 0.9 m. Changed wet well duty 2 start from 1.3 m to 1.7 m. Kept duty 2 stop the same at 1.1 m Reenabled low level lockout Checked dry well once again and confirmed normal plant operation | FLAG | stage2_low_confidence | 0.017943 | ML: above threshold (no LLM available) — 0.018 |  | 0.017943 | 0 | 0
2026-03 | 2026-03-10 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Checked station and recorded readings on SharePoint. No new issues Inspected raw sampler. No issues | FLAG | stage2_low_confidence | 0.012113 | ML: above threshold (no LLM available) — 0.012 |  | 0.012113 | 0 | 0
2026-03 | 2026-03-11 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Dropped off Kleinburg WRRF weekly compliance samples | FLAG | stage2_low_confidence | 0.021138 | ML: above threshold (no LLM available) — 0.021 | compliance [regulatory] | 0.021138 | 0 | 0
2026-03 | 2026-03-09 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | On site to meet Wessuc to finish up sewer line cleaning. Notified ROC of the work being performed Disabled low level lock out to bring the wet well down to operate at a lower pump start and stop cycle. Currently hydrostatic is controlling. Placed pump 2 to duty 1, pump 1 to duty 2, and pump 3 to duty 4. Changed wet well duty 1 start from 1.4 m to 0.9 m. Duty 1 stop from 0.9 m to 0.63 m Changed wet well duty 2 start from 1.7 m to 1.3 m. Kept stop at the same level at 1.10 m. Pumped down wet well using pump 1 at manual 100% speed. Once wet well level went down to 0.63 m and pumps shut off. Changed pump duty rotation to all stop and to rotate between pump 1 and 2. Placed pump 3 into duty 4. Placed pump 1 and pump 2 to manual speed 85%. Will monitor and adjust pump speed as needed depending on incoming flows | FLAG | stage2_low_confidence | 0.043699 | ML: above threshold (no LLM available) — 0.044 |  | 0.043699 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | On site to meet Wessuc for sewer line cleaning. Notified ROC of the work being performed Disabled low level lock out to bring the wet well down to operate at a lower pump start and stop cycle. Currently hydrostatic is controlling. Placed pump 2 to duty 1, pump 1 to duty 2, and pump 3 to duty 4. Changed wet well duty 1 start from 1.4 m to 1.00 m. Duty 1 stop from 0.9 m to 0.74 m Changed wet well duty 2 start from 1.7 m to 1.3 m. Kept stop at the same level at 1.10 m. Pumped down wet well using pump 1 at manual 100% speed and pump 2 in auto speed. Once wet well level went down to 0.8 and pumps shut off. Changed pump duty rotation to all stop and to rotate between pump 1 and 2. Placed pump 3 into duty 4. Will monitor and adjust pump speed as needed depending on incoming flows | FLAG | stage2_low_confidence | 0.026613 | ML: above threshold (no LLM available) — 0.027 |  | 0.026613 | 0 | 0
2026-03 | 2026-03-03 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | - Checked station and recorded readings on SharePoint. No new issues - Notified ROC of the work being performed - Inspected the generator and fuel level, all okay. Started the generator at 10:56. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 456:57:00 hrs to 458:00:00 hrs. Fuel level from 76 cm (1496 L) to 76 cm (1494 L). Past trend shows LIT for fuel level bouncing around. Will monitor and create a work order if it occurs again - Performed JHSC inspection. Tested eyewash. No issues found | FLAG | stage2_low_confidence | 0.093431 | ML: above threshold (no LLM available) — 0.093 | work order [maintenance_action] | 0.093431 | 0 | 0
2026-03 | 2026-03-27 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Checked station and recorded readings on SharePoint. No new issues | FLAG | stage2_low_confidence | 0.014988 | ML: above threshold (no LLM available) — 0.015 |  | 0.014988 | 0 | 0
2026-03 | 2026-03-23 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Worked on valve exercise and comprehensive housekeeping work orders. | FLAG | stage2_low_confidence | 0.025152 | ML: above threshold (no LLM available) — 0.025 | work order [maintenance_action] | 0.025152 | 0 | 0
2026-03 | 2026-03-20 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | On site for vibration. Rotated all 3 pumps | FLAG | stage2_low_confidence | 0.017458 | ML: above threshold (no LLM available) — 0.017 | vibration [equipment_failure] | 0.017458 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Dropped off Kleinburg WRRF weekly compliance samples | FLAG | stage2_low_confidence | 0.021436 | ML: above threshold (no LLM available) — 0.021 | compliance [regulatory] | 0.021436 | 0 | 0
2026-03 | 2026-03-16 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | In to Investigate Pump #1 VFD Fault Communicated by the ROC. Pump #1 Overcurrent Fault Outstanding. No Other Issues Observed. Reset Fault Locally and Via SCADA. Returned Pump to Duty. | FLAG | stage2_low_confidence | 0.028266 | ML: above threshold (no LLM available) — 0.028 | fault [equipment_failure]; scada [control_system] | 0.028266 | 0 | 0
2026-03 | 2026-03-23 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Completed comprehensive housekeeping and valve exercise work orders. | FLAG | stage2_low_confidence | 0.025141 | ML: above threshold (no LLM available) — 0.025 | work order [maintenance_action] | 0.025141 | 0 | 0
2026-03 | 2026-03-24 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Checked station and recorded readings on SharePoint. No new issues | FLAG | stage2_low_confidence | 0.014988 | ML: above threshold (no LLM available) — 0.015 |  | 0.014988 | 0 | 0
2026-03 | 2026-03-20 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Checked station and trends, and recorded readings on SharePoint | FLAG | stage2_low_confidence | 0.014745 | ML: above threshold (no LLM available) — 0.015 |  | 0.014745 | 0 | 0
2026-03 | 2026-03-17 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Checked station and trends. No new issues | FLAG | stage2_low_confidence | 0.013306 | ML: above threshold (no LLM available) — 0.013 |  | 0.013306 | 0 | 0
2026-03 | 2026-03-25 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | On site to collect weekly regulatory samples. No issues | FLAG | stage2_low_confidence | 0.020509 | ML: above threshold (no LLM available) — 0.021 | regulatory [regulatory] | 0.020509 | 0 | 0
2026-03 | 2026-03-18 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Collected weekly regulatory samples | FLAG | stage2_low_confidence | 0.019929 | ML: above threshold (no LLM available) — 0.02 | regulatory [regulatory] | 0.019929 | 0 | 0
2026-03 | 2026-03-31 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint | FLAG | stage2_low_confidence | 0.016581 | ML: above threshold (no LLM available) — 0.017 |  | 0.016581 | 0 | 0
2026-03 | 2026-03-04 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Collected regulatory samples | FLAG | stage2_low_confidence | 0.01928 | ML: above threshold (no LLM available) — 0.019 | regulatory [regulatory] | 0.01928 | 0 | 0
2026-03 | 2026-03-06 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | - Inspected the hoist system. No issues - Inspected pump 1-3, motor and check valve. No issues found - Flushed air relief valve. All okay - Tested dry well flood alarm. Alarm received on dialer and SCADA as sewage station flood alarm - Tested building how and low temperature alarm. Alarm received - Tested sump pump. Both sump pumps run on hand control and by float. No issues - Checked station and recorded readings on SharePoint. No new issues | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system] | flood [critical]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. | FLAG | stage2_low_confidence | 0.016654 | ML: above threshold (no LLM available) — 0.017 |  | 0.016654 | 0 | 0
2026-03 | 2026-03-03 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check - no new issues reviewed trends and added data into SharePoint. | FLAG | stage2_low_confidence | 0.016581 | ML: above threshold (no LLM available) — 0.017 |  | 0.016581 | 0 | 0
2026-03 | 2026-03-23 | Vaughan Pine Valley Pumping Station | WW-WEST | On site for odour control PM. Completed | FLAG | stage2_low_confidence | 0.012409 | ML: above threshold (no LLM available) — 0.012 |  | 0.012409 | 0 | 0
2026-03 | 2026-03-17 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Checked overflow spill kit and checked expiration date. No issues found. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; spill [critical]; overflow [infrastructure] | overflow [critical]; spill [critical]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-20 | Vaughan Pine Valley Pumping Station | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Reviewed SCADA and Trends. Identified Discrepancy Between Hydrostatic and Ultrasonic LITs. Notified TL for Future Corrective Action. Duty Pumps Cycling Without Issue Despite. Transferred Station to Generator Power with No Issues. Acknowledged Associated Alarms. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. Completed Generator Exhaust Stack Condensate Draining with No Issues. Completed Consolidated Dry Well Inspections. Confirmed Reception of Associated Alarms with ROC. Returned to Service and Cleared Associated Alarms. Completed JHSC and Hazardous Waste Inspections. Identified Degrading of Station External Roof Material and Notified TL and West WW-Staff. No Other Issues Found. Completed Odour Control Scrubber System Inspection. Belt and Media OK. Exercised Manual Isolation Valve and Greased Bearings. Identified Burnt Out Intrinsically Safe Bulb within Odour Control Room. Notified TL for Replacement. | FLAG | stage2_low_confidence | 0.36149 | ML: above threshold (no LLM available) — 0.361 | sso [critical]; burnt out [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] | 0.36149 | 0 | 0
2026-03 | 2026-03-27 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Odour control unit room okay. | FLAG | stage2_low_confidence | 0.013327 | ML: above threshold (no LLM available) — 0.013 |  | 0.013327 | 0 | 0
2026-03 | 2026-03-06 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check and manual valve exercise PM Station check ok. No new issues. Reviewed trends and added data into SharePoint. Completed manual valve exercise WO. When doing the manual valve exercise WO. pumps 2 and 3 were placed into manual off with pump 1 in auto. Pump 1 kicked on in ultrasonic mode at 100% and interlocked causing alarm. When pumps 2 and 3 placed back into auto pump 1 interlock caused pump 2 to come on causing discharge flow hihi alarm. Placed pump 1 into local off to stop pump. Pump 1 back up mode most likely triggered due to wrong duty rotation. Placed pump 1 back into remote on cleared alarms and placed back into duty 1 with pumps 2 and 3 in auto. Pump 1 was called for as normal operation, and ran normally for multiple cycles. Will continue to monitor in case of sensor issue or PAC issue. | FLAG | stage2_low_confidence | 0.039924 | ML: above threshold (no LLM available) — 0.04 | alarm [control_system]; alarms [control_system] | 0.039924 | 0 | 0
2026-03 | 2026-03-10 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check - no new issues reviewed trends and added data into SharePoint. | FLAG | stage2_low_confidence | 0.016581 | ML: above threshold (no LLM available) — 0.017 |  | 0.016581 | 0 | 0
2026-03 | 2026-03-24 | Vaughan Pine Valley Pumping Station | WW-WEST | In to Drop Off Oil Storage Skid for Station. | FLAG | stage2_low_confidence | 0.013492 | ML: above threshold (no LLM available) — 0.013 |  | 0.013492 | 0 | 0
2026-03 | 2026-03-23 | Vaughan Pine Valley Pumping Station | WW-WEST | In to Complete Scheduled WO. Notified ROC. Placed LITs #2 and 4 in Calibration Mode Independently and Sequentially. Completed Wet Well Inspection and Flushing. Greased Channel Grinder. Inspected and Flushed Hydrostatic LIT Sensor Lines and Heads. Returned to Service. Cleared Associated Interlocks and Alarms. | FLAG | stage2_low_confidence | 0.046917 | ML: above threshold (no LLM available) — 0.047 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.046917 | 0 | 0
2026-03 | 2026-03-24 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check and housekeeping PM Station check ok - no new issues. Reviewed trends and added data into SharePoint. Swept main room and bathroom. | FLAG | stage2_low_confidence | 0.01095 | ML: above threshold (no LLM available) — 0.011 |  | 0.01095 | 0 | 0
2026-03 | 2026-03-30 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Auto batch wasted from clarifier 2 over the weekend: Friday: 48m3 Saturday: 47m3 Sunday 49m3 Everything operating as intended | FLAG | stage2_low_confidence | 0.0078544 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078544 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Water Resource Recovery Facility | WW-WEST | Received alum delivery. Reviewed and signed bill of lading and certificate of analysis. Filled tanks from 0.882m/0.872m to 2.586m/2.592m. Collected weekly compliance samples. Started in-house labs. | FLAG | stage2_low_confidence | 0.015377 | ML: above threshold (no LLM available) — 0.015 | compliance [regulatory] | 0.015377 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed labs and entered data in ace sheets. Completed station check. No issues found. Set ras P1 to manual on at 50% speed to help ras P2, which is duty 1, meet flow requirements. | FLAG | stage2_low_confidence | 0.013655 | ML: above threshold (no LLM available) — 0.014 |  | 0.013655 | 0 | 0
2026-03 | 2026-03-06 | Schomberg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. WAS Pump #1 Auto-Wasted 46 m3 Overnight. Lowered and Activated Decant Pump. Completed Sludge Blower Building Room Supply Fan Filter Replacement with No Issues. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Inspected Alum Dosage Points, Pump Function and Trends. Inspected Sand Filter Function. All OK. Adjusted Clarifier Eff. Alum Dosage Set-point Based On In-House and External Laboratory Results: 20 ?> 23 mg/L. Completed Compressors #1 and 2 Inspections. Tested Low Oil Level Alarms. Confirmed Reception by the ROC. Identified Slow Inlet Leak on Compressor #2 and Condensation Leak on Compressor #1 Air Dryer. Notified Appropriate Staff of Potential Deficiencies. No Other Issues Found. Cleared Associated Alarms. | FLAG | stage2_low_confidence | 0.14724 | ML: above threshold (no LLM available) — 0.147 | sso [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.14724 | 0 | 0
2026-03 | 2026-03-10 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed labs and entered data in ace sheet. Completed station check. No issues found. Adjusted aeration alum dosage from 115 mg/l to 110 mg/l to account for high volumes of melt-water. Set RAS P3 in manual on at 60% speed. RAS P2 is running auto speed in duty 1. This will help meet higher RAS flow requirements. Exercised SHT overflow valve. Tested SHT high level float. Inspected PB sump system. Inspected BB sump system. ROC received high level alarms from all three floats. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-13 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Decanted the sludge thickening tank Batch wasted 43m3 from clarifier 2 overnight | FLAG | stage2_low_confidence | 0.010079 | ML: above threshold (no LLM available) — 0.01 |  | 0.010079 | 0 | 0
2026-03 | 2026-03-12 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Was pump 1 wasted 46m3 from clarifier 2 RAS pump 2 kept getting a speed deviation alarm and was running loud Tried some troubleshooting but could not get it running properly, placed it in manual for the night until I can open it up Greased and inspected RAS, WAS and scum pumps Placed RAS pumps 1 and 3 in duty 1 to hit the desired flow rate | FLAG | stage2_low_confidence | 0.022194 | ML: above threshold (no LLM available) — 0.022 | alarm [control_system] | 0.022194 | 0 | 0
2026-03 | 2026-03-03 | Schomberg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. WAS Pump #1 Auto-Wasted 49 m3 Overnight. Lowered and Activated Decant Pump. Pulled and Cleaned Raw Composite Sampler Suction Line. Returned to Service with No Interruption to Sampling Schedule for Regulatory Sampling. Decant Complete, Raised and Deactivated Decant Pump. | FLAG | stage2_low_confidence | 0.011597 | ML: above threshold (no LLM available) — 0.012 | regulatory [regulatory] | 0.011597 | 0 | 0
2026-03 | 2026-03-09 | Schomberg Water Resource Recovery Facility | WW-WEST | Supernated STT and released some to SHT. left 1.76 m in thickening tank as holding tank reached high level. Auto wasting wasted 40 m3 yesterday. Completed labs and entered data in ace sheet. Completed station check. No issues found. Cleared rags from RAS pump 2. Set to duty 1 and it seems to work well with no speed deviation alarms. Completed consolidated head works work order. ROC received e-stop alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; alarm [control_system]; alarms [control_system] | work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed regulatory weekly sampling. Decanted sludge thickening tank and transferred remaining sludge to holding. Completed daily lab and station check no new issues - added data into SharePoint WAS pump wasted 47m3 overnight. Cleaned and verified aeration tank DO probes. | FLAG | stage2_low_confidence | 0.01286 | ML: above threshold (no LLM available) — 0.013 | regulatory [regulatory] | 0.01286 | 0 | 0
2026-03 | 2026-03-11 | Schomberg Water Resource Recovery Facility | WW-WEST | Collected weekly compliance samples | FLAG | stage2_low_confidence | 0.019871 | ML: above threshold (no LLM available) — 0.02 | compliance [regulatory] | 0.019871 | 0 | 0
2026-03 | 2026-03-05 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Decanted the sludge thickening tank Inspected the aeration blowers | FLAG | stage2_low_confidence | 0.012421 | ML: above threshold (no LLM available) — 0.012 |  | 0.012421 | 0 | 0
2026-03 | 2026-03-10 | Schomberg Water Resource Recovery Facility | WW-WEST | On site to check UV bank B, rack 7. Found blown fuse. Could not find cause of blown fuse. Replaced fuse. Was able to reset major fault alarm. Tested bank B. Ok now. | FLAG | stage2_low_confidence | 0.035806 | ML: above threshold (no LLM available) — 0.036 | fault [equipment_failure]; alarm [control_system] | 0.035806 | 0 | 0
2026-03 | 2026-03-17 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Batch wasted 56m3 from clarifier 2 overnight Everything operating as intended | FLAG | stage2_low_confidence | 0.0098939 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098939 | 0 | 0
2026-03 | 2026-03-23 | Schomberg Water Resource Recovery Facility | WW-WEST | On site for blower 1 oil leak. We will return with seals | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-19 | Schomberg Water Resource Recovery Facility | WW-WEST | Began diverting flow from the head works to the lagoon at 9:00am and ended at 11:15am. Diverted 169m3 total We diverted flow to drain the filter inlet channel to replace the filter inlet valves Work wasn?t completed and will be addressed at a later date Completed the station check and daily lab work Entered data into SharePoint Batch wasted 56m3 overnight | FLAG | stage2_low_confidence | 0.014802 | ML: above threshold (no LLM available) — 0.015 |  | 0.014802 | 0 | 0
2026-03 | 2026-03-19 | Schomberg Water Resource Recovery Facility | WW-WEST | Investigate hydraulics for valve replacement Will reschedule with operations. | FLAG | stage2_low_confidence | 0.013086 | ML: above threshold (no LLM available) — 0.013 |  | 0.013086 | 0 | 0
2026-03 | 2026-03-25 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Batch wasted 49m3 Tuesday night Hung warning signs around the lagoon and front entrance Cleaned the online DO probes Everything operating as intended | FLAG | stage2_low_confidence | 0.010035 | ML: above threshold (no LLM available) — 0.01 |  | 0.010035 | 0 | 0
2026-03 | 2026-03-25 | Schomberg Water Resource Recovery Facility | WW-WEST | Collected weekly compliance samples | FLAG | stage2_low_confidence | 0.019871 | ML: above threshold (no LLM available) — 0.02 | compliance [regulatory] | 0.019871 | 0 | 0
2026-03 | 2026-03-26 | Schomberg Water Resource Recovery Facility | WW-WEST | Pulled apart and cleaned out RAS pump 2, this pump was activating the speed deviation alarm and is making a loud noise when running Cleaned up in the aeration basement and process building | FLAG | stage2_low_confidence | 0.035058 | ML: above threshold (no LLM available) — 0.035 | noise [equipment_failure]; alarm [control_system] | 0.035058 | 0 | 0
2026-03 | 2026-03-20 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Everything operating as intended Batch wasted 56m3 from clarifier 2 overnight | FLAG | stage2_low_confidence | 0.0098939 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098939 | 0 | 0
2026-03 | 2026-03-16 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Overnight the plant batch wasted 40m3 from clarifier 2 Changed the batch wasting window from 16:00-22:00 to 16:00-23:00 Inspected the filter reject pumps Cleaned the tss probe in the aeration tank | FLAG | stage2_low_confidence | 0.010073 | ML: above threshold (no LLM available) — 0.01 |  | 0.010073 | 0 | 0
2026-03 | 2026-03-23 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Batch wasted 51m3 Friday night, 47m3 Saturday night and 47m3 Sunday night Cleaned the washrooms on site Inspected the lagoon berm | FLAG | stage2_low_confidence | 0.0098682 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098682 | 0 | 0
2026-03 | 2026-03-24 | Schomberg Water Resource Recovery Facility | WW-WEST | Installed new shaft seals(Viton) Sealed flange with silicone Installed back shroud Installed sheaves and aligned with straight edge. Installed belts with Gavin Installed front shroud Filled blower with oil. Complete | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-03 | 2026-03-19 | Schomberg Water Resource Recovery Facility | WW-WEST | Returned RAS operation to one pump as average daily flows are back to normal. P3 in duty 2. P2 in duty 2. P1 is duty 3/OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | Schomberg Water Resource Recovery Facility | WW-WEST | Collected weekly compliance samples | FLAG | stage2_low_confidence | 0.019871 | ML: above threshold (no LLM available) — 0.02 | compliance [regulatory] | 0.019871 | 0 | 0
2026-03 | 2026-03-11 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Decanted the sludge thickening tank Reset aeration blower 1, test ran it and it ran well Cleaned the tss and do probes | FLAG | stage2_low_confidence | 0.01056 | ML: above threshold (no LLM available) — 0.011 |  | 0.01056 | 0 | 0
2026-03 | 2026-03-02 | Schomberg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. Notified ROC. King Township Staff and Contractor On-site for Water Meter Replacement. WAS Pump #2 Cumulatively Auto-Wasted 104 m3 Over the Span of the Weekend. Placed Supernatant Drain Valve in Manual Open. Rotated WAS Pump Duties. Pump #2 Manual Off, Pump #1 in Auto. Lowered and Activated Decant Pump. Rotated RAS Pump Duties. Pump #3 in Duty #1, Pump #1 in Duty #3, OOS. Returned Supernatant Drain Valve to Manual Closed. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Identified Locally Outstanding Low Pressure Alarm on Compressor #2. Inspection Rendered No Issues. Notified Appropriate Staff of Potential Deficiency. Transferred Station to Generator Power with No Issues. Acknowledged and Cleared Associated Alarms. Completed JHSC Inspection. Topped Up Generator Room Spill Kit with Sorbent Socks. No Other Issues Found. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; sso [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | spill [critical]; sso [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-17 | Schomberg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WO. Notified ROC. Completed Consolidated Aer., Sludge and Vortex Blower Inspections. Topped Up Oil Reservoirs and Replaced Air Filters Where Necessary. All Belts OK. Returned to Service and Cleared Associated Alarms. Created Follow-Up WO Regarding Aer. Blower #1 Oil Leak for Maint. ?> W11740816. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; follow-up [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | sso [critical]; follow-up [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-26 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed daily lab and station check - no new issues. Recorded data into SharePoint. Batch wasted 49m3. Assisted Gavin with work on RAS pump 2. | FLAG | stage2_low_confidence | 0.0079961 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079961 | 0 | 0
2026-03 | 2026-03-18 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Batch wasted 51m3 overnight Cleaned the DO probes Aeration blower 1 cooling fan faulted and cannot be reset Blower 1 is currently left out of service | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure] | fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-24 | Schomberg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WO. Notified ROC. Completed UV System Inspection and Channel Clean Out. Replaced Damaged Sleeve and Tested Unit with No Issues. Returned to Service. | FLAG | stage2_low_confidence | 0.016636 | ML: above threshold (no LLM available) — 0.017 |  | 0.016636 | 0 | 0
2026-03 | 2026-03-27 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Cleaned the tss probe in the aeration tank There was a very brief power blip which put clarifier 2 and the grit blowers oos, I reset the clarifier but the grit blowers continued to trip Brent S. Came out to site and there was an issue with the PCS, Artour L. Was able to reprogram it and get the issue fixed | FLAG | stage1_keyword | 0.95 | Critical keyword match: trip [equipment_failure]; oos [equipment_failure] | trip [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-24 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Entered data into SharePoint Inspected the heat trace on the debris auger Batch wasted 54m3 on Monday night Cleaned the floor in the filter room | FLAG | stage2_low_confidence | 0.0098777 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098777 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Dr. Kay Pumping Station | WW-WEST | onsite due to power blip causing VFD failure on pump 1 - reset VFD and pump now back in duty | FLAG | stage2_low_confidence | 0.02386 | ML: above threshold (no LLM available) — 0.024 | failure [equipment_failure] | 0.02386 | 0 | 0
2026-03 | 2026-03-06 | Schomberg Dr. Kay Pumping Station | WW-WEST | In to Complete Station Check. Reviewed SCADA and trends. No Issues Found. | FLAG | stage2_low_confidence | 0.013649 | ML: above threshold (no LLM available) — 0.014 | scada [control_system] | 0.013649 | 0 | 0
2026-03 | 2026-03-31 | Schomberg Dr. Kay Pumping Station | WW-WEST | Completed station check. No issues found. | FLAG | stage2_low_confidence | 0.011047 | ML: above threshold (no LLM available) — 0.011 |  | 0.011047 | 0 | 0
2026-03 | 2026-03-03 | Schomberg Dr. Kay Pumping Station | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Transferred Station to Generator Power with No Issues. Acknowledged Associated Alarms. Reviewed SCADA and Trends. No Issues Found Completed Hi/Lo Temperature Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. Completed JHSC and Hazardous Materials Inspections with No Issues. Manually Activated Duty #1 Pump Start Set-point. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. | FLAG | stage2_low_confidence | 0.025015 | ML: above threshold (no LLM available) — 0.025 | sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] | 0.025015 | 0 | 0
2026-03 | 2026-03-10 | Schomberg Dr. Kay Pumping Station | WW-WEST | Completed station check. No issues found. | FLAG | stage2_low_confidence | 0.011047 | ML: above threshold (no LLM available) — 0.011 |  | 0.011047 | 0 | 0
2026-03 | 2026-03-13 | Schomberg Dr. Kay Pumping Station | WW-WEST | Completed the station check Entered data into SharePoint Everything operating as intended | FLAG | stage2_low_confidence | 0.01158 | ML: above threshold (no LLM available) — 0.012 |  | 0.01158 | 0 | 0
2026-03 | 2026-03-09 | Schomberg Dr. Kay Pumping Station | WW-WEST | Allowed access to Hydro One contractors to change hydro meter. Shut off diesel. Shut off main breaker. Meter changed. Restored power to facility. Returned diesel to auto. Cleared alarms. Activated duty 1. | FLAG | stage2_low_confidence | 0.010567 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010567 | 0 | 0
2026-03 | 2026-03-24 | Schomberg Dr. Kay Pumping Station | WW-WEST | In to Complete Station Check. Reviewed SCADA and Trends. No Issues Found. | FLAG | stage2_low_confidence | 0.013649 | ML: above threshold (no LLM available) — 0.014 | scada [control_system] | 0.013649 | 0 | 0
2026-03 | 2026-03-17 | Schomberg Dr. Kay Pumping Station | WW-WEST | Completed the station check Wessuc on site to do a wet well cleaning Disabled the low level lock out Manually pumped down the wet well during the cleaning Enabled the low level lock out when they finished the cleaning Returned the station to normal operation Everything operating as intended | FLAG | stage2_low_confidence | 0.013289 | ML: above threshold (no LLM available) — 0.013 |  | 0.013289 | 0 | 0
2026-03 | 2026-03-27 | Schomberg Dr. Kay Pumping Station | WW-WEST | Couldn?t make it to site due to issues at SBSP Did a remote station check and entered data into sharepoint | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066422 | 0 | 0
2026-03 | 2026-03-28 | Georgina Water Treatment Plant | EAST | SYSTEM TESTING - PLEASE IGNORE | FLAG | stage2_low_confidence | 0.012592 | ML: above threshold (no LLM available) — 0.013 |  | 0.012592 | 0 | 0
2026-03 | 2026-03-28 | Georgina Water Treatment Plant | EAST | SYSTEM TESTING - PLEASE IGNORE | FLAG | stage2_low_confidence | 0.012592 | ML: above threshold (no LLM available) — 0.013 |  | 0.012592 | 0 | 0
2026-03 | 2026-03-30 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. | FLAG | stage2_low_confidence | 0.0086291 | ML: above threshold (no LLM available) — 0.009 |  | 0.0086291 | 0 | 0
2026-03 | 2026-03-30 | Georgina Water Treatment Plant | EAST | On site to conduct manual backwash on GAC 1. Plant off during this time. Lee Ferguson on site for Backflow preventor work on UV cooling systems. 13:50hrs: Received a UV dosage High alarm due to running only one train through the UV system to top influent channel due to GAC 1 Filter to waste line open which draws down the channel. Informed ROC of disregard. Topped up Sodium Hydroxide from 60L to 100L. Completed GAC 1 and filter to waste at 14:30hrs. GAC 1 in service. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility for driveway/gate and GWTP intake works. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-30 | Georgina Water Treatment Plant | EAST | Informed ROC. Plant Running. Unable to perform calibrations. Informed ROC and left the site | FLAG | stage2_low_confidence | 0.016738 | ML: above threshold (no LLM available) — 0.017 |  | 0.016738 | 0 | 0
2026-03 | 2026-03-30 | Georgina Water Treatment Plant | EAST | Placed UV 1 & 2 manual off, and changed membrane trains 5-8 to OFF mode for instrumentation work. | FLAG | stage2_low_confidence | 0.013165 | ML: above threshold (no LLM available) — 0.013 |  | 0.013165 | 0 | 0
2026-03 | 2026-03-31 | Georgina Water Treatment Plant | EAST | On site for station check and to collect weekly micro samples (W11705578), Algae samples (W11705308), VOC (W11705280) and in house ATP samples, GLIP samples. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. 08:52hrs: Adjusted Clearwell 1 from 1.65mg/l to 1.75mg/l based on multiple CL2 grab residuals. 08:57hrs: Adjusted Clearwell 2 from 1.55mg/l to 1.70mg/l based on multiple CL2 grab residuals. 09:02hrs: Adjusted Post Clearwell from 1.47mg/l to 1.63mg/l based on multiple CL2 grab residuals. 09:30hrs: Adjusted Sutton Total from 1.76mg/l to 1.89mg/l based on multiple CL2 grab residuals. 09:35hrs: Adjusted Keswick Free from 1.46mg/l to 1.56mg/l based on multiple CL2 grab residuals. 09:38hrs: Adjusted Keswick Total from 1.77mg/l to 1.88mg/l based on multiple CL2 grab residuals. 11:25hrs: Collected all raw water samples. Collected Treated samples (Keswick Line) @ 11:35hrs. Cl2 grab residuals: FCL: 1.78mg/l TCL: 2.08mg/l Received Sodium Hydroxide delivery 31 jugs. Received Hypo delivery 1500L. Changed High Lift Duties due to low Chlorine in Contact #2. HL P3 now in duty 1. Turned off fluoride pumps during this change as to not cause a fluoride spike. Informed ROC. Collected Flouride grabs @ 14:25hrs: Keswick grab: 0.69mg/l, Analyzer: 0.70mg/l, Sutton Fluoride grab: 0.68mg/l Analyzer: 0.63mg/l. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-30 | Georgina Water Treatment Plant | EAST | AT 15:55 activated duty early to run through the night. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039673 | 0 | 0
2026-03 | 2026-03-31 | Georgina Water Treatment Plant | EAST | THIS IS A SYSTEM TEST PLEASE IGNORE Testing with iPhone on WIFI Testing revision | FLAG | stage2_low_confidence | 0.0076837 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076837 | 0 | 0
2026-03 | 2026-03-31 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Rotated air compressor duty to Kaiser. Triggered raw water sample pump duty rotation. Rotated chlorinator 5 into duty for clearwell dosing. | FLAG | stage2_low_confidence | 0.026045 | ML: above threshold (no LLM available) — 0.026 | sso [critical] | 0.026045 | 0 | 0
2026-03 | 2026-03-30 | Georgina Water Treatment Plant | EAST | Test backflow preventers All five passed | FLAG | stage2_low_confidence | 0.011019 | ML: above threshold (no LLM available) — 0.011 |  | 0.011019 | 0 | 0
2026-03 | 2026-03-02 | Georgina Water Treatment Plant | EAST | Informed ROC, GWTP Low Lift- onsite to perform annual calibration. Devices were done as below : NIT, AITs, pH, chlorine gas detector, TIT. Used calibration mode. Total chlorine analyzers were calibrated using service water and by taking multiple grab samples. Adjusted analyzers accordingly. G-1.75 mg/l, A- 1.75 mg/l Total chlorine analyzers as left at 0.00 mg/l using process water. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.00622 | 0 | 0
2026-03 | 2026-03-31 | Georgina Water Treatment Plant | EAST | SYSTEM TESTING PLEASE IGNORE Testing logentry without wifi Revision 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055245 | 0 | 0
2026-03 | 2026-03-31 | Georgina Water Treatment Plant | EAST | Test backflow preventers B1 both passed | FLAG | stage2_low_confidence | 0.0083397 | ML: above threshold (no LLM available) — 0.008 |  | 0.0083397 | 0 | 0
2026-03 | 2026-03-04 | Georgina Water Treatment Plant | EAST | On site for station check and to collect weekly micro samples (W11637418), Algae samples (W11637619), VOC (W11637148) and in house ATP samples, GLIP samples. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Placed Train #8 into ACID R-Clean. Data entered in PWQ sheets. Placed Low Lift P3 back into service. Instrumentation on site for calibrations. 10:15hrs: Collected all raw water samples. Collected Treated samples (Keswick Line) @ 10:35hrs. Cl2 grab residuals: FCL: 1.75mg/l FCL Analyzer: 1.71mg/l TCL: 1.97mg/l TCL Analyzer: 1.95mg/l Conducted Treated Header Cl2 Maintenance, verifications in station check PWQ sheet. Conducted Chlorine System Inspection - no issues. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. GAC 4 Offline for sample media collection today. Activated plant @ 12:55hrs 13:14hrs: Began filling Backwash Clearwell. Placed HLP2 off for contractors to have a look. Placed back online after inspection complete. Informed ROC of all work completed. Placed Trains 5 to 8 M-Clean schedule back on after SCADA upgrades today. Filled Backwash Clearwell Tank to refill GAC 4 this week. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | Georgina Water Treatment Plant | EAST | On site for weekly sampling, station check, and lab sampling. Entered data into PWQ Sheets. Refilling GAC4 using backwash system. Notified ROC, expecting turbidity alarms. 10:25 open backwash clearwell fill valve. 10:29 close backwash clearwell fill valve. 10:30 open back wash drain valve and backwash inlet valve. 10:33 open backwash pump 2 recirculating valve. 10:35 manual start backwash pump 2. 10:36 manual open backwash pump 2 FCV to 20%. 10:49 Increase backwash pump 2 FCV open setpoint to 25% 11:08 Close GAC4 backwash drain valve. 11:18 Close backwash FCV, manual stop backwash pump 2, close recirculating valve and backwash inlet valve. 11:33 Manual open GAC4 inlet valve, and GAC4 filter to waste valve. 11:55 Manual close GAC4 filter to waste valve, place effluent valve back in auto. GAC4 back in service. 13:30-14:30 Completed chlorine analyzer maintenance on Wash water and to the lake analyzers. | FLAG | stage2_low_confidence | 0.031088 | ML: above threshold (no LLM available) — 0.031 | alarm [control_system]; alarms [control_system] | 0.031088 | 0 | 0
2026-03 | 2026-03-10 | Georgina Water Treatment Plant | EAST | On site to replace network switch with network analyst Kevin wen, Aaron Magsakay and John Dimarco. Hub 1 and GWTP local server lost comms due to this. At GWTP, no trends between 9:25 AM and 10:20 AM Powered off the old switch and plugged in the ports to new switch. Checked the connections to all PAC and Servers once the replacement is completed Checked local OIT at GWTP - All ok | FLAG | stage1_keyword | 0.95 | Critical keyword match: plugged [infrastructure] | plugged [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | Georgina Water Treatment Plant | EAST | On site for MIT review, station check, lab analysis. Collected weekly micro samples (W11656959), GLIP samples. Data recorded in PWQ sheet. Reviewed MIT and daily filter performance on all trains - all passed. Reviewed SCADA trends and UV trends. 10:05hrs: Collected all raw water samples. Collected Treated samples (Keswick Line) @ 09:30hrs. Cl2 grab residuals: FCL: 1.55mg/l FCL Analyzer: 1.55mg/l TCL: 1.86mg/l TCL Analyzer: 1.79mg/l 10:10hrs: Train #1 shutdown on Uncommanded stop. Checked Train, did not see any issues with the pump or outstanding VFD alarms. Placed Train back into service to monitor. Refilling of GAC4 to place back into service. GAC 4 back online. Turned plant off @11:05hrs for instrumentation to conduct Calibrations on High Lift Keswick and Sutton Header including Fluoride probes. 14:25hrs: Verified Keswick Fluoride Analyzer after calibration: Grab: 0.73mg/l , Analyzer 0.70mg/l. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | Georgina Water Treatment Plant | EAST | Restarted the local sever for GWTPL PAC removal, trending is posted at the Hub server. Plant is off | FLAG | stage2_low_confidence | 0.007683 | ML: above threshold (no LLM available) — 0.008 |  | 0.007683 | 0 | 0
2026-03 | 2026-03-13 | Georgina Water Treatment Plant | EAST | On site for station check and lab analysis. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Reviewed SCADA, completed station check and lab analysis. Station OK. | FLAG | stage2_low_confidence | 0.019245 | ML: above threshold (no LLM available) — 0.019 | scada [control_system] | 0.019245 | 0 | 0
2026-03 | 2026-03-12 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. UV's in manual off for UV maintenance, cleaning and calibration. Informed ROC of work. Powered down UV's during work. Instrumentation on site for Annual calibrations. 13:30hrs: Swapped out dehumidifier in UVT Analyzer. UV alarms cleared after swap. 14:00hrs: Started up Duty #1 to monitor. 14:45hrs: Low Lift building flood alarm came in on SCADA. Went to investigate. Sump was high and high switch alarm was going off, was able to troubleshoot issue with floats over the phone with Dan B and managed to get P1 working. P2 is out of service in local off. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; flood [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; flood [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-05 | Georgina Water Treatment Plant | EAST | Onsite for annual calibrations Informed ROC and operations Plant offline Worked on train 6-7 FITs and NITs as well as train 7,6,5 and 1 MIT PITs Operations started plant Informed ROC Left site No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059568 | 0 | 0
2026-03 | 2026-03-05 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. PCS on site in low lift for PAC removal. Placed plant off for PAC panel replacement. Instrumentation on site conducting calibrations on Trains 6,7. Placed Trains off during this time. Placed Train 8 back online from ACID R-CLEAN yesterday. MIT conducted. Passed. Topped up Sodium Hydroxide Tanks from 50L to 102L. Low Lift Cl2 Analyzer maintenance, Treated Header Turbidity Maintenance and greasing of low lift sample pumps. Received 3 Full Chlorine Tonner's, sent back 3 empty to Brenntag. 14:05hrs: Started up plant for PCS to ensure plant functioning correctly after server work. 14:13hrs: Received a UV lockout on UV#1 critical fault, Lo Water flow alarm. Was able to switch to UV2 and cleared alarms on UV1. 14:26hrs: UV2 shutdown on critical fault, Lo water flow alarm. Deactivated the duty to investigate the issue. 14:45hrs: Restarted the plant to investigate the issue. Received a UV2 Critical fault alarm, low water flow alarm. Noticed that when the UV system is ready, the Trains are not starting up and providing any flow through the UV's causing the UV's to fault. Informed PCS Chris Scott of the issue as there is an interlock on the trains stating PAC-3 communication failed. 15:05hrs: Reset both UV's by powering them down and back up again. Chris Scott onsite to troubleshoot why trains are not starting when UV is ready. PCS looking into it. 16:14hrs: Activated Duty to run plant as per PCS request. Plant is now running with no issues. | FLAG | stage2_low_confidence | 0.25133 | ML: above threshold (no LLM available) — 0.251 | fault [equipment_failure]; failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.25133 | 0 | 0
2026-03 | 2026-03-04 | Georgina Water Treatment Plant | EAST | Informed ROC and operations. Onsite to perform annual calibration. Used calibration mode. Devices were done as below: Train 8 (NIT, PITs, FIT). Highlift LITs, Sutton and Keswick line FITs. Troubleshoot High lift AIT, found ingress of water at electric connections. Cleaned it and put it back in Service. Put everything back in service All the related alarms were cleared. No issues. Informed ROC and operations and left the site. | FLAG | stage2_low_confidence | 0.008723 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.008723 | 0 | 0
2026-03 | 2026-03-09 | Georgina Water Treatment Plant | EAST | 14:43 Initiated train 8 MIT. It passed with 1.95kpa/1.90kpa hi/low pressure decay. It is in standby. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033931 | 0 | 0
2026-03 | 2026-03-04 | Georgina Water Treatment Plant | EAST | Onsite to respond to chlorinators 5 and 6 vacuum hi hi alarm Before arriving to site asked ROC to deactivate duty. CC lo alarm active ~ CC1 analyzer reading 0.8 mg/l. Placed chlorine ejector solenoid valves in manual and tested both ejectors, no issues Tested chlorinators 5 and 6 in manual vacuum increased to over -500 mg Found chlorine line isolation valve closed. Opened valve and slowly pressurized chlorine gas line to chlorinators CC tanks residual further dropped down to 0.09 mg/l during troubleshooting with system water./ Collected grab on CC1 ~ 0.55 mg/l. Tank 2 analyzer was 1.25 mg/l, grabs was 1.22 mg/l Opened solenoid valve in manual and opened chlorinator 5 to push some chlorine solation into tanks. Ran recirculation pump in manual to good mixing in the CC. Activated duty monitored plant until residual from CC tanks recovered, notified ROC before leaving site | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-02 | Georgina Water Treatment Plant | EAST | Onsite for station check and lab analysis, entered data into PWQ sheets. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. *Also reviewed monthly filter performance on all membrane trains. No issues. 11:00hrs: Zero'd and calibrated High Lift Free Chlorine CL17 Analyzer. Adjusted Reading from 0.86mg/l to 1.64mg/l based on CL2 grab residuals. WO made for this analyzer as it continues to drift. Conducted JHSC inspection in the low lift. 13:50hrs: Adjusted Keswick Fluoride Analyzer from 0.85mg/l to 0.76mg/l using the offset based on in house lab analysis. 14:05hrs: Adjusted Sutton Fluoride Analyzer from 0.90mg/l to 0.77mg/l using the offset based on in house lab analysis. | FLAG | stage2_low_confidence | 0.031157 | ML: above threshold (no LLM available) — 0.031 |  | 0.031157 | 0 | 0
2026-03 | 2026-03-13 | Georgina Water Treatment Plant | EAST | Rebuilt 200ppd regulator. Instrumentation on site for calibrations. Responded to low lift flood alarm. Float was stuck against wall, was able to move float and allow P1 to run. P2 OOS, WO initiated to maintenance for replacement of pump. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; flood [critical]; out of service [equipment_failure]; oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; flood [critical]; out of service [equipment_failure]; oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-06 | Georgina Water Treatment Plant | EAST | Onsite for annual calibrations Informed ROC and operations Plant offline Worked on train 2-5 FITs and NITs as well as GAC 1 effluent Flow Operations started plant Informed ROC Left site No issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057493 | 0 | 0
2026-03 | 2026-03-02 | Georgina Water Treatment Plant | EAST | Verified low lift sump pump 2 is seized. Gathered info required for replacement. | FLAG | stage2_low_confidence | 0.022236 | ML: above threshold (no LLM available) — 0.022 | seized [equipment_failure] | 0.022236 | 0 | 0
2026-03 | 2026-03-12 | Georgina Water Treatment Plant | EAST | On site for work orders. Changed SBS pump duty change to All Stop, and triggered duty rotation. UV system cleaning, UV reactors sensors calibration, UV inventory assessment. | FLAG | stage2_low_confidence | 0.016428 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action] | 0.016428 | 0 | 0
2026-03 | 2026-03-12 | Georgina Water Treatment Plant | EAST | Inspected sump pump #2 after reports of it not working, removed unit and confirmed it does spin and pumps water, I believe there may be an underlying issue with the floats intermittently working. Will require Electrician on-site. | FLAG | stage2_low_confidence | 0.041211 | ML: above threshold (no LLM available) — 0.041 | not working [equipment_failure] | 0.041211 | 0 | 0
2026-03 | 2026-03-12 | Georgina Water Treatment Plant | EAST | Onsite to continue with annual calibrations Informed ROC and operations Plant off line Calibrated plant chlorine gas detectors and sulphonator detectors Cleared associated alarms Informed ROC and operations Left site | FLAG | stage2_low_confidence | 0.019827 | ML: above threshold (no LLM available) — 0.02 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.019827 | 0 | 0
2026-03 | 2026-03-05 | Georgina Water Treatment Plant | EAST | Received a call from the ROC at 16:31 for a Train 5 shutdown alarm. Attended SCADA to investigate. Found Train 5 turbidity erratic. Working with OIC Joe Mazza, Chris Scott (PCS) was troubleshooting UV programming, which caused unplanned UV duty rotation. The fluctuation of the low lift pumps starting on and shutting off would cause air entrainment in the membranes and result in false turbidity spikes. Train 5 left OFF for the night until an on site operator can investigate. Received a UV start/stop sequence fault at 17:08, resulting from troubleshooting. Reset UV2 alarms and monitored. Station back in service. | FLAG | stage2_low_confidence | 0.035305 | ML: above threshold (no LLM available) — 0.035 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.035305 | 0 | 0
2026-03 | 2026-03-04 | Georgina Water Treatment Plant | EAST | While on site completed multiple grab samples on the hi lift analyzer. This was done after instrumentation was here to validate that the analyzer was reading correctly. Time: 14:15 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.56 1.61 No issues with analyzer after verification. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065292 | 0 | 0
2026-03 | 2026-03-06 | Georgina Water Treatment Plant | EAST | Fluoride pumps manual off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054652 | 0 | 0
2026-03 | 2026-03-02 | Georgina Water Treatment Plant | EAST | Reviewed monthly turbidity performance data - all within spec. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064274 | 0 | 0
2026-03 | 2026-03-05 | Georgina Water Treatment Plant | EAST | Move water pumps inside | FLAG | stage2_low_confidence | 0.012284 | ML: above threshold (no LLM available) — 0.012 |  | 0.012284 | 0 | 0
2026-03 | 2026-03-13 | Georgina Water Treatment Plant | EAST | Onsite to continue with annual calibrations Informed ROC and operations Plant is off line Calibrated: Chemical room LITs, GAC LITs, CIP FITs, waste water LITs, sedimentation LITs, Backpulse FIT, channel LITs Informed Operations and ROC No issues Left site | FLAG | stage2_low_confidence | 0.0099936 | ML: above threshold (no LLM available) — 0.01 |  | 0.0099936 | 0 | 0
2026-03 | 2026-03-06 | Georgina Water Treatment Plant | EAST | Attended site to address Train 3 turbidity fault - informed by RO Adam Button. CMU5 W11714562. Removed cuvette and flushed entrained bubbles that were adhered to the side of the cuvette. Placed Train 3 back in service. | FLAG | stage2_low_confidence | 0.018484 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure] | 0.018484 | 0 | 0
2026-03 | 2026-03-09 | Georgina Water Treatment Plant | EAST | Onsite for annual calibrations Informed ROC Coordinated calibration with operations. Plant offline Instruments calibrated: Train 1 NIT and FIT GAC 2-4 FITs Low Lift FIT High lift NITs Informed operations. Plant available to go online Informed ROC No issues Left site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038301 | 0 | 0
2026-03 | 2026-03-14 | Georgina Water Treatment Plant | EAST | Logged in for Contact Tank 1 lolo alarm which caused GAC's to stop flowing. Deactivated duty to allow UV's to shut down, received UV Critical Fault alarm on shutdown. Was able to clear alarm and restart duty and plant. Switched to High Lift P1 to bring up residual in Clearwell. | FLAG | stage2_low_confidence | 0.027819 | ML: above threshold (no LLM available) — 0.028 | fault [equipment_failure]; alarm [control_system] | 0.027819 | 0 | 0
2026-03 | 2026-03-23 | Georgina Water Treatment Plant | EAST | ROC called @16:15 for UV intensity low alarm. Came in on plant startup when UV first saw flow. Immediately recovered to normal levels | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0062612 | 0 | 0
2026-03 | 2026-03-27 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all trains - all passed. Also on site for monthly meeting and OJT training. At 10:16 turned trains 1, 4 and 8 off for instrumentation to complete annual calibrations. | FLAG | stage2_low_confidence | 0.0084567 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084567 | 0 | 0
2026-03 | 2026-03-22 | Georgina Water Treatment Plant | EAST | @14:00 ROC called for High lift tanks 1 and 2 low alarms - levels are 4.59 / 4.56 m. Alarms were a result from the GAC 2 Lolo alarms that came in overnight - The GAC 2 LIT is not working properly, causing GAC 2 to be interlocked. Will need instrumentation to investigate tomorrow. 148 L/s is going to the Clearwell, while 180 L/s is being pumped by high lifts. With GAC 2 still in service, but interlocked, the other GACs could not increase flow to compensate. Placed GAC 2 OOS on the GAC setpoints filtration page, allowing the other GACs to increase flow. There is now 206 L/s GAC flow going to the Clearwell. GAC2 OOS. Clearwell levels will now recover slowly. Informed ROC to monitor | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; not working [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; not working [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-17 | Georgina Water Treatment Plant | EAST | eviewed MIT and daily filter performance on all trains - all passed. 09:05hrs: Conducted manual backwash on GAC 3, informed ROC of work. Instrumentation on site for rebuild and calibration of Mussel Control Chlorine system. Plant off during this time. Chlorinator 7 and 8. Aeration blower maintenance. Sludge Pump inspection completed. Flood alarm testing in plant completed, no issues. High Lift Pump inspection completed. OJT on R and M-clean with Jackie S. Conducted M-Clean check on Train #7. Hypo residual was 100ppm, neutralization was 0ppm. No issues with M-Clean process. 13:25hrs: Activated plant for instrumentation to calibrate Chlorinator's 7 and 8. Left duty active. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; flood [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; flood [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-19 | Georgina Water Treatment Plant | EAST | Onsite to continue annual calibrations Informed ROC and operations Completed high lift pumps 1, 2 and 4 PITs Informed ROC and operations Completed Left site No issues | FLAG | stage2_low_confidence | 0.0072427 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072427 | 0 | 0
2026-03 | 2026-03-25 | Georgina Water Treatment Plant | EAST | Onsite to continue with annual calibrations Informed ROC and operations Plant offline Completed GAC NITs, Backwash LIT and Filter NIT Cleared associated alarms Informed ROC and operations Left site | FLAG | stage2_low_confidence | 0.018269 | ML: above threshold (no LLM available) — 0.018 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.018269 | 0 | 0
2026-03 | 2026-03-23 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Conducted station check and lab analysis. Readings in PWQ sheet. Placed Train 7 back on line. Initiated MIT. Train 7 had MIT failure over the weekend. Re-trying MIT test. MIT test showed increased pressure decay (6.5kpa) on low pressure side. Investigated train and found significant leak on Cassette G. WO issued to further repair. Will keep Train 7 offline. Placed GAC 2 back into service, LIT issues over the weekend. Trend show LIT back online. Instrumentation on site and investigated the LIT. No further issues at this point. Will monitor. Changed Duty on Air compressors. BOGE now Duty 1. Changed Duty on Low Lift sample pumps: P2 from D1 to D3 and P1 to D1. Reviewed MIT and daily filter performance on all trains - all passed. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; emergency [critical]; failure [equipment_failure]; out of service [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | sso [critical]; emergency [critical]; failure [equipment_failure]; out of service [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-16 | Georgina Water Treatment Plant | EAST | On site for station check, lab analysis. Data recorded in PWQ sheet. Placed plant to offline by placing UV's to manual and placed Sutton PRV valves into local and closed valves in basement for Trial Isolation of valve work to be completed to fix broken gear box in Valve chamber that feeds Keswick to Sutton. Completed Maple Reindeers GWTP site online orientation. Reviewed MIT and daily filter performance on all trains - all passed. 10:30hrs: Purged Clearwell Chlorinators 5 and 6 for instrumentation to rebuild chlorinators. 13:00hrs: Instrumentation conducted Chlorinator calibrations, require operational assistance to open and close Post chlorination solenoids during calibrations. 14:00hrs: Activated duty to run plant and ensure Sutton PRVs working as intended and GWTP Chlorinators working. 14:00hrs: There is an outstanding High Alarm on Contact Tank 1 due to the Chlorinator calibrations. Residual will decrease as plant is running. Reviewed SCADA trends and UV trends. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-24 | Georgina Water Treatment Plant | EAST | Troubleshoot MIT high pressure side on train #6 - it has been high (8.12 kpa last nights MIT) Manually added pressure to train #6 using MIT SV2 69kpa. Pressurized high pressure side of train only. Once pressurized, isolated all the cassettes, to test if we are still losing pressure with only the header / valves. Pressure is still dropping, indicating that the backpulse or permeate valve are passing. Reopened cassettes and purged air from train @11:15. Left train in OFF position for now Deactivated duty @13:30 to have the plant quiet during train #6 testing Pressurized train #6 again @13:31 and inspected train on the valve side. Observed a drip leak coming from the permeate valve. Upon closer inspection it is leaking and hissing air while pressurized. Purged train @13:53. Placed valves back to auto. Created W11756506 for maintenance to address the valve. The train can still be ran Placed train to ON @14:31 - it?s back in standby Activated system duty again @14:34 | FLAG | stage2_low_confidence | 0.15729 | ML: above threshold (no LLM available) — 0.157 | leak [infrastructure]; leaking [infrastructure]; drip [infrastructure] | 0.15729 | 0 | 0
2026-03 | 2026-03-24 | Georgina Water Treatment Plant | EAST | On site to complete comprehensive housekeeping. Deactivating plant at 13:30. Troubleshooting train 6 on hi MIT results. Train 6 had an issue with a permeate valve passing which is contributing to the hi MIT results. Work order has been created. | FLAG | stage2_low_confidence | 0.038155 | ML: above threshold (no LLM available) — 0.038 | work order [maintenance_action] | 0.038155 | 0 | 0
2026-03 | 2026-03-25 | Georgina Water Treatment Plant | EAST | Activated both the Sutton and Keswick duties at 15:47. Will monitor off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036487 | 0 | 0
2026-03 | 2026-03-25 | Georgina Water Treatment Plant | EAST | Test backflow preventers All 4 passed | FLAG | stage2_low_confidence | 0.0082653 | ML: above threshold (no LLM available) — 0.008 |  | 0.0082653 | 0 | 0
2026-03 | 2026-03-20 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all trains - all passed. At 11:10 put train 4 back on line to complete an MIT that is currently outstanding. Train 4 MIT passed. At 11:50 activated duty for both Sutton and Keswick due to instrumentation finishing their work early. Time: 12:45 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.42 Time: 12:52 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.45 1.47 Total: 1.69 1.69 Time: 12:55 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.41 Total: 1.71 1.68 Verified analyzers on site and completed station check. Switched duty 1 hi lift pumps from pump 2 to pump 3 to bring up the contact tank 2 residual. Checked station and trends. Entered data into the PWQ sheet. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0015807 | 0 | 0
2026-03 | 2026-03-27 | Georgina Water Treatment Plant | EAST | Instrumentation on site for Train 1, 4, 8 LIT calibration. Placed trains offline for calibrations. Conducted on site OJT for Tonner Change with Travis W, Jackie S, Patrick F, Dan Z. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility for driveway/gate and GWTP intake works. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-09 | Georgina Water Treatment Plant | EAST | On site for station check and lab analysis. Verified Keswick header, Sutton header, and CT&CW chlorine analyzers. Entered data into PWQ Sheets. Adjusted free chlorine analyzer for post clear well after three grab samples. Sample at 10:46 - Free grab: 1.71 mg/L Analyzer: 1.59 mg/L Adjusted free chlorine analyzer for contact tank 2 after three grab samples. Sample at 11:05 - Free grab: 2.74 mg/L Analyzer: 2.55 mg/L | FLAG | stage2_low_confidence | 0.012487 | ML: above threshold (no LLM available) — 0.012 |  | 0.012487 | 0 | 0
2026-03 | 2026-03-10 | Georgina Water Treatment Plant | EAST | On site for work orders. Completed the following work orders: Clear well drain pump maintenance and inspection, placed pump manual off to inspect. Clear well drain valves exercise. GAC4 media sampling. 12:55 Chlorine gas leak detector test, Notified ROC of alarm test. Chlorine gas scrubber check. Permeate/BP pumps inspections. Wastewater transfer pump inspection and duty change. 13:45 Manual closed GAC4 filter to waste valve, and manual closed backwash drain valve. 13:47 Manual open GAC backwash tank fill valve. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | Georgina Water Treatment Plant | EAST | Onsite for annual calibrations Coordinated calibration with operations. Plant offline Instruments calibrated: High Lift AIT, Keswick and Sutton line free AIT Keswick Fluoride AIT UVT AIT Informed operations. Plant available to go online No issues Left site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069415 | 0 | 0
2026-03 | 2026-03-02 | Georgina Water Treatment Plant | EAST | On site to investigate scada position feedback error for GAC4 effluent valve. Found analog output from actuator zero out of adjustment. Found fully closed output at 4.7mA. Adjusted output to 4mA when valve fully closed. Reading 0% on scada now. | FLAG | stage2_low_confidence | 0.031043 | ML: above threshold (no LLM available) — 0.031 | scada [control_system] | 0.031043 | 0 | 0
2026-03 | 2026-03-09 | Georgina Water Treatment Plant | EAST | Train #1 was offline for the weekend - Had a low performance alarm come in (99.18%) at midnight on March 8, 2026. The low alarm is set to 99.20%. Monthly performance at 99.92%, well within the objectives. Train 1 placed online. Placed Train 1 back into service and conducted MIT. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Instrumentation conducting calibrations on Train #1, placed Train to off. Changed duty on Air compressors: BOGE in D1, Kaiser to Standby. Low Lift drainage pump #1 had an overload alarm from the weekend. Checked the VFD MCC and was able to reset the fault (Fault code 25). Will continue to monitor, if it comes in again, will send WO to electrical. Placed Pump 1 to D1 and activated duty. No issues/faults came back in. GAC 4 Offline for sample media collection tomorrow. Drained GAC 4 through the effluent valve and then to filter to waste to empty for tomorrow's sample collection. ROC informed. Opened backwash drain valve. GAC 4 empty at 13:50hrs. Turbidimeter in faulted state due to no flow. Changed duty setpoint on Raw water sample pumps: P2 was running in D1, placed it to D3, P3 to D1, P1 to D2. Disabled M-Cleans for Trains 5 to 8 for tomorrow. 14:50hrs: Placed Train # 1 back online Equipment out of service: Sludge P3 (leaking volute). GAC 4 offline for the night. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; emergency [critical]; fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | sso [critical]; emergency [critical]; fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-06 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Placed Train #5 back online due to turbidity spike yesterday. MIT initiated and recorded in PWQ sheet. Will monitor on next start up. Instrumentation working on Trains 4 and 5 calibrations. Placed to off. Conducted manual backwash on GAC4. Hoist inspection in low lift. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-03 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Conducted Turbidimeter TU5400 SC Analyzer maintenance and calibration on Trains 1 to 8 Permeate. Conducted Diesel generator test run. Disabled M-Cleans on Train 7 and 8. Informed ROC of the work. Diesel Generator Run Monthly Test: Start Runtime: 10:35hrs (Run hrs: 515.92hrs) Fuel Start: 1.01m Stop Runtime: 11:45hrs (Run hrs: 517.18hrs ) Fuel Stop: 0.97m Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 300amps Volts: 600 Hertz: 60 RPM: 2000 Oil Pressure: 100psi Water temp: 170F Oil temp: 190 Ran plant during test run under load. No issues during test run. Re-enabled M-Cleans after generator run. JHSC Inspection completed. Visual inspection of chemical system. No leaks observed. Train 8 to Chemical Injection via Recirculation for R-Clean Hypo tomorrow. Chemical pump system inspections completed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | leak [infrastructure] | 0.0032874 | 0 | 0
2026-03 | 2026-03-23 | Georgina Water Treatment Plant | EAST | On site to assist with station check and lab analysis. No issues on site. | FLAG | stage2_low_confidence | 0.012104 | ML: above threshold (no LLM available) — 0.012 |  | 0.012104 | 0 | 0
2026-03 | 2026-03-17 | Georgina Water Treatment Plant | EAST | Onsite to perform annual maintenance/Rebuild chlorinators #7 and #8. Informed ROC. Joe isolated gas cylinders and purged the lines. We rebuilt both the chlorinators. performed vacuum test. No leak found. Performed gas calibration and Performed verification and Put both chlorinators back in service. No issues. Operations put the plant in service during calibration. All the related alarms were cleared. No issues. Informed ROC and operations and left the site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; leak [infrastructure] | alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-16 | Georgina Water Treatment Plant | EAST | Onsite to perform annual maintenance/Rebuild chlorinators #5 and #6. Informed ROC and Joe isolated gas cylinders and purged the lines. We rebuilt both the chlorinators. performed vacuum test. No leak found. Performed gas calibration and Performed verification and Put both chlorinators back in service. No issues. Operations put the plant in service. All the related alarms were cleared. No issues. Informed ROC and operations and left the site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; leak [infrastructure] | alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-24 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on membrane trains - passed and within range - recorded data in PWQ sheets. Train #7 offline due to High MIT on Low Pressure side. Will be conducted repairs on low pressure cassette G today. Conducted repairs, replaced O rings on end cap of Cassette G. Conducted MIT test. MIT test passed. Placed Train 7 back online. Conducted Train 6 troubleshooting due to higher than normal MIT High Pressure decay. Found an air leak at the Permeate valve. WO issued. Train 6 back to online. Tested two way radio's on site. No issues. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-18 | Georgina Water Treatment Plant | EAST | On site for station check, lab analysis, and weekly sampling (W11672853) Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Manual start clearwell recirculation pump. Reviewed SCADA trends. 10:24 Activate Keswick system duty 11:41 Took TW and raw water samples. 14:39 Call from ROC regarding GWTP Comm alarms caused UV start/stop sequence fault alarms. Deactivated Keswick system duty. 14:52 Unable to clear alarms. Notified ROC and Called Chris Scott, on-call PCS, for assistance. 15:05 Alarms cleared. | FLAG | stage2_low_confidence | 0.032596 | ML: above threshold (no LLM available) — 0.033 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.032596 | 0 | 0
2026-03 | 2026-03-06 | Georgina Water Treatment Plant | EAST | On site to repair crane control cable. | FLAG | stage2_low_confidence | 0.022006 | ML: above threshold (no LLM available) — 0.022 | repair [maintenance_action] | 0.022006 | 0 | 0
2026-03 | 2026-03-10 | Georgina Water Treatment Plant | EAST | On site to complete following work orders: W11646352 Air Dryer Check. W11648000 Compressed Air System Inspection. W11646363 Air Compressor Maintenance. W11702020 GAC Sampling W11652127 MIT Daily Filter Performance Review Reviewed MIT and daily filter performance on all trains - all passed. At 09:02 duty for the system was shut down in anticipation for network having work done on it. At 12:53 activated duty. GAC 4 has been sampled with no issues. No issues with work orders being completed.. | FLAG | stage2_low_confidence | 0.026406 | ML: above threshold (no LLM available) — 0.026 | sso [critical]; work order [maintenance_action] | 0.026406 | 0 | 0
2026-03 | 2026-03-18 | Georgina Water Treatment Plant | EAST | On site to complete station check. Completing work order of low lift pump inspection. No issues with work order. Reviewed MIT and daily filter performance on all trains - all passed. Comm alarm caused UVs to interlock received call from ROC at 14:41. Deactivated duty at 14:42. On going comm fail at the UVs causing them to be interlocked. Will be calling on call PCS Chris Scott to see if the issue can be resolved. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; alarm [control_system] | work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | Georgina Water Treatment Plant | EAST | Onsite to perform annual calibration. Informed ROC and operations. Plant offline. Devices were done as below : Backwash PITs, High lift Disch2 PIT, Utility PIT, Gen LIT, back pulse LITs. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, left the site. | FLAG | stage2_low_confidence | 0.013998 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system]; alarms [control_system] | 0.013998 | 0 | 0
2026-03 | 2026-03-16 | Georgina Water Treatment Plant | EAST | On site for station check and lab analysis. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Changed duty from BOGE air compressor to Kaiser air compressor. Triggered duty rotation for raw sample pumps. | FLAG | stage2_low_confidence | 0.034306 | ML: above threshold (no LLM available) — 0.034 | sso [critical] | 0.034306 | 0 | 0
2026-03 | 2026-03-25 | Georgina Water Treatment Plant | EAST | On site for MIT review, station check, lab analysis. Collected weekly micro samples (W11690826), GLIP samples. Data recorded in PWQ sheet. Reviewed MIT and daily filter performance on all trains - all passed. 09:35hrs: Adjusted Contact Tank 2 Cl2 Analyzer from 1.68mg/l to 1.53mg/l based on multiple CL2 grab residuals. 09:38hrs: Adjusted Contact Tank 1 Cl2 Analyzer from 1.68mg/l to 1.55mg/l based on multiple CL2 grab residuals. 10:55hrs: Collected all raw water samples. Collected Treated samples (Keswick Line) @ 11:10hrs. Cl2 grab residuals: FCL: 1.61mg/l TCL: 1.95mg/l 11:25hrs: Adjusted Keswick Fluoride reading from 0.77mg/l to 0.72mg/l based on in house lab analysis. 12:30hrs: Instrumentation on site for annual calibrations on GAC Turbidimeters, refer to instrumentation e-log entry. Sedimentation and Outfall to lake Cl2 Analyzer maintenance completed. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] | emergency [critical]; out of service [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 0
2026-03 | 2026-03-19 | Georgina Water Treatment Plant | EAST | ROC called regarding UV comm alarms and UV start/stop sequence fault alarms. Alarms occurred at 05:57. UV had been running for about 1 hour when the alarms came in Duty is active - Controlling ET is at 48% Cleared alarms - UV1 started. Same issue occurred yesterday afternoon. Will get PCs involved if the alarms come in again Will monitor | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all trains - all passed. Also on site to complete comprehensive housekeeping work orders. At 11:38 transmembrane pressure alarm came in on train 5 was able to clear it with no issues. Put all high lift pumps in manual off for instrumentation at 13:07. Completed a vial cleaning and replacement on GAC2 due to NTU not dropping below 0.199. Did all this between 13:30 and 13:50. At 14:12 put the hi lift pumps back to auto after instrumentation finished their work. No issues with work orders on site. | FLAG | stage2_low_confidence | 0.055059 | ML: above threshold (no LLM available) — 0.055 | work order [maintenance_action]; alarm [control_system] | 0.055059 | 0 | 0
2026-03 | 2026-03-20 | Georgina Water Treatment Plant | EAST | Onsite for annual calibrations Informed ROC and ops Plant offline Calibrated HLP PITs Informed ROC and ops Left site | FLAG | stage2_low_confidence | 0.0075587 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075587 | 0 | 0
2026-03 | 2026-03-21 | Georgina Water Treatment Plant | EAST | Train #7 had shutdown overnight on MIT low pressure decay failed alarm. It failed at a 7.66 kpa. Cleared alarms and initiated another MIT on train #7 @11:26. @11:27 - Activated duty 1 Low pressure passed - 5.19 kpa decay | FLAG | stage2_low_confidence | 0.0086462 | ML: above threshold (no LLM available) — 0.009 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0086462 | 0 | 0
2026-03 | 2026-03-25 | Georgina Water Treatment Plant | EAST | On site to help with getting site ready for tours tomorrow. Instrumentation currently on site to complete annual calibrations. | FLAG | stage2_low_confidence | 0.01844 | ML: above threshold (no LLM available) — 0.018 |  | 0.01844 | 0 | 0
2026-03 | 2026-03-26 | Georgina Water Treatment Plant | EAST | Onsite to continue with annual calibrations Informed ROC and operations Plant offline Completed Train # 2,3,5.6,7,8 LITs Cleared associated alarms Informed ROC and operations Left site | FLAG | stage2_low_confidence | 0.013053 | ML: above threshold (no LLM available) — 0.013 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.013053 | 0 | 0
2026-03 | 2026-03-22 | Georgina Water Treatment Plant | EAST | @11:08 - Activated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034376 | 0 | 0
2026-03 | 2026-03-16 | Georgina Water Treatment Plant | EAST | Started Duty 1 for Keswick at 07:45. Will monitor off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003358 | 0 | 0
2026-03 | 2026-03-06 | Georgina Water Treatment Plant | EAST | On site for station check and lab analysis. Verified basement chlorine analyzers. Adjusted Post clearwell free chlorine analyzer after three grab samples: Grab: 1.66 mg/L Analyzer: 1.93 mg/L Completed the following work orders: Chlorine analyzer maintenance - Permeate and CIP 12:55 Start back wash sequence on GAC 4: Open back wash drain valve, Open backwash recirculating valve, and backwash inlet valve. Start backwash pump 1, Open backwash pump 1 flow control valve to 25% for 2 mins. Increase flow control valve to 40% open for 7 mins, Reduce flow control valve to 25% open for 2 mins, Close backwash drain valve. 13:23 close flow control valve, shut off backwash pump 1, close recirculation valve, and close backwash inlet valve. Letting GAC filter settle. 13:40 open GAC4 inlet valve and filter to waste valve. 14:45 close GAC4 filter to waste valve, place effluent valve back in auto, and change filter setpoint back to in service. 13:30 Instrumentation team completed work on trains 4 and 5. Turned both trains back on. Will be working on train 2 and 3 next, placed both trains in off mode. 14:30 Instrumentation team completed work on trains 2 and 3, placed trains back on. 14:33 Activated system duty 14:38 Placed fluoride pumps back in auto. | FLAG | stage2_low_confidence | 0.05745 | ML: above threshold (no LLM available) — 0.057 | work order [maintenance_action] | 0.05745 | 0 | 0
2026-03 | 2026-03-19 | Georgina Water Treatment Plant | EAST | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. 9:40-13:20 GAC2 Backwash - Followed procedure for GAC backwash. Notified ROC that GAC2 placed OOS for the duration. Any Backwash and GAC2 alarms will be related to the procedure and will be assessed and reset when completed. 12:51 ROC called for UV1 and UV2 comm alarms, requested Christian V.B. to deactivate system duty. Reset Comm alarms. Called Chris S. to request assistance in determining why the comm alarms have occurred multiple times. Completed housekeeping work orders. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-27 | Georgina Water Treatment Plant | EAST | Onsite to continue with annual calibrations Informed ROC and operations Plant offline Completed: Train LITs 1, 4 and 8 Train header PITs 4, 3 and 2 Cleared associated alarms Informed operations and ROC No issues Left site | FLAG | stage2_low_confidence | 0.0091217 | ML: above threshold (no LLM available) — 0.009 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.0091217 | 0 | 0
2026-03 | 2026-03-09 | Newmarket Pinch Valves | WW-NORTH | Rotate duty?s on pinch valves Pinch valve # 2 now in duty 1 for the day 185kpa | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036871 | 0 | 0
2026-03 | 2026-03-10 | Newmarket Pinch Valves | WW-NORTH | Switch back to pinch valve 1 after 24hr rotation on 2. Pinch valve operation on 2 ok however the low pressure alarm will come in while duty is active | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065258 | 0 | 0
2026-03 | 2026-03-20 | Newmarket Pinch Valves | WW-NORTH | Onsite for CSE inspection Check air valves Inspect sump pit/ test float functionality | FLAG | stage2_low_confidence | 0.011351 | ML: above threshold (no LLM available) — 0.011 |  | 0.011351 | 0 | 0
2026-03 | 2026-03-29 | ROC General | ROC | Christian Van Beek signing in. Weather 10C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-29 | ROC General | ROC | Ethan U signing in Weather 0. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-29 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-28 | ROC General | ROC | Christian Van Beek creating a test log entry at the request of Jennifer Chung. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069174 | 0 | 0
2026-03 | 2026-03-29 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-28 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | Adeela Khan Signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | Ethan U signing in Weather 4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-31 | ROC General | ROC | Testing eLog | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050944 | 0 | 0
2026-03 | 2026-03-31 | ROC General | ROC | AUSS, Garrick from Ferguson Electric is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056018 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | AUSS - Theodore (AB) on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051608 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | KSSP - Drew from Ferguson finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058338 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | MTSP - Steve from LCD mechanical for maintenance on auto drain for compressed air system | FLAG | stage2_low_confidence | 0.0073016 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073016 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | Adeela Khan signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052508 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-31 | ROC General | ROC | SUSSHS, Chad S from Bell Canada is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005499 | 0 | 0
2026-03 | 2026-03-30 | ROC General | ROC | Christian Van Beek signing in. Weather: 18C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-31 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-31 | ROC General | ROC | NBSP - Ben from Property Services is on site for HVAC PM's | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059313 | 0 | 0
2026-03 | 2026-03-31 | ROC General | ROC | Ethan U signing in Weather 14. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-08 | ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | Angelica Chepiga signing in,weather -6C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | Christian Van Beek signing in. Weather: 2C and rain. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045651 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | KSETDP - Owen S from Asset management leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060754 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | MAPS - Dave from property services on site to work on an air handling system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064944 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | EGSSSC - Joe O from CPD on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052736 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | YDOC - Drew from Ferguson Electric on site for a generator TSSA inspection and test. Arthur L monitoring remotely. | FLAG | stage2_low_confidence | 0.0076654 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076654 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | SHSP - Steve B onsite for for clean up with electrical inspector SHSP - Steve B onsite for for clean up with elctrical inspector | FLAG | stage2_low_confidence | 0.0073128 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073128 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | GWTP - Derek S (contractor) attending site for pick up on some gear. Will be working on project for muscle control system throughout the year | FLAG | stage2_low_confidence | 0.0093103 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093103 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | KSSP - Garrick from Ferguson onsite running some pipe | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061524 | 0 | 0
2026-03 | 2026-03-06 | ROC General | ROC | KSSP- Garrick from Ferguson Electric is on site NMETYS- Dennis from Landmark is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056055 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | MKPSSA - Drew from Ferguson Electric on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055568 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | KSSP - Garrick from Ferguson finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059238 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | NMPSKC, Theodor from AB is leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057628 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | KSTKWP - Dominic from Honeywell on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054567 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | KSSSQW - Joe O on site to complete a warranty walkthrough. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059454 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | KSTKWP - Dominic from Honeywell leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059273 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | NBW3, Drew from Ferguson Electric is leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045562 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | NBW3, Drew from Ferguson Electric is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041878 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | NMTKKC - Theodore from ABPMC on site for TSSA generator inspection with no transfer to load. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069403 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | Ethan U signing in Weather -7. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | Adeela Khan signing in. Weather: 16C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004454 | 0 | 0
2026-03 | 2026-03-15 | ROC General | ROC | STRS48, STW56, STETBR - Security intrusion alarm. FMC will notify Corp security. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057109 | 0 | 0
2026-03 | 2026-03-15 | ROC General | ROC | STPSTL - Security intrusion alarm. FMC will notify Corp security. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070295 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | YDOC 9 - Jon from property services leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045765 | 0 | 0
2026-03 | 2026-03-15 | ROC General | ROC | Angelica Chepiga signing in,weather -4C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-15 | ROC General | ROC | NBSP - Ken from ITS on site for High-speed internet upgrade. Will attend NBETRS site after. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068845 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | NMETYS - Thomas from IM onsite for minor repairs | FLAG | stage2_low_confidence | 0.010762 | ML: above threshold (no LLM available) — 0.011 | repair [maintenance_action] | 0.010762 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | MKPSSA - Drew from Ferguson Electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060394 | 0 | 0
2026-03 | 2026-03-14 | ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | Adeela Khan signing in. Weather: 0C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044345 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | JDSS, Phil from AB is leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056353 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | Adeela Khan signing in. Weather: 0C and snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044729 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | GWTP - Evan from Hydro One (705 783 2728) is on site and is taking a look at the meter. Requests access to the gate. Called Joe M. who will let Evan in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058985 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | SUSP - David from property services on site to complete maintenance on an electrical heater. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069452 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | BLETNL - Dominic from Honeywell on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054568 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | KSSP - Garrick from Ferguson electric on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055882 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | LSSS - Emily from EME on site to collect samples. Emily requested that pump 6 be placed into duty 1. Made the necessary change. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062255 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | AUSS - Scott L from AIM leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057171 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | MTETNL - Dominic from Honeywell off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058337 | 0 | 0
2026-03 | 2026-03-06 | ROC General | ROC | Stouffville - Lane from town of Stouffville flushing zone 2 all day | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050063 | 0 | 0
2026-03 | 2026-03-08 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-15 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-07 | ROC General | ROC | Carter Dunn Signing In, 16D/Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041783 | 0 | 0
2026-03 | 2026-03-07 | ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | SECC- Johnathan from Property Services onsite for fire testing. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical] | fire [critical] |  | 1 | 0
2026-03 | 2026-03-15 | ROC General | ROC | Carter Dunn Signing in, 3D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-15 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-06 | ROC General | ROC | Ethan U singing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052194 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | BLETNL - Dominic from Honeywell leaving site. Heading to MTETNL. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064686 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | BLETNL - Sean from Stouffville water will be flushing in the Ballantrae Water System today. | FLAG | stage2_low_confidence | 0.0073464 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073464 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | AUSS - Scott from IAM on site for the tour. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055593 | 0 | 0
2026-03 | 2026-03-06 | ROC General | ROC | Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | GWTPLL - Joe O from CPD on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052692 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | KBSP - Drew from Ferguson Electric on site for pipe work. No alarms anticipated from this work. | FLAG | stage2_low_confidence | 0.0086344 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0086344 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | NMETYS - Carlos from landmark Municipal Services attended site to gain access. Carlos's security card is not working as intended and he will be contacting his York Region contact to fix it. Carlos noticed that the door to the tower opens freely. Contacted Security who will send a mobile operator to secure the site. Also informed Area operations. | FLAG | stage2_low_confidence | 0.04361 | ML: above threshold (no LLM available) — 0.044 | not working [equipment_failure] | 0.04361 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | NBSP - Dave from property services leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059948 | 0 | 0
2026-03 | 2026-03-07 | ROC General | ROC | Adam Button signing in 8C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041579 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | Christian Van Beek signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054296 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | KSTP - Theodore from AB onsite for measurements 9:19 - Finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035459 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | KSTP - Apurva from Honeywell leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058304 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | STETBR - Dominic from Honeywell on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054522 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | BLSS - Chris from property services on site to test the fire alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | KSSP - Drew from Ferguson Electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059815 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | KSSP - Drew from Ferguson onsite ESA inspector 11:54 - Drew will run generator temporarily | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038616 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-01 | ROC General | ROC | Connor Smith signing in -12 C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042384 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | VNET - Meaguel from YR police onsite for Monthly site visit | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063382 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | NBSP - Dave from property services on site to complete work on the diesel room exhaust fan. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069532 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | KSSP, Garrick from Ferguson Electric is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055988 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | QVW12 - Drew from Ferguson Electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045593 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | Pesticon Visiting Following Sites; NBSSJA, KCSSKR, KCETFS, KCETDS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065366 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | JDSS - Stephen from AB project. Generator back in auto and can run KSETDP - Will from Honeywell onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064595 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | NBSP - Dave from PS leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055858 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | GWTP- Chris from Property Services onsite to check out fire panel | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical] | fire [critical] |  | 1 | 0
2026-03 | 2026-03-03 | ROC General | ROC | Connor Smith signing in 1C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | Angelica Chepiga signing in, weather +7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-07 | ROC General | ROC | Forced corporate computer restart | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005639 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | STETBR- Dominic from Honeywell finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059789 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | Carter Dunn Signing In, -2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | KSSP - Garrick from Ferguson onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005659 | 0 | 0
2026-03 | 2026-03-07 | ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-06 | ROC General | ROC | Adam Button signing in 0C Raining | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041938 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | NMETYS - Junjie from CPD leaving site with Landmark contractors. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006471 | 0 | 0
2026-03 | 2026-03-01 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | KSSSQW - Joe O finished and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058229 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | Christian Van Beek signing in. Weather: 10C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | AUSS, Dave from Property services is leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060254 | 0 | 0
2026-03 | 2026-03-08 | ROC General | ROC | Adeela Khan signing in. Weather: 10C and sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004454 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | SUSP - David from property services leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006024 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | STRS48 - Dominic from Honeywell leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044947 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | Angelica Chepiga signing in, weather +7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | KSTP - Apurva from Honeywell on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053647 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | KSTP - Garrick from Ferguson Electric on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055885 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | RHPSPA - Dominic from Honeywell on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005456 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | RHPSPA - Dominic from Honeywell leaving site and heading to BLETNL. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065566 | 0 | 0
2026-03 | 2026-03-06 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-01 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | SEOC6/7 - Drew from Ferguson Leaving site and headed to YDOC for sticker placement. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053454 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | KSETDP, Dominic from honey well is leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059724 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | Carter Dunn Signing In, -2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | KBSP - Drew from Ferguson Electric on site for photos. Drew will be on site for a short period. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070273 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | STPSMR - Antonio from Torbear construction on site to complete some hot work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064878 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | Town of Stouffville - Corey from Stouffville informed they are flushing nineth line North of Hoover | FLAG | stage2_low_confidence | 0.0076535 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076535 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | KCETFS, Kingsley from Freedom Mobile is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055971 | 0 | 0
2026-03 | 2026-03-06 | ROC General | ROC | Carter Dunn Signing In, 1D/Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041599 | 0 | 0
2026-03 | 2026-03-08 | ROC General | ROC | Angelica Chepiga signing in, weather +3C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-14 | ROC General | ROC | Ethan U signing in Weather 0. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-15 | ROC General | ROC | MAPS - Intrusion alarm, FMC will notify Corp security. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066824 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | Carter Dunn Signing In, -7D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-15 | ROC General | ROC | STRS48/STPS48 - Intrusion alarm, FMC will notify Corp security. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052742 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | QVW12- Gerrick from Ferguson onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042826 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | SEOC - Drew from Ferguson Electric on site to complete a generator TSSA inspection and test. Arthur L monitoring remotely. | FLAG | stage2_low_confidence | 0.0079672 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079672 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-03 | ROC General | ROC | SEOC 6/7 Drew from Ferguson Electric on site to complete work on the local fuel transmitter. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052728 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | PVSS - Scott from IAM on site with Mike L for a tour of the facility. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063073 | 0 | 0
2026-03 | 2026-03-14 | ROC General | ROC | Carter Dunn Signing In. -3D/Snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042339 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | Christian Van Beek signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054296 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | Connor Smith signing in -1C windy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041936 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | BLW12 - Shahin with Torbear onsite for soldering work 416-4254-9527 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034852 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | NBW3 - Drew from Ferguson Electric will be testing the generator wit no transfer to load. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055098 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | KSTP - Drew from Ferguson electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059877 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | Angelica Chepiga signing in,weather +5C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-14 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | PVSS - Scott finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055279 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | Angelica Chepiga signing in, weather +4C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | Adeela Khan signing in. Weather: -7C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | AUSS- Phil from AB onsite. 14:13- Offsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030849 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | KSSP - Cody from Ferguson onsite for epoxy work | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059858 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | SHETCS - Rob from Chubb on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052531 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | NMTKKC- Jamie from ETO Engineering onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058536 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | Christine S visiting the following sites; JDSS, KSETP, KSSP, GRSSWA | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065926 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | RHAMF1, Eric from NAC on site, Fixed the Recirculation Pump 1/2 issue, reset alarms | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0064813 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | STPSMR - Drew from Ferguson Electric is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005601 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | MTSS - Andrew from Westlake construction called to inform that the gate was repaired and locked. | FLAG | stage2_low_confidence | 0.013369 | ML: above threshold (no LLM available) — 0.013 | repair [maintenance_action] | 0.013369 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | KSTP - Garrick from Ferguson electric leaving site, heading to KSSP. KSSP - Drew from Ferguson electric on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052506 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | Gluzen Ramos Ong signing in KSSP - Drew (Ferguson) onsite working on PAC panels, informed Artour L (PCS) will also be on site. Will follow up with Artour L. if alarms received | FLAG | stage2_low_confidence | 0.0090561 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0090561 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | KBSP- Phil from AB is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051824 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | Carter Dunn Signing In, 3D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | Angelica Chepiga signing in,weather -11C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043101 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | QVW12- Will M onsite for analyzer maintenance. Disregard alarms while onsite. *Wrong Book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.004851 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | JDSS - Drew from Ferguson electric on site. 16:00 Drew off site. AURSBS - Mark from Process optimization on site 15:30 Mark leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026049 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | Adeela Khan signing in. Weather: 8C and raining | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044658 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | 16:09 - KBSP - Theodore (AB Constr.) leaving site 17:20 - KSSP - Garrick (Ferguson) leaving Generator Bldg. Confirmed Armed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004504 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | HLETPR- Megsen from YRP onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055237 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | Connor Smith signing in 0C Snowy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041992 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | KBSP - Theodore from AB onsite working on fuel system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061456 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | GWTP- Derek from Maple Reinders onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057538 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | KSSSQW- Joe O CPD offsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054585 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | Pestacon visiting the following sites; NMETIB, NMETHW, NMETDD, NMSSBP, NMSSHS, NMW12, NMW15, NMETYS, NMPSKC, NMW136, NMTKBS, ANW23 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067305 | 0 | 0
2026-03 | 2026-03-21 | ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | AUSS - Dan T from ABPMC on site for piping work related to the generator fuel system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067298 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | NMETYS- Kevin from Yorknet onsite. 13:43- Offsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032036 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | KSSP - Christian from Ferguson Electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061193 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | SEOC67 - Dominic from Honeywell off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044258 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | Christian Van Beek signing in. Weather: 2C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | HLSSBS - Kevin K. (CPD) on site for site meeting Heading to QVSSSC, EGSSSC | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053193 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | KBSP- Steven from AB onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054736 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | KSSSQW - Joe O from CPD with contractor Tormont working on generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066238 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | KSSP - Phil from ABPMC on site to complete work in the generator room. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063141 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | JDSS- Drew from Ferguson onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055684 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | KSSP - Phil from AB on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051639 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | MARS- Chris from Property Services onsite for fire alarm testing | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-17 | ROC General | ROC | NMETHW - Kalid from AIM on site with contractors. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056752 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | MTSP- Dominic from Honeywell onsite. 08:35- Offsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032326 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | KBSP - Garrick from Ferguson electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060748 | 0 | 0
2026-03 | 2026-03-21 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | STRS48 - Drew from Ferguson electric on site and requested a fuel tank level reading. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050744 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | Adeela Khan signing in. Weather: -2C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | STPSMR - Drew from Ferguson Electric on site for tagging. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058685 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | KSSSQW - Joe O from CPD on site with Toromont to complete work on the generator starter. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006846 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | Carter Dunn Signing In, 0D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | KSSP - Drew from Ferguson electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059815 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | Connor Smith signing in -3C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00423 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | SEOC4, SEOC OCF, SEOC6/7, SEOC8 -Jonathan from Property services attending sites for Fire alarm testing. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-25 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | KSSP- Gerrick from Ferguson onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056436 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | Adeela Khan Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | SUSP - Steven T from CPD leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057467 | 0 | 0
2026-03 | 2026-03-22 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | KSSP - Garrick from Ferguson Electric is on site and will be entering the generator building. Garrick informed he will not be running the generator at this time | FLAG | stage2_low_confidence | 0.0094921 | ML: above threshold (no LLM available) — 0.009 |  | 0.0094921 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | KSSSQW- Joe O CPD Leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055545 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | KSTP - Hamid from ETO engineering leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059809 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | EGSSSC- Cameron from IT onsite troubleshooting modem | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061327 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | QVW12 - Mark from Process optimization team on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043586 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | SEOC OCF - Ben (PSB) finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053822 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | KBSP - Drew from Fergugon entering site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057545 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | SEOC67 - Dominic from Honeywell on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041393 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | Adeela Khan signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052508 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | Kingsley M restarting SCADA screens and Patriot | FLAG | stage2_low_confidence | 0.0076969 | ML: above threshold (no LLM available) — 0.008 | scada [control_system] | 0.0076969 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | NRETBR - Stephen from Newcort tech on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055214 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | STPSMR/TSRS48/STW12/STW3/STETTL/STETBR/BLETNL/STW56/BLW3, PCO Pest Control on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005054 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | KBSP - Theodore from ABPMC on site to complete a generator pressure test. The generator will be offline and unavailable during this test | FLAG | stage2_low_confidence | 0.0085082 | ML: above threshold (no LLM available) — 0.009 |  | 0.0085082 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | AUSS - Rory from PS testing fire alarm 8:43 - Leaving site | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-20 | ROC General | ROC | STRS48 - Drew from Ferguson onsite removing scrap metal onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048533 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | MKETFA, David from the RCMP is on site, moving some of his equipment/antenna | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064381 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | KBSP- Theodore from AB Offsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055677 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | NMETYS - Freedom Mobile contractor on site. 12:20 Off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031577 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | KSSP - Gerrick from Ferguson Electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060662 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | QVW12- Drew from Ferguson onsite. 15:06- Offsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031754 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | NMSSHS- Joe O CPD onsite. 10:30 Offsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003067 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | EGSSSC - Kevin K from CPD on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053269 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | Connor Smith signing in -12C Windy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042119 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | KSSP - Garrick from Ferguson Electric on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055882 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | Connor Smith signing in 9C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | HLPSYS- Dominic from Honeywell off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058021 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | EGSSSC - Kevin from CPD off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056316 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | KBSP - Teodore from AB leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056702 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | JDSS- Drew from Ferguson offsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055747 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | SEOC OCF - Ben Han from property services on site to work on an air handling unit. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066745 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | NBSSJA - Dave W from property services leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061142 | 0 | 0
2026-03 | 2026-03-21 | ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | KSSP- Gerrick from Ferguson offsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005675 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | BLSS - Mohsen from CPD on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052426 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | Carter D Signing In, 4D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041331 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | Angelica Chepiga signing in,weather -7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | KSTP- Gerrick from Ferguson onsite. 08:10- Gerrick informed that door of generator building was wide open when he arrived. Informed Security and they will send someone to check it out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059931 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | MKPSSA- Drew from Ferguson onsite. 14:28- Offsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031916 | 0 | 0
2026-03 | 2026-03-22 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | QVW34- Drew from Ferguson onsite. 15:45- Offsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031761 | 0 | 0
2026-03 | 2026-03-21 | ROC General | ROC | Christian Van Beek signing in. Weather: 3C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | QVW12- Rory from Property Services onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044265 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | STPSTL- Drew from Ferguson onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056179 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | STRS48- Drew from Ferguson offsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042854 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | KBSP- Drew from Ferguson leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057016 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | QVW12 - Mark S from process optimization leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046711 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | NMSSBP- Pat from Property Services onsite for fire testing. 087:18- Finished onsite. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical] | fire [critical] |  | 1 | 0
2026-03 | 2026-03-25 | ROC General | ROC | STRS48- Drew from Ferguson onsite working on generator. May have to shut it down and trigger some alarms. | FLAG | stage2_low_confidence | 0.0075795 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0075795 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | SEOC Shaft 6/7 - Jeff from Keyshack on site to work on a fan room door. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004827 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | QVW12 - Rory from Property Services is on site to take a look at a broken door | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049705 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | KSSP - Cody from Ferguson electric on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055065 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | RHRSTR - Jonathan from Property Services is on site for a sprinkler flow test | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064449 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | Connor Smith signing in 3C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041757 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | KCETDS- Kalid from IM offsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055469 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | YDOC- Ben from Property Services onsite. 13:49- Offsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033033 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | Christian Van Beek signing in. Weather: -2C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-22 | ROC General | ROC | Ethan U signing in Weather 5. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-25 | ROC General | ROC | SEOC67- Kevin from Yorknet offsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043053 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | HLW2 - Treated free chlorine hihi HLW1 - Combined chlorine lo. Alarms came in during start up. Readings came back within range and cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0065279 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | HLW1 - Treated free chlorine hihi alarm. Checked site, well is manual/off no water being directed to users. Trending shows a variable reading of the treated free chlorine and treated combined chlorine. Possible analyzer issue. Continuing to monitor. | FLAG | stage2_low_confidence | 0.012804 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.012804 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | KSTP - Raw water turbidity fault. Disregard as per shift report | FLAG | stage2_low_confidence | 0.010156 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.010156 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | HLETYS - Noted the inlet tower flow has dropped below the threshold to activate the chemical rechlorination system. Increasing flow setpoint at HLW2 FCV, SCADA will not accept command. Contacted Cole W who assisted with the the adjustment of the flow setpoint. Increased flow from 20L/s to 30L/s in 5L/s increments. #consult | FLAG | stage2_low_confidence | 0.014628 | ML: above threshold (no LLM available) — 0.015 | scada [control_system] | 0.014628 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Pouvia) and requested two pumps be activated to fill the reservoir. | FLAG | stage2_low_confidence | 0.0075814 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075814 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | NMW12 - Treated combined and treated total chlorine lolo alarms. Checked site, wells are not running no water being directed to users. Trending shows an abnormal dip of the treated total and combined chlorine readings which recovered within two reading intervals. SHTP - Filter 3 post rinse NIT high alarm. Checked site, plant is active. Shift report states this alarm can be reset once by remote operators. Reset alarm. | FLAG | stage2_low_confidence | 0.036636 | ML: above threshold (no LLM available) — 0.037 | not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.036636 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | VNRSKS - Activated duty 1 to drawdown MARS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044607 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | STW12/STW3 - Place well 2 & 3 man/on for Zone 1 tower KSTP - Filter 2 backwash OOS. Informed Phil D, will investigate Consult ARPS - Jerry (Peel) informed they are switching from pump 7 to pump 5. May experience pressure fluctuation temporarily | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | NMW15 - Chlorinator 1 fail to close, interlocked well. Place well in man/off as duty nearing stop as to not let well run at this point. Able to clear alarm. Will place back in auto after duty stop | FLAG | stage2_low_confidence | 0.010131 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010131 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | JFPS- Deactivated duty in preparation for Maple to Jefferson feed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065395 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | KCETDS - Metering chamber flood alarm. No note on disregard list. Previous log entries for this alarm from this month state that this alarm is a disregard overnight and can be handled by operators in the morning. Sent email to OCO. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | GWTP LL - low lift pump 4 hydraulic valve fail to close alarm. Shift report states this alarm can be reset and the valve returned to service. Able to reset alarm. | FLAG | stage2_low_confidence | 0.0086896 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086896 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto mode as per the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0062985 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | QVW34 - Chlorine gas leak, CL2 emergency valve closure active. Informed Joe D of update. Placed well 3 man/off for remainder of weekend Consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; gas leak [critical]; leak [infrastructure] | emergency [critical]; gas leak [critical]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | MKRSEM- Called Toronto and requested pumps off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059819 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather 10C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | HLW1 - Treated free chlorine climbed following the ammonia pump rotation. Rotated back to ammonia pump 1. Noted that the free chlorine hihi alarm is currently deactivated. Contacted Cole W to ask if the treated free chlorine hihi alarm is disabled for a reason, Cole W was unaware of this and directed to enable the alarm. Treated free chlorine reading is dropping with ammonia pump 2 active. May see a drop of combined chlorine reading on the HLETYS analyzer. #consult | FLAG | stage2_low_confidence | 0.024782 | ML: above threshold (no LLM available) — 0.025 | alarm [control_system] | 0.024782 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | RHRSTR - Activate duty 1 AURSBS - Deactivate duty 1 to lessen demand for MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043646 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | QVW34 - Joe D found no leaks, placed well back in auto as possible faulty reading on gas detector. Will investigate further tomorrow. Leaving site | FLAG | stage2_low_confidence | 0.021397 | ML: above threshold (no LLM available) — 0.021 | fault [equipment_failure]; leak [infrastructure] | 0.021397 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two VNPS pumps to one VNPS pump and one MAPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0072194 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | HLW2 - Silicate pump 1 leak and uncommanded stop alarm. Checked site, duty 1 rotated to silicate pump 2 which activated. Will monitor system for containment and abnormal operation alarms. | FLAG | stage2_low_confidence | 0.024473 | ML: above threshold (no LLM available) — 0.024 | alarm [control_system]; alarms [control_system]; leak [infrastructure]; containment [safety] | 0.024473 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | NMVCBA- Placed valve in manual 20L/s to assist in keeping NMETIB and NMETHW offset. 00:53- Placed valve back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044337 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | HLW1 - Treated free chlorine reading is still above the hihi alarm setpoint. Deactivated HLW1 in manual mode. HLW2 and HLW2FCV still running. Will monitor system to ensure tower still fills without HLW1. | FLAG | stage2_low_confidence | 0.010351 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010351 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to two MAPS pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060547 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | HLW1 - Treated free chlorine hi alarm. Checked site, well is active. Trending shows that the treated free chlorine is reading higher than normal the last two run cycles. Swapped ammonia tank duties and monitored. 18:45 - HLW1 - Treated free chlorine reading still hi. Rotated ammonia pump duty. | FLAG | stage2_low_confidence | 0.0091796 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0091796 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | Connor Smith signing in 1C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041757 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | QVW34 - Chlorine gas leak hihi, CL2 emergency valve closure activity. Informed Joe D of outstanding alarm and ppm reading going up. Joe will take a look on SCADA 10:49 - Joe D placed wells 3 & 4 man/off for now, will head out later to address issue w Phil D, gas level went down now chlorinators are isolated. CMU = 11765263 | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; gas leak [critical]; scada [control_system]; alarm [control_system]; leak [infrastructure] | emergency [critical]; gas leak [critical]; scada [control_system]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | MARS- Cell1(North) Lvl Lo Alarm VNRSKS- Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043441 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | AURSBS - Activated duty 1 to fill the reservoir. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045715 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Pouria) and requested they stop flow to MKRSEM | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068665 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Ethan U signing in Weather 4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | AURSBS - Activated duty 1 to drawdown MARS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044591 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | NBW2 - Place well back in auto as noted in shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047609 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Gluzen Ramos Ong signing in BVPS - Dan B. and Kyle R. doing generator load test. Informed will not be transferring or losing power to station, pumps unaffected. MKETFA - Andrew (Toronto Water) testing PRV to ET. Duty currently active, about halfway through cycle. Monitoring | FLAG | stage2_low_confidence | 0.0082418 | ML: above threshold (no LLM available) — 0.008 |  | 0.0082418 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | 08:44 - HLW2 - Tim H., Benson S., Adeela K., Ethan U., on site for cylinder change 08:56 - NBW2 - Jacob M. with GFL on site for silicate removal. Duty just deactivated and well in local off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058246 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | RHRSTR - Deactivated duty 1 to prevent overfilling in low morning demand. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051222 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | SHTP - Filter 3 Post Rinse NIT High alarm came in. Ack/reset as per shift repot 07:24 - Alarm came back in. Spoke to Cole W. who directed to ack/reset alarm again but to let him know if alarm comes back in 07:45: Alarm came back in. Spoke to Cole W. who directed to initiate a backwash and someone will attend site today for a turbidimeter clean. Backwash has been initiated | FLAG | stage2_low_confidence | 0.0094899 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0094899 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | MARS - Tegbeer from OCWA called to inform that he will be completing the daily pump change. Will be going from pump 6 to 7 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064793 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | GWTP - Ricardo L, Parth P. and Eric S. are on site for annual calibration | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063859 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | GWTP - UV reactor 2 intensity lo. Checking site reading came back within range GWTP - GAC 4 flow control valve deviation alarm. Disregard as per shift report VNP8 - Duty shows OOS, place pump back man/off | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | BLW3 - working on chemical train 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042823 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Adeela Khan signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052508 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | HLW1 - Combined Chlorine LoLo. Ongoing WM break. Well is man/off and water is not being directed to users. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059722 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | HLW1 - Tim H onsite working on silicate and pump GWTP - Joe M onsite for GAC 1 backwash | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045943 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | BVPS - Dan B. and Kyle R. are on site for generator maintenance and will be placing the generator on/off throughout the day. Operations will not be affected. | FLAG | stage2_low_confidence | 0.009394 | ML: above threshold (no LLM available) — 0.009 |  | 0.009394 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | NMTKBS, Outlet Flow OOR/Fault and hi flow alarm, contacted Jason G but no response, left a voice message, will call him back within 5 minutes again | FLAG | stage2_low_confidence | 0.01519 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system] | 0.01519 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | RHRSTR - Deactivated duty 1 to avoid overfilling during low demand morning period. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053441 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | EGMCRW - PAC Control panel power failure alarm. Checked site, operations appear normal. Trending shows no interruptions to data collection. Unable to clear alarm. Will email area operations. | FLAG | stage2_low_confidence | 0.023992 | ML: above threshold (no LLM available) — 0.024 | failure [equipment_failure]; alarm [control_system] | 0.023992 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | NMVCBA/NMVCIB - Reverted setpoints back to 40L/s and 80 L/s respectively NMETIB - Deactivated duty to help offset with NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045183 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from one VNPS and one MAPS to two MAPS pumps to increase the demand on MARS. | FLAG | stage2_low_confidence | 0.0079325 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079325 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | MKVCMM - Site power failure alarm and PAC control panel power failure alarm. Checked site, operations appear normal. Able to clear alarms. | FLAG | stage2_low_confidence | 0.018925 | ML: above threshold (no LLM available) — 0.019 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.018925 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | AUW57 - Influent free chlorine hihi. Checked site, Well recently started, trending shows a spike of the influent free chlorine reading which returned to normal range within two reading intervals. Reset alarms, | FLAG | stage2_low_confidence | 0.012244 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012244 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Keswick - Derek from Aquazition will be flushing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006022 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | STETBR - Tower low level alarm. Delaying the start of STW12 and STW3 until the duty at STETBR begins. STETTL has been overfilled through the morning by flow from STETBR to STETL through the flow control valve. Day shift operators will activate STW12 and STW3 when STETTL begins to drain. | FLAG | stage2_low_confidence | 0.015447 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.015447 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | HLETYS - Outlet flow hihi alarm. Checked site, tower is draining and system duty is not active. Trending shows three abnormal spikes of the outlet flow reading. It is possible that local municipality operators are completing spring hydrant flushing. Will monitor. | FLAG | stage2_low_confidence | 0.018127 | ML: above threshold (no LLM available) — 0.018 | alarm [control_system] | 0.018127 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | HLETYS - PAC control panel pwoer failure alarm. Checked site, tower is currently filling. Chemical system shut down during the initial power failure resulting in a post injection combined chlorine low alarm. Not able to reset power related alarms. Informed Cole W during initial call for SHTP. ANW23 Generator running status alarm and discharge pressure low and lolo alarms. Checked site, no duty 1 assigned to pumps. Re-applied duties. Trending shows that the distribution system pressure has recovered. Generator running alarm outstanding. Will monitor. HLPSYS - Generator running alarm. Checked site, pumps are active, normal operations. | FLAG | stage2_low_confidence | 0.071101 | ML: above threshold (no LLM available) — 0.071 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.071101 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | MKRSEM - PAC Control panel power fail alarm. Checked site, operations appear normal. Reservoir is filling from Toronto COTFA pumps. Trending not impacted. | FLAG | stage2_low_confidence | 0.010864 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010864 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | HLW1 and HLW2 - HLW1 and HLW2 to HLETYS communication failure alarms. Checked site, wells have interlocked. Wells were active when the alarms triggered. Placed the wells manual/off to prevent activation as the tower is very close to duty stop. Cole W called to state he is on the way to the HLETYS tower to check the system during the power fail. Created CMU5#W11768997 #CMU5 | FLAG | stage2_low_confidence | 0.036453 | ML: above threshold (no LLM available) — 0.036 | failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system] | 0.036453 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | EGSSSC - recirculation loop flow low and lowlow alarms. Flow control valve fault alarms and recirculation mode failure alarm. Station still operating, wet well cycling. Able to reset valve faults and recirculation flow alarms. Will monitor. *wrong book* | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | HLW2 - Ammonia pump 1 fault alarm and treated free chlorine hihi alarm. Checked site, well is currently active. Ammonia pump duty 1 rotated to ammonia pump 2 which is active. Treated free chlorine spiked following the ammonia pump fault. Able to clear the fault alarm. Will monitor the free chlorine reading. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; pump fault [infrastructure] | fault [equipment_failure]; alarm [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | STW12/STW3 - Man/start both well 2 & 3 for zone 1 fill | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047213 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | GWTP - Low lift pump 3 uncommanded stop alarm. Checked site, plant is active. Low lift pump 2 currently running in duty 1. Reset alarm. | FLAG | stage2_low_confidence | 0.0076021 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076021 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | MKRSEM - Low level alarm. Called Toronto Water (Zoran) and requested they activate two pumps to push flow to MKRSEM. | FLAG | stage2_low_confidence | 0.0091365 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0091365 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | STW3 - Effluent Free Chlorine LoLo Switch alarm came in. Well is not running and water is not being directed to users | FLAG | stage2_low_confidence | 0.013164 | ML: above threshold (no LLM available) — 0.013 | not running [equipment_failure]; alarm [control_system] | 0.013164 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | HLETYS - CMU5 for historian heartbeat alarm from earlier W11769421 #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0041204 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | AUPSOH - Kinglsey M. called to inform that he will be working on the OIT and will receive a historian heartbeat alarm. Operations will not be affected | FLAG | stage2_low_confidence | 0.010686 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010686 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | AUETOH - Parth P. Ricardo L. and Eric S. are on site for a flowmeter installation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066335 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | AUPSRR - Kinglsey M. called back to inform that he will be restarting the OIT and will trigger a historian heartbeat. Operations will not be affected | FLAG | stage2_low_confidence | 0.0096049 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096049 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | MARS - Cell 1 Level Lo alarm came in. Deactivated duty 1 at AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054923 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: 18C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | MTW3 - Emergency Eyewash Flow Switch Alarm came in. Called Travis W. who informed he was cleaning the station and triggered the alarm. Travis will try to clear on site but if it does not clear, Travis would like a call back | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system] | emergency [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055122 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | YWS + NYWS Normal HLW2 - Downstream pressure hihi alarm. Checked site, system duty is active and tower is filling. Flow setpoints for the HLW2 FCV were changed yesterday to accommodate the loss of HLW1. HLW1 is back in service today but the flow setpoint was not reverted. Waited for the HLW2 FCV to close and then reverted the flow setpoint from 30L/s back to 20L/s and cleared alarm. Monitored valve opening. | FLAG | stage2_low_confidence | 0.018048 | ML: above threshold (no LLM available) — 0.018 | alarm [control_system] | 0.018048 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | GWTP, Contact Chamber 2 Cl2 lo alarm, notified Joe M, he is looking into it 12:55, Joe M called directed to disregard fluoride lo alarm, he has placed both fluoride pumps in man/off at the moment | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0056603 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | MTETNL - Travis W. called to inform that he is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058165 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | VNPSCD - Chlorine System Failure and Scrubber Gas Leak alarms came in. Checked site. Chlorine system is interlocked. Called Benson S. who will take a look 12:31 - Due to this Chlorine System Failure, switched back to MAPS PD7 for VNRSKS fill cycle 12:40 - MARS - Due to VNRSKS about to start up, Called Toronto Water (Brett) and requested increased flow to reservoir | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; failure [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | gas leak [critical]; failure [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | BVPS - Activated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040663 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Adeela Khan Signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | Toronto Water - Gary T. called to inform of a sodium adverse. Notified Dean L. Zahra K. and Central and East Water. Jeremy H. forwarded AWQI forms to areas and the City of Vaughan. AWQI 171877 Sodium Adverse Occurred at the Dufferin Reservoir Date/Time ? Mar/16 2026 12:00 Sodium levels = 20.5 mg/L AWQI 171876 Sodium Adverse Occurred at the Keele Reservoir Date/Time ? Mar/16 2026 13:30 Sodium 27.5 mg/L | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003157 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | HLW1 - Treated free chlorine hihi alarm. Checked site, well recently activated to fill the system. Trending shows the treated free chlorine reading is higher the last few run cycles. Will monitor site to determine if the reading will drop. | FLAG | stage2_low_confidence | 0.012219 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.012219 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | HLW2 - Downstream pressure hihi alarm. HLW2 FCV closing due to alarm. Tower almost finished fill cycle, system pressure is naturally high. Will address this when system hydro failures have been addressed. | FLAG | stage2_low_confidence | 0.01961 | ML: above threshold (no LLM available) — 0.02 | failure [equipment_failure]; alarm [control_system] | 0.01961 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | VNPSCD - Called Benson S. for an update. Benson informed that he cleared alarms and monitored site. | FLAG | stage2_low_confidence | 0.0093695 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0093695 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | HLETYS - Noticed all chem pumps were left man/off. Nothing noted in elogbook at the site or shift report. Called Cole W to confirm any abnormalities that cause chem pumps left off as i see post-inj total is at lo level. Placed all chem pumps back in auto Consult | FLAG | stage2_low_confidence | 0.013594 | ML: above threshold (no LLM available) — 0.014 |  | 0.013594 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | Gluzen Ramos Ong signing in AUPSRR - Kingsley M. working on OIT. Pumps currently not active, but 1% away from starting. Placed man/off until work complete MAPS - Talha H. working on OIT panel, no expected comm disruptions or alarms | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0062953 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | NBET - Rob P. is on site to complete Pm's | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055148 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | BVPS, Duty was activated however pump 3 was failing to open due to a suction valve failure, no alarms present just the interlock, rotated pump duty so pump 3 is in D2 and pump 4 is in D1. Change priority so pump 4 has 1 priority. Notified Patrick F, he will attend site to look into the issue | FLAG | stage2_low_confidence | 0.03425 | ML: above threshold (no LLM available) — 0.034 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.03425 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | NBET27, Rob P on site doing work orders, testing level alarms/temp alarms/sump alarms | FLAG | stage2_low_confidence | 0.011947 | ML: above threshold (no LLM available) — 0.012 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.011947 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | MAPS PD7, Placed pump 2/3 man/off VNPS PD7, Placed pump 1 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034516 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | KSTP, Cl2 Emerg Vlv Closure Sys Fault/Active, notified Jerry Z, he will look into it | FLAG | stage2_low_confidence | 0.0083274 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0083274 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | BVPS - Dan B. called to request to deactivate duty so he can switch over to generator power for a test run. Dan informed he confirmed with Dan Z. and Jack P. Deactivated duty 1 at BVPS 13:43 - Placed pumps in man/off. During transfer, Discharge Total/Free Chlorine OOR and multiple suction VC fault alarms. Informed Patrick F. who is headed to site. CMU5 Created W11769868 #CMU5 | FLAG | stage2_low_confidence | 0.018766 | ML: above threshold (no LLM available) — 0.019 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.018766 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | YWS + NYWS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038512 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | NMTKBS - Hi outlet flows. Called Ben H. who informed there is a WM break in the Town of Newmarket. Ben informed that he contacted the Town of Newmarket and operator has been dispatched. Ben also informed that an YR operator will also attend site 13:46 - Jason G. called back to inform that Town of Newmarket was able to isolate their main and NMTKBS is filling again | FLAG | stage2_low_confidence | 0.011057 | ML: above threshold (no LLM available) — 0.011 |  | 0.011057 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | SHTP/SHETCS, Power Outage, a blip occurred on both sites, Plant was running when the blip occurred, Plant shutdown. All alarms were able to be cleared, notified Cole W of the power outage on site consult | FLAG | stage2_low_confidence | 0.010064 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010064 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | MARS - Lo Level alarms came in. Deactivated duty 1 at AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0061717 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | VNPSAP, Tim H on site, testing low temp and flood alarm. HLETYS, Tower is flat lining, contacted Artour L he is looking into it NMETIB, Historian Heartbeat Alarm, notified Artour L, he is looking into it | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | MKRSEM - Request (Zoran) TO to run 2 pumps MARS - Request TO to go back to regular flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046138 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | STW12/STW3 - Place well 1 & 3 back in auto as Zone 1 finished filling | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050713 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | MAPS PD7, Placed pumps 2/3 man/off VNPS PD7, Placed pumps 1/3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035045 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | JSPS - Jerry Z finished at site, pumps restored. Informed of generator running at QVW34, okay to leave running for night. Will monitor. Infomred NMW15 man/off VNP7 - place remainder pumps man/off MAP8 - Place pump 3 auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070349 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | QVW34 - Combined Chlorine Hi and Effluent Free Chlorine hi alarms came in. Checked site. Well is man/on. Called Ben H. who informed he is running the site in manual due to a high turbidity. Ben informed that if the well locks out, it can be left man/off for the night | FLAG | stage2_low_confidence | 0.016189 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system]; alarms [control_system] | 0.016189 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | AUPSRR - Placed pumps back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056737 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | HLETYS, Rick L/Parth P finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005404 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | JFPS - WPS gen xfer switch, WPS pumps 2 & 3 fail to start. Unable to clear alarm as pump fail to start again. Pump 4 not comin on with duty. Ran in man/on as pump 1-3 fail to start. Infomred Jerry Z, will attend site CMU = 11770073 AUMCBS - Control panel power fail. Status went to normal RHRSTR - Site power fail alarm, control panel power failure. VNP8 - PROC sump pump 1 & 2 fault, able to clear alarm RHPSPA - Hydro power failure, able to clear HLW2 FCV2 - Cole W requested FCV2 back in duty 1 & monitor start up for any pressure or flow alarms. Will place well 2 back in duty 1 as well shortly after as requested Downstream pressure or no flow | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | AURSBS, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040354 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | NMETIB - Historian Heartbeat Alarm came in. Called Artour L. who will take a look | FLAG | stage2_low_confidence | 0.007735 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.007735 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | VNETAG, Tim H directed to call him if the hi/lo level alarms come in on site | FLAG | stage2_low_confidence | 0.0083017 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0083017 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | QVW34 - RIO control panel power failure, PAC control panel power failure. Generator running. Control panel power failure alarms cleared right away, generator running, will monitor site | FLAG | stage2_low_confidence | 0.020562 | ML: above threshold (no LLM available) — 0.021 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.020562 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | NMW136 - Well not avialbel, well 13 uncmd stop, able to reset. NMW15 - Well 15 VFD fault. left man/off | FLAG | stage2_low_confidence | 0.0077907 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0077907 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | BVPS, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039622 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | Ethan U signing in Weather 14. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | Carter Dunn signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | GWTP- ZW1 Permeate Pump Uncommanded Stop, Shutdown. Notified Joe M. He will look into it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053811 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | JFPS- Ernie H onsite. Requested to run Pump 1 in manual. Placed man/on. Placed pumps 3,4 in manual so would not start up in duty. Pump 2 already man/off. 11:51- Ernie H requested to stop pump and place back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070453 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | *Wrong Book Entry* | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052685 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | NMTKKC - Ammonia Pump 1 failed to start alarm. Ammonia pump 1 faulting consistently on activation. Checked site, duty 1 rotated to ammonia pump 2 which is operating normally. Spoke with Joe W who stated that the ammonia pump 1 can be placed into manual off and he will inform the rest of area operations. Leaving alarm outstanding as there is a work order in place to have the pump inspected and fixed. | FLAG | stage2_low_confidence | 0.088715 | ML: above threshold (no LLM available) — 0.089 | fault [equipment_failure]; faulting [equipment_failure]; failed [equipment_failure]; work order [maintenance_action]; alarm [control_system] | 0.088715 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MKETFA - Patrick F onsite testing low temp, working on LIT, and valve exercise. Requested TO (Peter) to stop pumping for valve work 12:02 - Request TO (Peter) to put pumps back to normal operations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063857 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | KSTP - Settl water Turbidity Hi alarm. Disregard alarm until morning as per Joe M. # Consult | FLAG | stage2_low_confidence | 0.0081482 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081482 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MKRSEM- Called Toronto and requested both pumps off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061203 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | MKRSEM - Called Toronto water (Zoran) and requested stop filling Res. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066203 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | GWTP- Train 4 turbidity OOR/ fault alarms came in. Notified Joe M. Parth P is performing annual calibrations on trains 4/5 | FLAG | stage2_low_confidence | 0.013072 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.013072 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | RHMCMD - Man/open 100% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040508 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NMW12 - Silicate tank 1 level lolo alarm. Checked site, well is active and the silicate pumps have interlocked on the lolo level alarm. Deactivated duty 1 for NMTKKC to shut down the wells and called Joe D to inform. Joe D stated that Jason G is completing the Silicate top ups today. Will contact Jason G and request he visit NMW12 asap. | FLAG | stage2_low_confidence | 0.019562 | ML: above threshold (no LLM available) — 0.02 | alarm [control_system] | 0.019562 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | VNPS PD7- Placed pump 3 in manual MAPS PD7- Placed pump 2 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041641 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | MKPSSA - Danielle Z called and requested that the pumps at MKPSSA be exercised. MKRSMR duty 1 is almost active, called Toronto Water and requested they activate the duty early for MKRSMR. When the valves have rotated and the flow from Toronto has started, will exercise each pump at MKPSSA individually for fifteen minutes. | FLAG | stage2_low_confidence | 0.016512 | ML: above threshold (no LLM available) — 0.017 |  | 0.016512 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | RHRSTR/VNPS - Benson S on site for station checks and requested that the duty 1 for RHRSTR be activated to initiate flow into the reservoir. Activated duty 1 and monitored BVPS pump start. | FLAG | stage2_low_confidence | 0.0082128 | ML: above threshold (no LLM available) — 0.008 |  | 0.0082128 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | QVW34 - Treated total chlorine OOR, lolo alarm. Called Donald M confirming he is onsite. Ernie H replacing analyzer, taking out total. Wells local off isolated. | FLAG | stage2_low_confidence | 0.0084428 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0084428 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | STW12- Placed well 1 back into auto STW3- Placed well back into auto. STETBR Fill cycle complete | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047685 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | STRS48 - High lift pump 1 fail to stop alarm. Checked site, system duty is not active but the pump is still pushing flow. Placed the pump in manual mode and tried to stop it. The pump remained on. Contacted Jack P who will attend site. Ian W from PCS completed OIT work at this site earlier today. Jack P requested that Ian be contacted to have him check whether the previous work may have impacted the SCADA logic for the high lift pump. Contacted Ian W who will check the system. 13:34 - STRS48 - jack P attended site and requested a CMU5. Created CMU5#W11722310 #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system] | scada [control_system]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | GWTP - High lift pump 2 emergency stop alarm. Joe M called to inform that he triggered the high lift pump 2 emergency stop. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system] | emergency [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NBW2 - Jake M finished and leaving site. Jake directed to leave the well running in manual mode until 16:00. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050618 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP - Sutton header fluoride low alarm. Checked site, Sutton PRV is not open no flow into Sutton tower system. Trending shows the fluoride level dipped earlier in the morning and stayed low but is starting to recover. Will monitor site to determine if the value will recover before duty starts for SUETDR. | FLAG | stage2_low_confidence | 0.022066 | ML: above threshold (no LLM available) — 0.022 | alarm [control_system] | 0.022066 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP - Joe M onsite working on GAC2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042999 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | Connor Smith signing in 3 C Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041948 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | JFRS - Sean P outside valve house for valve actuator work | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063349 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | KSTP - CO2 adjusted pH LoLo alarm. Checked site, high lift pumps not active, plant not active and low lift pumps interlocked on the alarm. Trending indicates that there was a small dip of the adjusted pH value which is slowly recovering. Reset alarm when it passed the alarm setpoint. | FLAG | stage2_low_confidence | 0.015193 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.015193 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | HLETYS - Tower Mixer VFD Fault alarm. Spoke with Cole W who stated that Tyler CS from maintenance will be attending site. | FLAG | stage2_low_confidence | 0.017646 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.017646 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | KSTP - Jason G on site, draining Filter 1 for manual cleaning. Filter 1 off for the night. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052606 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | VNPSAP - Aaron CM from PCS called to inform he will be completing a reboot of the cellular modem for this location. Aaron stated the work would be best completed with pumps off. Deactivated the tower duty at VNETAG and confirmed pumps are off and the valve is closed before informing Aaron they can move forward with the reboot. | FLAG | stage2_low_confidence | 0.02218 | ML: above threshold (no LLM available) — 0.022 |  | 0.02218 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to one MAPS pump and one VNPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065724 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA Report | FLAG | stage2_low_confidence | 0.013702 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.013702 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | VNPSAP/VNETAG, Aaron M from PCS is finished working on the signal on site, Trends for both sites are normal | FLAG | stage2_low_confidence | 0.0073897 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073897 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | GWTP- Joe M requested to activate duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057362 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MAPSN1 SCADA Server Reset, Kingsley M called, will be resetting the server at 09:30 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0057681 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | MARS - High level alarm. Activated AURSRS duty 1 to draw down the reservoir. YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0042601 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | ARPS - Sam from Peel/OCWA control room called to inform that there is an operator changing the reagents for the chemical analyzer at ARPS and that he will be making the daily pump rotation at ARPS. No impact to YWS expected. | FLAG | stage2_low_confidence | 0.013636 | ML: above threshold (no LLM available) — 0.014 |  | 0.013636 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | *WRONG BOOK ENTRY* | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052685 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | QVW34 - PAC Communication failure alarm came in. Checked site. Site came back within 2 mins and alarms cleared. Trending is okay | FLAG | stage2_low_confidence | 0.013741 | ML: above threshold (no LLM available) — 0.014 | failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system] | 0.013741 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | GWTP- Eric S and Parth P on site for calibrations. Will speak with OPS on site before starting work RHRSTR- Benson S on site to do station checks. Req BVPS to be activated. Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067575 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | NMETHW- Activated D1 at 45% to offset from NMETIB as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050115 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | RHPSPA - Generator Warning alarm came in. Checked site. Site is still connected to hydro power and generator is not running. Alarm is unable to clear. Not mentioned in the shift report. Will continue to monitor site. 03:35 - Called Ben H. who directed to disregard alarm #CONSULT | FLAG | stage2_low_confidence | 0.011117 | ML: above threshold (no LLM available) — 0.011 | not running [equipment_failure]; alarm [control_system] | 0.011117 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | BLW3- Travis W onsite for health and safety work orders and turbidimeter cleaning. | FLAG | stage2_low_confidence | 0.0089791 | ML: above threshold (no LLM available) — 0.009 | work order [maintenance_action] | 0.0089791 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NMW136- Eric S onsite troubleshooting free chlorine analyzer. Placed well man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052654 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NMW136- Treated Free Chlorine Hi Alarm. Value did not recover. Rotated Ammonia pumps so pump 1 in duty 1. Will monitor. 09:29- Joe D requested to rotate Ammonia Pump tanks and call if it does not come down in 20 minutes. 09:38- Joe D will go to site. 10:13- Joe D finished onsite. Instrumentation will attend. W11722182 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053907 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | KLPSWL/ KLW34- Dave T onsite for work orders. Running generator, Cl analyzer maintenance, Health and Safety, Cl Leak detection, low temp, and flood alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | flood [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | NBW5 - Eric S finished at site NMW12 - Influent free chlorine hihi on startup | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043368 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | AUW57- Joe D and Donald M onsite for chlorine cylinder change. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048608 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | QVW34 - Rick L & Parth P onsite for chlorine analyzer switching out Cl17 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050819 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP LL, Chris S on site removing the PAC on site, directed to disregard comm alarms until he has left | FLAG | stage2_low_confidence | 0.0093066 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0093066 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | QVETQS - Will M onsite cleaning analyzer for free and total | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063102 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | GWTP/KSTP/SUETDR - John Demarco ready to initiate the network maintenance for the Keswick/Georgina/Sutton water systems. Contacted Dan Z to inform that the duty will be shut down for this work. Dan Z stated they will inform the area operators. | FLAG | stage2_low_confidence | 0.014965 | ML: above threshold (no LLM available) — 0.015 |  | 0.014965 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | NBW2 - Chris I onsite. Leaving well man/off to work on broken valve, isolating section | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054368 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS Normal GWTP, ZW1 Performance Yesterday Lo Alarm, as per instructions/SOP, Sent email to on call operator and area so they are aware that this alarm did come in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058861 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | MTW12 - Travis W on site to complete JHSC and station checks. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045872 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | AURSBS, Donald M on site, he is placing the chemical system offline, testing the Ammonia flood alarm, dehumidifier off/Cl2 leak detection, chemscan offline. Doing work orders for the site | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | flood [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | NMW136 - Alex B onsite putting well 13 in local, isolated, pulling silicate injection point MKETFA - Peter (TO) informed they are rotating pump 1 to duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005221 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | GWTP- Keswick Header Fluoride HiHi Alarm. High LIft Pump 1,2,3 Lockout Alarms. Called Joe M. No answer, informed that instrumentation is onsite for calibrations. | FLAG | stage2_low_confidence | 0.0085195 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0085195 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMW12 - Eric S on site to complete a button replacement on the CL17. Eric has requested that the well be deactivated. System duty is almost complete. Contacted Alex B to confirm the wells do not need to be on for other work orders. Deactivated NMTKKC duty to shut down NMW12. | FLAG | stage2_low_confidence | 0.02129 | ML: above threshold (no LLM available) — 0.021 | work order [maintenance_action] | 0.02129 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to two MAPS pumps to increase demand on MARS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068548 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NMVCBA - Placed valve in manual at 40 L/s 00:15 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030365 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | MKRSEM - Reservoir 1 Level Lo. Called Toronto Water (Paul) and requested 2 pumps on. 03:10 - Called Toronto Water (Paul) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045211 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | KSTP - Clearwell influent free CL2 res lo. Informed Donald M. Low lift turbidity reading high while low lifts off. Place raw water turbidity in calibration mode at request of Donald M. Donald M looking into issue and chlorine pumps | FLAG | stage2_low_confidence | 0.010666 | ML: above threshold (no LLM available) — 0.011 |  | 0.010666 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | ARPS- Jerry from Peel called and is switching from transfer pump 7 to pump 5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052336 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | GWTP - Erick S & Parth P & Rick L onsite for annual calibrations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065218 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | MKPSSA - Patrick F running generator, flood alarm, analyzer maintenance GWTP - Joe M onsite with Jackie S working on UV maintenance | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | SHTP- Filter 3 Post Rinse NIT High Alarm. Reset alarm as per SCADA Report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0056904 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | NMVCBA- Placed valve in manual 20L/s to assist in keeping NMETIB and NMETHW offset. 01:15- Placed back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042939 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | VNPS PD7- Placed pumps 1 and 2 in auto MAPS PD7- Placed Pump 2 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042747 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | GWTP, Low Lift Drainage Pump 1 Overload Alarm, Still have 1 drainage pump available, notified Jack P, he will look into it 19:44, Jack P to disregard for the night since there is still 1 other pump available at this time. Jack P adjusted the hi level alarm from 4.0 to 4.1 and turned on the hi level alarm so that if the pump can't keep up with the drainage, there will be a notification to the ROC and the RO will contact Jack P consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | AUW23/5, Placed wells man/off to take more water from AURSBS. This will help take more water from MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058564 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | AUPSWS - Lee F on site to complete vibration testing on the pumps and would like the duty 1 to be rotated from pump 5 to pump 4. Made the necessary duty change. | FLAG | stage2_low_confidence | 0.013517 | ML: above threshold (no LLM available) — 0.014 | vibration [equipment_failure] | 0.013517 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MKRSMR - Artour L finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056534 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | HLETYS - Activated duty 1 as per Tim H. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043825 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | MTW3, Sean P/Ernie H working on the generator switch 10:52, Sean/Ernie are leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031735 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | GWTP, Rick L/Eric S on site, doing annual calibrations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058155 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to two MAPS pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060547 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to one MAPS pump and one VNPS pump to equalize the demand between RHRSTR and MARS. | FLAG | stage2_low_confidence | 0.0081613 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081613 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | QVW34- Ben H called to imform wells will remain man/off. Can be used in an emergency. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | SUSP - UV channel 1 common critical alarm, UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 2 is active. Trending shows that flow through the UV channel recently started. Shift report states these alarms trigger when flow starts and are a disregard. Cleared alarms. *Wrong book. Belongs in ROC Wastewater* | FLAG | stage2_low_confidence | 0.026637 | ML: above threshold (no LLM available) — 0.027 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.026637 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | VNPS PD7, Placed pumps 2/3 in man/off MAPS PD7, Placed pumps 2/3 in auto RHRSTR, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0027378 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038034 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | KSTP, Fin Water Fluoride Res Hi, Notified Joe M and Ben H, they are looking into it | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069332 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | SHTP - Treated water turbidity fault. Highlifts not running, plant is running. trend shows no value change for NTU last hour but on SCADA can see third decimal value change showing movement. Informed Jordan B of outstanding alarm, will wait till highlifts come on and see if able to clear fault. Will monitor 19:12 - Treated water turbidity hi, start up of highlifts shows increase in turbidity. Informed Jordan B, will head to site CMU = 11733253 20:33 - Jordan B finished at site. | FLAG | stage2_low_confidence | 0.02394 | ML: above threshold (no LLM available) — 0.024 | fault [equipment_failure]; not running [equipment_failure]; scada [control_system]; alarm [control_system] | 0.02394 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053624 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | STW12 - Communication loss to STW12 alarm. STETL to STW12 Comm alarm. Notified Yash S. He will check SCADA. # CMU5 W11700739 11:36 Yash S called, communication restored. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0063319 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MKRSEM- Free Chlorine Residual Fault Alarm. Alarm cleared. | FLAG | stage2_low_confidence | 0.012998 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.012998 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | NMTKKC - Outlet total CL2 lolo, reading within range able to clear alarm. No dips appear in trends. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064026 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMTKKC - Ammonia pump 1 uncommanded stop alarm. Checked site, ammonia pump 2 started on duty 1. Was able to clear alarm. Will monitor. | FLAG | stage2_low_confidence | 0.0075437 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075437 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | AUW2/3/5, Placed wells man/off to help take water from AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048321 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MKRSEM - Called Toronto water (Paul) and requested to start filling Res. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067074 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | GWTP, Filter 2 Shutdown alarm/Filter 2 BW Exceeded duration alarm, notified Jack P, he will look into it, directed to place the filter 2 off for the time being consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059519 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | MAPS PD7, Placed pump 2 man/off VNPS PD7, Placed pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034231 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | GWTP - ZW1 Permeate Pump Uncommanded Start and ZW1 Shutdown alarms came in. Checked site. Called Jack P. who directed to ack/reset permeate pump alarm and then directed to place the train mode off and then back on. Both alarms have cleared #CONSULT | FLAG | stage2_low_confidence | 0.0088598 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0088598 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | AURSOH - Joe D finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055767 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004717 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | GWTP - ZW3 membrane tank level hi alarm. Checked site, train 3 is going through a chemical clean process. Trending shows the filter level is slightly above the hi alarm setpoint. Filter level will drop as the cleaning sequence progresses | FLAG | stage2_low_confidence | 0.012185 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.012185 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | VNPS7 - Place pumps 1 & 2man/off MAP7 - Place pump 3 in auto. Done to slow demand pulling from MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048878 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | Connor Smith signing in -1C windy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041936 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | AUW14- Joe D called and requested all wells man/on for sampling | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048805 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | NMVCBA, Placed valve in manual and set it to 40L/sec | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046716 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | NMVCBA, Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056142 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STW2/3, Placed wells back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042623 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | GWTPLL, Low Lift Surge Relief Valve Open alarm, Came in on Plant shutdown, Past elogs showed the alarm can be reset, will wait 15 minutes and then reset 03:09, Alarm has cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053609 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | RHRSTR, Deactivated D1 so more water moves from MARS to RHRSTR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048625 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | NMTKKC- Kingsley M performing server reboot. Requested to have tank topped up. Confirmed with Jason G and activated duty | FLAG | stage2_low_confidence | 0.0084163 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084163 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | QVW34 - Donald M informed testing of Flood containment alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; containment [safety] | flood [critical]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | RHRSWA - Ian W. informed that he is working on the OIT and requested to disregard the Historian Heartbeat alarm 14:25 - Ian informed that he is finished working on the OIT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005216 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal HLW2, Ammonia pump 1 fault, placed pump man/off for the time being, emailed on call operator/area to let them know | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure] | 0.0070484 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | NMETHW, Activated D1 to have the towers offset | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045261 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | KLPS27/KLET27 - Yash S on site to complete the scheduled PCS network maintenance. Deactivated tower duty to shutdown the pumps for the duration of the maintenance. | FLAG | stage2_low_confidence | 0.0073576 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073576 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | Carter Dunn Signing In, 16D/Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041783 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | KLET27, KLMCHR, KLMCIA, KLPS27, KLPSWL, KLW34, NBETRS, NBET27, NBW2, NBW3, NBW5 - Kingsley M completing a Hub 5 server restart. No impact to operations. | FLAG | stage2_low_confidence | 0.0074387 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074387 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | HLW1 - Treated free chlorine hi. Ammonia pump 1 running. Informed Jordan B as known issue with this ammonia pump. Place ammonia pump 2 duty 1. Place ammonia pump 1 man/off | FLAG | stage2_low_confidence | 0.0080918 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080918 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | MARS, Contacted Toronto operator Paul to increase the flow to MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065512 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | KSTP, Fin Water Fluoride Res Hi Alarm, Notified Joe M, directed to disregard as plant just started up | FLAG | stage2_low_confidence | 0.0082761 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0082761 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | VNMVYS- Ric L onsite troubleshooting flow meter. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060382 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | GWTP - Rick L on site to complete annual calibrations at the low lift building. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065638 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | Ethan U signing in Weather 0. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003854 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | SHTP - Well pump 2 uncommanded start alarm. Checked site, plant is not active. Well pump 2 is not active. Trending shows the plant recently shut down. Able to clear alarm. SHTP - Site power failure and generator running status alarms. SCADA shows the ATS in local connected to the generator indicating this is an operator activated test. Jen S is on site. Alarms cleared locally. Plant not active. MTW12/MTW3 - Placed well pumps in auto following the completion of the historian trend maintenance. STRS48 - High lift pump 1 failed to stop alarm. Alarm triggered when the system was deactivated in preparation for the Historian trend maintenance. Able to reset alarm. | FLAG | stage2_low_confidence | 0.051786 | ML: above threshold (no LLM available) — 0.052 | failed [equipment_failure]; failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.051786 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | SHTP - High lift pump 4 fault. Checked site, high lift pump 4 is local off. STW3 - Jack P on site to complete chemical system inspections including turbidity analyzer, Chlorine analyzer and silicate system. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | GWTP - Sutton header fluoride low alarm. Checked site, when the alarm triggered there was no flow to the Sutton system. Trending shows a dip of the fluoride reading which recovered. Cleared alarm. | FLAG | stage2_low_confidence | 0.012739 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.012739 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | NMW12 - Christian B. called to inform that he is on site with Alex B. and they will be completing PM's. These include testing the Chlorine Detection, Chlorine Analyzer maintenance, ammonia inspection and Turbidimeter maintenance | FLAG | stage2_low_confidence | 0.0098833 | ML: above threshold (no LLM available) — 0.01 |  | 0.0098833 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP, Rick L/Eric S is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054102 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | VNPS PD7, Placed pump 2 man/off MAPS PD7, Placed pumps 2/3 in auto MARS is on the higher end, trying to help draw it back down for night shift RO | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035041 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | QVETQS, Comb Inlet Cl2 lo alarm, tower is filling, notified Donald M as this could affect the outlet since the residual has dropped quite a bit and is on a constant decline, Reason for drop in Residual is due to the work that was happening at QVW12, Donald M will look into the situation 20:02, Donald M called back, Operator placed the tie valve man/open. directed to place the valve back to auto either at 10PM or if the residual goes back to normal level. Also notified the RO that he would like QVW3 to also go back to auto at 10PM. 21:02, Placed tie valve back to auto as per Donald M instructions, the residuals have come back to normal range 21:09, Inlet Free Cl2 hihi Switch Alarm, HMA alarm/High Priority, contacted Donald M as this may be caused by his earlier work, he will look into it 21:18, Directed to disregard at this time, if the hihi alarm comes in, he will attend site consult | FLAG | stage2_low_confidence | 0.034634 | ML: above threshold (no LLM available) — 0.035 | alarm [control_system] | 0.034634 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | Christian Van Beek signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054296 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MAPS - Tim H onsite running diesel, testing diesel spill, and eyewash alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; alarm [control_system]; alarms [control_system] | spill [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | AUW14 - Joe D running generator. Wells placed man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046493 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | KCETDS - Metering chamber flood. Informed Jordan B, disregard for the night will drain it out in the morning Consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | SHTP- FILT 1 Turbidity Hi, Filter 3 Turbidity Hi Alarms. Backwash just completed. Disregard as per SCADA report | FLAG | stage2_low_confidence | 0.0077882 | ML: above threshold (no LLM available) — 0.008 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0077882 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | H1GWTPP1 - Chris S restarting serve. QVW12 - Lee F onsite looking to check waste valve issue. Activated duty as near duty start Hub2 - Kingsley M restarting server | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005407 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Mehdi) and requested they deactivate the pumps pushing flow to MKRSEM. | FLAG | stage2_low_confidence | 0.0076905 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076905 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | VNMCYS - Kevin W called to inform he is re-booting the APN for this site. No impact to operations expected. | FLAG | stage2_low_confidence | 0.00792 | ML: above threshold (no LLM available) — 0.008 |  | 0.00792 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | RHRSTR - Deactivated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041621 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | NBW2 - Historian heartbeat alarm, able to clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005028 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | AUW5- Joe D onsite for work orders including Cl analyzer and turbidimeter maintenance, and Cl Leak. | FLAG | stage2_low_confidence | 0.0158 | ML: above threshold (no LLM available) — 0.016 | work order [maintenance_action]; leak [infrastructure] | 0.0158 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | HLETYS - Tower Mixer uncommanded stop alarm came in. Checked site. Tower is still filling. Ack/reset alarm and alarm cleared. Will monitor | FLAG | stage2_low_confidence | 0.010047 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010047 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MARS - Tim H onsite for cleaning analyzer, & hi/lo level | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062323 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | AUW57 - Joe D. called and requested to place the well back to auto. Well is now running in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005709 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | NMW136, Placed well 13 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043034 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | Ethan U signing in Weather -0. Snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035846 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | NMETHW - Activated Duty 1 @ 43% to offset NMETIB. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045908 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | STW12 - Well 1 pump fault alarm. Generator running alarm. Placed Well 1 pump man/off. STPSTL - Generator running alarm. Power outage, pumps stopped and restarted. ATS switch in local mode. BLW12 - Pump 1 VFD fault alarm after power blip. Placed Pump 1 man/off. Duty not active. STW3 - Well 3 pump was running in manual, power blip, pump stopped. No outstanding alarms. Placed P3 to auto, restarted ok. 12:44 BLW12 - Generator running alarm. 12:45 Checked Hydro one website. Power outage in the area. BLW12 - ETR 15:30, STW12 - ETR 15:30. ATS switch at STPSTL back in auto. # Notified Joe M. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; alarms [control_system]; pump fault [infrastructure] | fault [equipment_failure]; alarm [control_system]; alarms [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | STRS48 - Sample pump 1 fault alarm. Sample pump 2 is running, will monitor. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | NMETIB - Activated Duty 1 to offset NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044585 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MARS - Tim H onsite for cleaning analyzer, & hi/lo level KSTP - Fin water flouride res hi near startup, reading came down within range | FLAG | stage2_low_confidence | 0.0074748 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074748 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | Angelica Chepiga signing in,weather -4C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | STW12 - Power restored. Generator stopped. Assigned Well 2 pump to Duty 1/ placed man/on for STETBR fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006117 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | STPSTL - Power restored/generator stopped. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058653 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | VNPS PD7- Placed P3 man/off MARS PD7 - Placed P3 to auto. To help maintain MARS and RHRSTR levels. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048061 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | GWTP - Joe M on site to complete maintenance on the turbidity sensors of all the membrane trains and to complete a chlorine system inspection. Joe M directed to disregard the associated alarms. HLW2 - Influent free chlorine hihi alarm. Checked site, well is active. Tim H signed in on site and recently completed a chlorine cylinder change. | FLAG | stage2_low_confidence | 0.020744 | ML: above threshold (no LLM available) — 0.021 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.020744 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | ANW23 - Sean P completed with his ATS testing. Activated reservoir duty 1 and monitored well activation. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059324 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | QVETQS, Residual at the tower is dropping slowly, QVW12 is filling and putting out good residuals. Earlier Donald M had to go to site to work on the chlorinators which did have low residuals. As a game plane on what RO did last night, opened up the tie valve at QVETQS to not fill the tower with bad water. Will continue to monitor site. Notified Donald M for a game plan just incase the inlet does drop. Donald M requests a call if the inlet does drop to the low low level alarm 20:25, Placed tie valve back to auto, residuals are back to normal levels consult | FLAG | stage2_low_confidence | 0.021978 | ML: above threshold (no LLM available) — 0.022 | alarm [control_system] | 0.021978 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | STW3 - Running in auto. Zone 1 filling, placed well man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047767 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | KSTP - Raw water turbidity fault. Disregard as per shift report | FLAG | stage2_low_confidence | 0.010156 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.010156 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | NMETIB, Activated D1 to keep the towers offset | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045246 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | MAPS PD7- Placed pump 2 to man/off VNPS PD7- Placed pump 2 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034858 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | STW12, STW3- Placed well 1 and well 3 pumps man/on for STETBR fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051364 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | ARPS -David from OCWA called. Completing daily pump duty rotation, from Pump 7 to Pump 6. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055636 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | MARS - High level alarm. Placed VNPSPD7P2 man/off, MARS PD7 pump 2 back to auto and activated Duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064828 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | BLW12 - Site back to normal OP, Joe M leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046019 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | SHTP - Well pump 2 uncommanded start alarm. Checked site, plant is not active. Well pump 2 flow recently stopped. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070495 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | MTW3- Travis W on site for turbidity analyzer maintenance | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044611 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | KSETDP - Phil D onsite with Chris S. Chlorine E-stop, chlorine analyzer, & halogen alarms and cylinders | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | NBW2 - Chris I finished at site. Well back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046334 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS normal Adeela Khan Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038512 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | wrong book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050742 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | STRS48/STPS48, Jack P on site running the generator, doing analyzer maintenance and working on the turbidity analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059193 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | NMW12 - Christian B onsite with Alex B pulling injector lines for silicate | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051622 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | KSETDP - Post injection free and combined chlorine lolo alarms are still active. Contacted Phil D who stated that these alarms will be disregarded and outstanding until maintenance can attend site. Requested that Phil D has these alarms added to the shift report. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | STPSMR - Historian Heartbeat Alarm. Checked site, pump was active when alarm came in. Alarm cleared on an acknowledge and reset. Pumps activated but trends are now showing "No Data" shutdown the pumps in manual mode. Called Yash S who will check the system. Created CMU5#W11702333 #consult #CMU5 | FLAG | stage2_low_confidence | 0.011591 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.011591 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | NBW5, Yash S resetting OIT on site, well is currently man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045532 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | AUW57, Joe D is leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041623 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | MAP8 - Pump 2 discharge valve failed to open and Pump 2 failed to start alarms came in. Checked site. Duty recently activated. This fault inhibited the pumps. After 10 mins, the pumps rotated duty so pump 2 is no longer in duty 1. Alarms and inhibit cleared and pump 1 and 3 started up. | FLAG | stage2_low_confidence | 0.047701 | ML: above threshold (no LLM available) — 0.048 | fault [equipment_failure]; failed [equipment_failure]; alarm [control_system]; alarms [control_system]; valve failed [infrastructure] | 0.047701 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | SHETCS - Tim H heading to site later this morning to complete chlorine analyzer maintenance and test the high/low temperature alarms. | FLAG | stage2_low_confidence | 0.011369 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011369 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | YWS+NYWS normal Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046111 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | NMVCBA - Placed valve in man at 40 L/s 00:05 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029913 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MMW1-Kyle C called ROC for update on site. Notified Kyle C that Sean P is attempting to restore power to site via generator and that the ROC will contact Kyle C if outstanding historian heartbeat alarm is not able to clear or if any other alarms are outstanding. NBW3- Influent free Cl2 lolo alarm came in on scheduled start up. Reset alarms after 6 mins and monitored well start up | FLAG | stage2_low_confidence | 0.017541 | ML: above threshold (no LLM available) — 0.018 | alarm [control_system]; alarms [control_system] | 0.017541 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MMW1- Rob P. Notified ROC wells are back on and station is running on generator. Called Kyle C about outstanding historian heartbeat alarm. Created CMU5 W11714725 #CMU5 | FLAG | stage2_low_confidence | 0.0075273 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075273 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NBW5 - Silicate pump 2 uncommanded start and Turbidity Hi alrms, Jacob M working on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051942 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | QVW12 - Noticed NMETHW duty is active but no duty 1 well was available. Called Will M. to confirm sampling was finished as the wells were left in manual. Will informed that he is finished on site and requested to place wells back to auto | FLAG | stage2_low_confidence | 0.010338 | ML: above threshold (no LLM available) — 0.01 |  | 0.010338 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | NMETIB - activated D1 to offset NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043577 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | JFPS- Benson S onsite for generator run, flood test, hi/low temp, health and safety and valve exercise. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | MAPS PD7- Placed pump 3 man/off VNPS PD7- Placed pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041061 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | MKRSEM- Called Toronto (Mehdi) and requested pumps on. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061774 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | KLMCHR - Vaughan Pressure HiHi alarm came in. Checked site. Checked MARS. TMC317 has been pushing 42 ML/d since around 2:05 AM. Called Paul at Toronto Water who informed a pump had started in auto. Paul informed that he will shut that pump down and go back to normal flows 03:53 - KLMCHR - Pressure went back to normal range and alarm cleared | FLAG | stage2_low_confidence | 0.011101 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011101 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | KLPS27, KLET27 - Jen S. doing cl analyzer maintenance, testing flood and temp alarms. GWTP - Yash S. informed finished with network, he will notify ops. Left HLP man/off | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | STETBR - Hi level alarm, placed STW12 pump 2 and STW3 back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055645 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMW15 - Treated free chlorine hi. Alarm triggered earlier this morning on well activation. Alarm was addressed by area operations and ROC operator Ethan U. Alex B and Donald M attending site to inspect the ammonia pumping system. Created CMU5#W11701894 at the request of Alex B. #CMU5 | FLAG | stage2_low_confidence | 0.01106 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.01106 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | Christian Van Beek signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054296 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMW15 - treated free hihi, combined chlorine lo. Rotated ammonia pump 1 to duty 1. Readings came back down. Noticed central ops rotated ammonia pump back. Reading back to normal. Issue came back with free chlorine. Well was placed man/off | FLAG | stage2_low_confidence | 0.0091304 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091304 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | BLW34 - Travis W on site to complete a generator test with a contractor, no ATS activation. Travis will also be completing chlorine and turbidity analyzer maintenance. | FLAG | stage2_low_confidence | 0.0074498 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074498 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | AUW57 - Treated free chlorine residual Hi alarm at duty startup. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057908 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | GWTP - sodium, hypo tank level hihi. Chemical delivery scheduled for today. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068482 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | AUPSRR - Donald M on site to complete a chlorine leak detection test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | MARS- Called Toronto (Mehdi) and requested to revert back to normal flow VNPS PD7- Placed Pump 3 in manual MAPS PD7- Placed Pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048221 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | GWTP- Jack P heading to site Created CMU5 W11714562 #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041824 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MAP7 - place pump 3 man/off VNP7 - Place pump 2 auto. Change made to help assist with demand from MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049296 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | AUPSWS- PAC control panel power fail alarm came in. Cleared upon acknowledgement pump 4 running okay . | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065043 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | STW12/3- Placed well 1/3 man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045035 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -11C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044737 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MARS- Called Metro spoke with Zorhan to increase flow VNPS PD7- Placed P2 in man/off MAPS PD7- Placed P2 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042696 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MAPS- Air handling unit compressor fault outstanding. Notified Dave T directed to call if VFD room temp hi comes in JFPS- Res temp alarm came in. Notified Donald M directed to disregard #consult | FLAG | stage2_low_confidence | 0.027364 | ML: above threshold (no LLM available) — 0.027 | sso [critical]; fault [equipment_failure]; alarm [control_system] | 0.027364 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MMW1- Kyle C was able to restore trends on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043044 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | NBW5 - Pump uncommanded stop alarm. Called Jake M who stated he is on site and will be decreasing the flow setpoint before re-activating the pump and monitoring system. | FLAG | stage2_low_confidence | 0.0083064 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0083064 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | NBW5 - Turbidity high alarm. Well recently activated. Will monitor site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0056278 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | SHTP - KMNO Pump 2 Uncommanded stop alarm. Duty rotated, Pump 1 running on duty 1. Was able to clear alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067089 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | Angelica Chepiga signing in,weather +5C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | VNMCYS- PAC comm fail on site alarm cleared upon acknowledgement | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | GWTP, UV Reactor 1 Start/Stop Fault//uncommanded stop and a UV Comm alarm came in, notified Jack P, he is looking into it consult | FLAG | stage2_low_confidence | 0.0094137 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure]; alarm [control_system] | 0.0094137 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | AUW2/3/5, Placed wells back to auto RHRSTR, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033071 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | HLETYS - Benson S. called back and requested to place the start setpoint at the tower from 25% back to 35% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059994 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | ARPS -Benish from OCWA called, Completing daily pump duty rotation. Will run pump 4 for 2 hours and switch to pump 5 after. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065301 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | VNPSCD - Benson S on site to complete station checks and requested that the RHRSTR duty be activated so that BVPS pumps start and push flow into RHRSTR to activate the chemical system. Activated RHRSTR duty 1. | FLAG | stage2_low_confidence | 0.0090677 | ML: above threshold (no LLM available) — 0.009 |  | 0.0090677 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | NMVCBA-Placed valve manual 30L/s to assist in NMETHW and NMETIB offset 00:29- Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041085 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | KSTP- Raw Water Turbidity Fault. Disregard as per SCADA Report. | FLAG | stage2_low_confidence | 0.013399 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; scada [control_system] | 0.013399 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | KLMCIA - Security Intrusion and Meter Chamber Flood alarms came in. Shift report indicates that the site is OOS. Called Rob P. who directed to disregard alarms and someone will attend site tomorrow to pump down the chamber. Rob informed that the security intrusion and meter chamber flood alarms are tied together and come in at the same time #CONSULT | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | flood [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | GWTP - PLC-3 (LLP) Permissive to Run Lost alarm. Called Joe M, no response. Sent message, will call again. GWTPLL - Permissive to Run Lost alarm, Joe M draining GAC4. | FLAG | stage2_low_confidence | 0.0073101 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073101 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | AUW57 - Combine chlorine residual low alarm after duty stop, no water directed to users, residual recovered in 8 minutes. Alarm cleared. | FLAG | stage2_low_confidence | 0.0075586 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075586 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NMMCBR - Created CMU5#W11719262 for Rob P at the request of Dwayne L. #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003825 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | STW3- Placed well back into auto for STETBR fill cycle completion | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049524 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | STETBR - Low level alarm. Man/started Well 3 pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051046 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | QVW34 - Chris I finished on site. Generator back to normal OP. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045455 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | STRS48 - Ian W on site to complete work on the OIT and has directed to disregard the associated historian heartbeat alarm. | FLAG | stage2_low_confidence | 0.011042 | ML: above threshold (no LLM available) — 0.011 | sso [critical]; alarm [control_system] | 0.011042 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | STW12 - Effluent turbidity Hi alarm. Pumps placed man/off earlier today, no water directed to users. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064102 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP - Sutton header fluoride low alarm. Value has recovered with no actions taken. Cleared alarm. | FLAG | stage2_low_confidence | 0.0080789 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080789 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | MTW12/MTW3 - Place wells man/off STW3 - Place back auto STETTL - Deactivate duty 1 STETBR - Deactivate duty 1. Done as preemptive response to network trend maintenance impacting those sites. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050989 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | NMTKKC- Chloramine Analyzer Offline Alarm. Joe W onsite performing analyzer hot flush. | FLAG | stage2_low_confidence | 0.0079021 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079021 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | GWTP- RIc L finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054719 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | KSTP - Joe M called, he started filter 1 backwash, requested High lift Pump back to auto. Joe M will notify OP. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059822 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NMTKKC - Chloramine analyzer offline alarm. Checked site, Joe W signed into facility in the logbook. SCADA shows the chemical system is all manual/off. The Chloramine analyzer offline alarm changed to Normal status and cleared on acknowledgement. Called Joe W, no answer. Will monitor site and wait for reply. | FLAG | stage2_low_confidence | 0.02227 | ML: above threshold (no LLM available) — 0.022 | scada [control_system]; alarm [control_system] | 0.02227 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: 10C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -3C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | MKRSEM - Request TO (Peter) to drop both pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059895 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | VNP7 - Place pump 2 auto MAP7 - Place pumps man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038887 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two MAPS pumps to one MAPS and one VNPS pump to equalize demand on MARS and RHRSTR. | FLAG | stage2_low_confidence | 0.0083875 | ML: above threshold (no LLM available) — 0.008 |  | 0.0083875 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA Report | FLAG | stage2_low_confidence | 0.013702 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.013702 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | QVW12 - Sean P on site to complete a generator load bank test. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046082 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | MARS- Cell1 (North) Lvl Lo Alarm AURSBS- Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043675 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | QVW12 - Will M on site to complete a chlorine leak detection test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | MAPS PD7 - Placed the active pump (Pump 3) in manual mode and deactivated to reduce the demand on MARS while ARPS is down. VNPS PD7 - Placed pump 3 in auto mode and monitored start up. MARS - Called Toronto Water and requested additional flow to MARS through TMC317 while ARPS is down. NMW136 - Eric S completed his work on site and leaving | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005673 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | KSTP - Filter 1 and Filter 2 Backwash is out of services alarms. Jerry Z is signed into the facility logbook. MWW1 - Tyler ZJ on site and will be turning off the temporary generator to complete some wiring changes. Estimated work duration is thirty minutes. | FLAG | stage2_low_confidence | 0.023714 | ML: above threshold (no LLM available) — 0.024 | out of service [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.023714 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | STPSMR - Dan B onsite working on fan exhaust | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059067 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | GWTP- Jackie S called and is filling GAC4 and placing turbidimeter back into service. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054467 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | GWTP - Chris S called to inform he will be completing a server restart for GWTP. Chris will contact operations to ensure there is no impact to operations. Plant is currently offline for UV system work. | FLAG | stage2_low_confidence | 0.012267 | ML: above threshold (no LLM available) — 0.012 |  | 0.012267 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | KCPSDS - Benson S. informed that if the hypo pump 2 fails to start alarm comes back in, place the pump in manual and send an email. | FLAG | stage2_low_confidence | 0.0075714 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075714 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | GWTP - Outstanding High Lift Free Chlorine Lo alarm. Plant recently started up. Free chlorine Levels are still low. Called Stephen B. who informed that this alarm can be disregarded. Stephen informed he would like a call back for any clearwell related alarms and if the keswick and sutton free chlorine line starts to drop. #CONSULT | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | VNRSKS - Deactivated duty and switched pumps from VNPS PD7 to MAPS PD7 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050602 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | KSETDP - Post injection free chlorine lolo and combined chlorine lolo alarms. Checked site, outlet analyzer reading stable and normal values while the post injection analyzer showing abnormal values. Facility logbook shows Phil D on site for flushing to waste and to bring the tower online. Phil D still logged in indicating he is on site. Phil D collected grab samples which show normal range for free and total chlorine. | FLAG | stage2_low_confidence | 0.040331 | ML: above threshold (no LLM available) — 0.04 | alarm [control_system]; alarms [control_system] | 0.040331 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | KSTP- CO2 Adjusted pH LoLo Alarm. Notified Jerry Z. he will look into it. 14:40- Jerry Z cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0042509 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from one VNPS and one MAPS pump to two MAPS pumps to increase demand on MARS. | FLAG | stage2_low_confidence | 0.007972 | ML: above threshold (no LLM available) — 0.008 |  | 0.007972 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | NMVCBA - Placed valve in man/open at 30 L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004472 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | QVW34 - Treated Toral chlorine low alarm. Wells off, no water directed to users. Value recovered in two readings. Alarm cleared. | FLAG | stage2_low_confidence | 0.0072882 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072882 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | NBW37- Influent free Cl2 lolo alarm on Schedule mode start up. Influent free chlorine residual recovered, cleared alarm and restarted well pump 7 on schedule mode. | FLAG | stage2_low_confidence | 0.0082458 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0082458 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | VNRSKS - swapped supply pumps to one VNPS pump and one MAPS pump to equalize the draw on MARS and RHRSTR. | FLAG | stage2_low_confidence | 0.0079111 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079111 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | EGMCDD - Arthur L on site to complete commissioning of new instruments on site. Arhtur requested that alarms be disregarded from this site. | FLAG | stage2_low_confidence | 0.01102 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.01102 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | AUW57 - Free chlorine hi, rotate ammonia pump 2 duty 1, reading came down AUW14 - Joe D onsite placing wells man/off. Working on chlorine analyzer, turbidimeter, chlorine leak. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MKRSEM- Artour L. onsite working on PAC. No impact to operations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064541 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048355 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | GWTP - GAC4 control valve deviation, backwash tank 1 level high, disregard as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056289 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NMVCBA- Placed valve in manual 20L/s to keep NMETIB and NMETHW offset 17:31- Adjusted to 30L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039461 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | NMVCBA- Placed valve in manual 30L/s to assist offset of NMETIB and NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051567 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | RHRSTR, Deactivated D1 to allow more water to move from MARS to RHRSTR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050572 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | BLW3 - Travis W onsite. Scrubber check, exhaust, fan, chlorine leak, temp alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | Carter Dunn Signing In, -2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | HLETYS- Kingsley M requested to deactivate duty for HUB3VR reset. Confirmed with Tim H NMTKKC- Kingsley M requested to deactivated duty for HUB3SVR reset. Notified Alex B as NMW13 running in manual. Alex informed Ben H. Kingsley confirmed still able to perform reset. Will lose comms for 5-10 minutes. | FLAG | stage2_low_confidence | 0.012035 | ML: above threshold (no LLM available) — 0.012 |  | 0.012035 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather +7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NBW5 - Influent free chlorine residual Hi alarm at duty start up. Alarm cleared in 5 minutes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061937 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | RHMCMD - Control panel power failure, site power failure and valve 1 and 2 fault alarms. Suite of power failure alarms triggered for site within Richmond Hill. Checked site, trending shows the valves closed and then opened. Able to reset alarms. RHPSWA /RHRSWA - Control panel power failure and site power failure alarm. Checked site, reservoir was draining when alarms triggered. RHPSWA was not active when the alarms triggered. SCADA showing normal operations. Reset alarms. AUMCBS - Control panel power failure and site hydro power failure alarms. Checked site, trending indicates normal operations. Cleared alarms. JFPS - Power failure affected pump operations. Tim H investigating and cleared alarms before the site could be checked. BVPS - Pump 1 multilin alarm. Station was affected by a power failure which interlocked the pumps during duty start. Tim H completed a site check on SCADA and cleared alarms. VNMCBA - Control panel power failure and site hydro failure. Checked site, trending shows normal operations. Cleared alarms. RHPSPA - Hydro power failure alarm. Richmond Hill was affected by a brief power failure. Checked site, trending show operations are normal. Pumps were not active during the power failure. Cleared alarms. | FLAG | stage2_low_confidence | 0.23527 | ML: above threshold (no LLM available) — 0.235 | fault [equipment_failure]; failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.23527 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | John D called back informing of roll back on East historian trends | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065511 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | VNPS- Chlorine System Failure Alarm VNPS- CL2 Emergency System 1,2 Fault Alarm. Chemical system is interlocked. Notified Ben H. He will attend site. Placed BVPS man/off 22:04- Ben H finished onsite. All alarms cleared. Chemical system back in operation. Placed BVPS back into auto W11702361 CMU5 JFPS- RES UPS ATS Source S2 (Line), WPS UPS ATS Source S2 (line) Not Ok Alarm- Alarm Cleared VNPS- Pump 2 Not Ready Alarm, Soft Starter Fault- Pump OOS VNPS- Chlorine Water Pressure LoLo Alarm- Alarm Cleared RHPSPA- Such. Pressure HiHi, Hydro Power Failure - Alarm Cleared VNPS PD8- Pumps shut down. Rotated duties so pump 4 and 1 in duty 1,2 and restarted duty | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; fault [equipment_failure]; failure [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | emergency [critical]; fault [equipment_failure]; failure [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMETIB - Activated D1 to offset with NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044833 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MKRSEM- Called Toronto (Mehdi) and requested pumps off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061833 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | KSTP- CO2 Adjusted pH LoLo, Fin Water Fluoride Res Hi Alarm, Settl Water Cond Level LoLo Alarm. Called Jerry Z No answer. Jerry Z called back. He will look into it. | FLAG | stage2_low_confidence | 0.0072489 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072489 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NMTKKC - Outlet Total CL2 Lo and LoLo Alarms, checked site, Outlet total chlorine residual reading 2,22 mg/l. Trending indicates that the value did not drop to the lo and lolo level alarm setpoints. Cleared alarms. Will monitor and notify area in the morning. | FLAG | stage2_low_confidence | 0.012573 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012573 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | BLW34 - Silicate mixer 1 fault. Silicate tank reads empty. Mixer in local off. | FLAG | stage2_low_confidence | 0.0083768 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0083768 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | H4AUSSP1- Kingsley M performing server reset. Will lose comms for 5-10 minutes. AURSOH duty has shut down. Confirmed with Kingsley M. Will not impact AURSBS. 14:02- Work completed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058994 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | BVPS - Pump1 multilin and umcmd stop. Able to clear alarm. Pump 1 & 4 duty 1 running. power blip and uncmd caused some undesired duty rotations. Rotated pump 1 & 4 duty 1. | FLAG | stage2_low_confidence | 0.0091067 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0091067 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | ANW23 - RSVR inlet free chlorine hihi, David T still Onsight looking into issue | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052814 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | ARPS- OCWA called (Martin) and informed will be switching pumps over from pump 5 to pump 6 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055822 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA Report. | FLAG | stage2_low_confidence | 0.013759 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.013759 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | STPSMR- Historian Heartbeat Alarm came back in. Notified Yash S. He will look into it. 18:47- John D called. Heartbeat alarm caused by reboot performed. Requested to clear alarm. 19:15- John D called and informed trending should be back and will slowly repopulate over the night for Stouffville, Mount Albert and Ballantrae, but live trending is available. Informed John D no trending at MAPS, RHRSTR, VNPS, VNRSKS, ARPS. He will look into it. 20:03- John D called back and issue has been fixed. Trending is back. | FLAG | stage2_low_confidence | 0.020807 | ML: above threshold (no LLM available) — 0.021 | alarm [control_system] | 0.020807 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | AUW14 - Placed back to auto. VNRSKS - Switched feed from MAPS PD7 (P2,3) to VNPS PD7(P2,3). | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046491 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | HLW2 - Well 2 pump failed to stop alarm. Duty just deactivated. Pump stopped. Cleared alarm. | FLAG | stage2_low_confidence | 0.019205 | ML: above threshold (no LLM available) — 0.019 | failed [equipment_failure]; alarm [control_system]; pump failed [infrastructure] | 0.019205 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | AURSBS - Activated Duty 1 to maintain MARS level. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004585 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | RHRSTR- Deactivated Duty 1 to maintain MARS level. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046008 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMW136- Combined and treated total chlorine residual lo alarms. Wells not running, no water directed to users. Chlorine residuals recovered in 6 minutes, alarms cleared. | FLAG | stage2_low_confidence | 0.018975 | ML: above threshold (no LLM available) — 0.019 | not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.018975 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | AUW14- Joe D running wells 2, 3 in manual for sampling. He will revert to auto once completed AUW57- Joe D running well in manual for sampling. He will revert to auto once completed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070932 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | ARPS- Martin from Peel called to notify ROC they will be switching from P5 to P6. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051947 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | QVW34- Eric S finished onsite. Requested to run well. Confirmed with Will M and placed well 3 man/on. 15:49- Placed wells back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047804 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP - UV reactor 2 intensity lo. Appears within normal range now. Joe M called us to inform he has left site, aware of alarm KSTP - Place highlifts back in auto as per Joe M | FLAG | stage2_low_confidence | 0.0076727 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076727 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP - High lift free chlorine low alarm. Checked site, chlorine analyzer is showing erratic trends. Analyzer is in calibration mode and instrumentation team is on site completing annual calibrations. Analyzer readings returned to normal range shortly after, alarm was cleared locally. | FLAG | stage2_low_confidence | 0.018087 | ML: above threshold (no LLM available) — 0.018 | alarm [control_system] | 0.018087 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | QVW12 - Rick L & Parth P onsite for chlorinator rebuild. Placed well 1 & 2 man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053579 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | QVW12 - Parth P finished and leaving site. Parth is headed to AUW14 to assist Joe D. Parth informed that operations will be attending QVW12 to complete some work and that the well is not supposed to run until they complete this work. Deactivated NMETIB duty 1 to reduce the demand on the NMETHW system until the work at QVW12 can be completed. | FLAG | stage2_low_confidence | 0.018053 | ML: above threshold (no LLM available) — 0.018 |  | 0.018053 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | Stouffville, Mount Albert, Ballantrae- During shift transfer noticed no trending at all sites. Christian VB called John D who was performing work. John D called back and confirmed this is related to work being performed and data being collected locally. No ETA on when trends will be back. | FLAG | stage2_low_confidence | 0.018533 | ML: above threshold (no LLM available) — 0.019 |  | 0.018533 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | MARS- Cell1 (North) Lvl Lo Alarm AURSBS- Deactivated duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043863 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | QVW12- PAC Control Panel Power Failure, Generator Running Alarm, Gas Scrubber Overload Alarm (cleared). Well shutdown and then started back up. Site currently running on generator 00:01- Contacted Hydro One. Power outage in the area and estimated time of restoration is 02:30. QVETQS- System Pressure LoLo Alarm- Cleared 02:05- QVW12- PAC Control Panel Power Failure, Well 1 Pump VFD Fault Alarm. Well 1 shut down. Deactivated duty. Unable to clear VFD Fault. Switched well 2 into duty 1. Generator has shut off and station back on utility power. Will email Ben H | FLAG | stage2_low_confidence | 0.049871 | ML: above threshold (no LLM available) — 0.05 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system] | 0.049871 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | HLW2 - Jordan B on site to complete work orders including chlorine analyzer, chlorine leak test, turbidity analyzer maintenance hi/low temperature alarm test and PRV exercise. NBW7 - Jake M on site to complete a generator test run, chlorine analyzer maintenance and chemical system inspections. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | work order [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | GWTP - Joe M requesting electrical on-call. Issue with sump pump not working with building flood. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; not working [equipment_failure] | flood [critical]; not working [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | VNRSKS - Due to lower levels at MARS, switched from MAPS PD7 to VNPS PD7 VNPS - PD7 Pump 3 Failed to Open alarm came in. Checked site. Ack/reset alarm and valve opened and pump is now running 22:31 - VNRSKS - Switched back to MAPS PD7 | FLAG | stage2_low_confidence | 0.0093961 | ML: above threshold (no LLM available) — 0.009 | failed [equipment_failure]; alarm [control_system] | 0.0093961 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | Angelica Chepiga signing in,weather -6C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | ANW23 - Cole W running highlifts in local on. Disregard highlift pumps OOS alarm ad turbidity alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | RHPSWA - Man/stop pump 2 VNP8 - Place pumps back in auto one at a time as Tim H finished with surge tank work MKRSMR - Patrick F onsite running Pump 4 jokey pump | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054795 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | RHPSPA - Lee F finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055816 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | SUSP- Influent hihi alarm came in as both SUSSHS and SUSSWB were pumping to headworks. Trends recovered and alarm cleared **WRONG BOOK** | FLAG | stage2_low_confidence | 0.0083098 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0083098 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NBW5- Jacob M leaving site. He will leave well running in manual for the next hour then place back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060818 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | MAP8 - Place pump 1 & 3 man/off VNP7 - Place pump 3 auto. Done to preserve water for MARS and pull more from Teston | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052637 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | SHETCS- Hypo pump 2 failed to stop alarm came in 3 times notified Stephen B. Stephen B on site working on pump. Directed to place in man/off will trouble shoot next week | FLAG | stage2_low_confidence | 0.015413 | ML: above threshold (no LLM available) — 0.015 | failed [equipment_failure]; alarm [control_system] | 0.015413 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | HLETYS, Darrick/Jordan B on site, testing flow control valves | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059978 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | NMTKKC, Ammonia Tank 1 lolo alarm, Joe W is on site filling the tank | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052499 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | ARPS - David from Peel informed they are rotating pumps. Currently pump 5 running, duty 1 pump will be swapped to pump 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064296 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | Ethan U signing in Weather -7. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | GWTP - Joe M and Jackie S on site to complete a generator test. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060908 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS + NYWS Norma | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049848 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | KSTP - CO2 Adjusted pH LoLo alarm. Checked site, the plant is active but the system duty is off so the high lift pumps are not pushing flow to the system. Trending shwos the pH reading dropped slightly before starting to recover. Alarm cleared and the low lift pumps activated to continue flow to the filters. Plant should shut down soon once the clearwell level reaches its setpoint. | FLAG | stage2_low_confidence | 0.02417 | ML: above threshold (no LLM available) — 0.024 | alarm [control_system] | 0.02417 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | RHPSPA - Lee F on site to complete vibration testing. Lee requested that pump 2 and 3 be deactivated and pump 1 and 4 be activated. Made the necessary duty changes. | FLAG | stage2_low_confidence | 0.013597 | ML: above threshold (no LLM available) — 0.014 | vibration [equipment_failure] | 0.013597 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | ARPS - Martin from Peel/OCWA control called to inform theyre completing the daily pump rotation | FLAG | stage2_low_confidence | 0.0075086 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075086 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | NMETIB, Activated D1 to keep towers offset | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044383 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | NBW5 - Turbidity Hi alarm outstanding, switched silicate pumps. Assigned silicate pump 1 to duty 1. Will monitor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068306 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | SHTP - UV Reactor 3 Minor fault alarm/low priority alarm. Duty just deactivated, no flow from filters. Emailed David T. | FLAG | stage2_low_confidence | 0.013256 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.013256 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | MKRSEM- Called Toronto and requested two pumps on to reservoir. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064406 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | VNPS- Placed PD7 pumps in manual MAPS- Placed PD7 pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041336 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | HLW2 - Treated Total chlorine Lo/ Combined chlorine LoLo alarms. Well 2 not running, no water directed to users. Values recovered in 5 minutes. Was able to clear alarms. | FLAG | stage2_low_confidence | 0.019161 | ML: above threshold (no LLM available) — 0.019 | not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019161 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YDSS + YNSS Normal *Wrong Book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037081 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | VNPSCD - Sani Sump Pump 1 and 2 Fault and Sump Pump 1 and 2 fault at VNPSP8. Checked site. Shift report indicates to send an email. Will call OIC if high level comes in. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | Connor Smith signing in 1C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | KCETDS- Outlet Total CL2 Res LoLo Alarm. Sudden drop in residual and returned to normal next reading. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066188 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | VNPS PD7- Paced pump 2 in manual MAPS PD7- Placed pump 2 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041838 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | STRS48 - Ian W completing work on the OIT and directed to disregard any historian heartbeat alarm util the work is completed. | FLAG | stage2_low_confidence | 0.0072341 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072341 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | AUEQSJ - Will from Landmark onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005593 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MKRSMR, Patrick F is on site, testing the flood analyzer, level alarms, temp alarm and preforming analyzer maint. Notified Toronto operator Paul to place his pumps to man/off for level testing | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | AUW57- influent free Cl2 lo alarm came in recovered after 3 mins alarm cleared. Treated free Cl2 hi alarm came in spike on well start up and recovered after 3 mins alarm cleared | FLAG | stage2_low_confidence | 0.0088216 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0088216 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | AUPSRR - Post-inj Free chlorine Hi and HiHi alarms. Quick spike for one reading. Duty recently activated. Alarms cleared. | FLAG | stage2_low_confidence | 0.01074 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.01074 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | MAP8 - Tyler C onsite to work on pump 4. As duty 1 about to start place pumps 1 & 2 man/off to prevent duty 1 pumps running. Left pump 3 auto, and man/start pump 4 as requested 9:42 - Tyler C finished at site. Pump 4 in good standing. Placed all pumps back in auto | FLAG | stage2_low_confidence | 0.0089439 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089439 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | MAPS PD7- Noticed Pump 1 was OOS on Pres Switch Low Alarm (Info). Reset alarm. Placed in manual and placed pump 2 into auto. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MMW1- Rob P leaving site as power cannot be restored at this time. Sean P is on site and will be attempting to hook up generator. Once power is restored Sean P will call Rob P to attend site or start pumps remotely. | FLAG | stage2_low_confidence | 0.0094332 | ML: above threshold (no LLM available) — 0.009 |  | 0.0094332 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP - ZW8 Neutralization Exceeded Duration Alarm came in. Checked site. Train 8 is still in neutralization mode. Called Jack P. who informed that this train went through and R-Clean today. Directed to disregard alarm #CONSULT | FLAG | stage2_low_confidence | 0.0079496 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079496 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | VNMCYS - Intrusion alarm. Checked site, unable to clear alarm. Called Rob P who stated that Dwayne L is on site. BLW12 - Travis W is on site to complete operational samples. Travis will be deactivating BLW3 so the system does not overfill. | FLAG | stage2_low_confidence | 0.0080109 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080109 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | GWTP- ZW4 Memb Tank Level Hi alarm, Train 4 in neutralization. Will monitor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057542 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | ANW23- Post-Inj Free Chlorine Fault/LoLo, Pre Inj Free Chlorine Fault/LoLo, Discharge Pressure LoLo. Interlocked High Lift Pumps. Notified Dave T. He will attend site. Notified King Township On Call Operator (Patrick) of likely pressure complaints. 23:12- Dave T. able to run high lift locally and clear interlock. Pumps interlocked on max number of starts. Requested to call Kyle C on call PCS to remove this inhibit. Notified Kyle C. 23:23- Patrick (437-429-3801) from Township of King called back and requested to have Dave T give him a call so that he could relay some more information to a resident that had called in. 00:32- Dave T. finished onsite. Site back to normal operations W11707888 for Dave T W11707895 for Kyle C CMU5 | FLAG | stage2_low_confidence | 0.041419 | ML: above threshold (no LLM available) — 0.041 | fault [equipment_failure] | 0.041419 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | GWTP, ZW1 Shutdown/Permeate Pump Uncommanded Stop alarm, notified Jack P, he is looking int it consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043818 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP - Chris S still onsite, requested to deactivate duty to look into UV intensity on startup issue | FLAG | stage2_low_confidence | 0.0076734 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076734 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | MMW1, Control Panel Power Failure Alarm, Wells currently man/off and aren't able to be placed in the on position. Notified Rob P, Directed to disregard well hi/hihi alarms as there is nothing he will be able to do on his end. Once power is back, RO will place wells in the man/on position. Checked Alectra Power outage map, Power won't be restored till roughly 00:00 - 02:00 23:52, Contacted Alectra has their map says all outages are recovered however MMW1 is still down. Talked with Alectra operator Troy who informed the RO that there is no power outages at 320 Major Mackenzie Drive (MMW1), it may be a site issue. Contacted Rob P to inform him of the updated situation, he is heading to site. Saturday March 7/2026, 00:05, Historian Heartbeat alarm, Contacted Kyle C, he is looking into the heartbeat alarm. Notified Rob P that power has been restored on site however cant place the wells back in man/on position 00:43, Rob P is on site, Notified RO that there is power around the station but specifically in MMW1, no power seems to be available, Rob P requests on call electrician to give him a call. 00:54: Rob P has confirmed that Sean P is heading to site. Rob P has also requested a call from Dan K (Water Manager On call) as he has a few questions about the site. W11714621 CMU5: W11714612 (Rob P) CMU5: W11714621 (Kyle C) CMU5: W11714629 (Sean P) Alectra Operator: Troy | FLAG | stage2_low_confidence | 0.24153 | ML: above threshold (no LLM available) — 0.242 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.24153 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | GWTP- Raw water sample P3 comm alarm came in. Able to reset trends okay sample P1 running in D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0062863 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | ARPS - Peel ammonia analyzer A Airport rd discharge alarm. Ammonia pumps recently switched. Alarm cleared when on the phone with Martin from OCWA. | FLAG | stage2_low_confidence | 0.010498 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010498 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | STW12 - Jack P on site to complete work orders including chlorine analyzer maintenance, turbidity analyzer maintenance, chemical pump inspections and a generator test run. SUETDR - Phil D on site to complete chlorine analyzer maintenance and low temperature alarm test. | FLAG | stage2_low_confidence | 0.016726 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action]; alarm [control_system] | 0.016726 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MAP8 - Pump 2 VFD fault, informed Jacob M. Will follow up with team | FLAG | stage2_low_confidence | 0.0080065 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0080065 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | GWTP - ZW4 membrane tank level hi and hihi switch alarm. Checked site, tank is going through a cleaning sequence. Alarm status changed to normal, alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.0089394 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0089394 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | NMW15 - Treated free chlorine HiHi alarm, switched ammonia pumps. Pump 1 to Duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005943 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | VNPSP8 - PD8 Pump 4 VFD Fault and Pump 4 Not ready alarm came in. Checked site. Ack/reset but alarm is unable to reset. Rotated duties so that pump 4 is no longer duty 1. Placed pump 4 man/off. Will send an email. | FLAG | stage2_low_confidence | 0.020986 | ML: above threshold (no LLM available) — 0.021 | fault [equipment_failure]; alarm [control_system] | 0.020986 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | STRS48 - Jack P. called and requested to place pump back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049373 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | MKRSEM - Low level alarm. Called Toronto Water (Peter) and requested they activate two pumps to push flow to MKRSEM. | FLAG | stage2_low_confidence | 0.0091358 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0091358 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060919 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | ANW23 - Sean P on site to complete a generator ATS switch test. The test will be five minutes. The system duty just deactivated. Deactivated the reservoir duty 1 so Sean P can complete the test. | FLAG | stage2_low_confidence | 0.0085015 | ML: above threshold (no LLM available) — 0.009 |  | 0.0085015 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather +7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | MARS - Called Toronto water (Paul) and requested reduce flow. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063751 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NBW5 - Turbidity Hi alarm, rotated silicate pumps. Assigned silicate pump 1 to duty 1. Will monitor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006439 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | ARPS - Flow lolo alarm. Checked site, all ARPS pumps either manual/off or local/off. Called Peel/OCWA (Jerry) who stated their SCADA team was working on the PLC and needed to shut down the pumps. Jerry has re-activated the pumps. | FLAG | stage2_low_confidence | 0.015464 | ML: above threshold (no LLM available) — 0.015 | scada [control_system]; alarm [control_system] | 0.015464 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | AUW5 - Erick S attending site for chlorinator. Placed well in man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050039 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | MMW1- Control Panel Power Failure, Well HiH Alarms Notified Gary P. Requested to place wells 8 and 13 man/on CONSULT | FLAG | stage2_low_confidence | 0.0085042 | ML: above threshold (no LLM available) — 0.009 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0085042 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMTKKC- Ammonia Pump 1 Failed to Start. Pump 2 took over in duty 1. Cleared alarm. | FLAG | stage2_low_confidence | 0.011303 | ML: above threshold (no LLM available) — 0.011 | failed [equipment_failure]; alarm [control_system] | 0.011303 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | STETBR - Hi level alarm, placed STW12 and STW3 back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053612 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | NMVCBA - Placed back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005522 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | KSTP - Noticed Finished Water Turbidity Spiked on Duty startup for one minute and back to optimal range. High lift pump 3 running normally. Raw water Turbidity fault alarm - disregard as per SCADA review. | FLAG | stage2_low_confidence | 0.016331 | ML: above threshold (no LLM available) — 0.016 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.016331 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | QVW12- Donald M on site booster pump airlocked. Will backflush well and troubleshoot booster pump AUW57- Treated free Cl2 hi alarm came in. Checked trends spike on start up and recovered after 6 mins MKRSEM- Reservoir lo alarm came in. Called Metro spoke with Zoran to start 2 pumps to fill reservoir | FLAG | stage2_low_confidence | 0.019878 | ML: above threshold (no LLM available) — 0.02 | oos [equipment_failure]; alarm [control_system] | 0.019878 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | QVW12. Placed well 1 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004264 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | STW1/3, Placed wells back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042639 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS+NYWS normal Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046111 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | MARS - Hi level alarm, activated VNRSKS duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0050331 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | NMETIB- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053242 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | STW12- Placed well 2 man/on STW3- Placed well 3 man/on For STETBR Fill Cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036089 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | AUW5 - Aurora Duty deactivated, placed well pump from man/on back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051344 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | SHTP - UV Reactor 1 Minor fault alarm. David T called and requested disregard Minor alarms. | FLAG | stage2_low_confidence | 0.011666 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011666 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | STRS48 - High Lift Pump 1 Failed to Stop Alarm came in. Checked site. Duty had recently deactivated and pump was in the process of shutting down. Ack/reset alarm and pump shut down and alarm cleared | FLAG | stage2_low_confidence | 0.019217 | ML: above threshold (no LLM available) — 0.019 | failed [equipment_failure]; alarm [control_system] | 0.019217 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | HLW1 - Jordan B and Darrick S on site to complete a chlorine leak detection test and complete maintenance on the chlorine analyzer. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | BLW12- Travis W onsite for work orders including generator run, CL17 maintenance, turbidimeter maintenance, hypo system cleaning and health and safety. | FLAG | stage2_low_confidence | 0.012286 | ML: above threshold (no LLM available) — 0.012 | work order [maintenance_action] | 0.012286 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | MARS- Cell1 (North) Lvl Hi Alarm AURSBS- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043329 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | AUW57 - Erick S onsite working on chlorinator 2. Was impacting chlorinator 1 giving hi influent on dose. Replacing tube | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006342 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | QVW34 - Man/stop well 3 as treated chlorine approaching hihi level. Cleared contact tank. QVW12 - Influent free chlorine lolo, Locked out wells. Informed Will M regarding wells GWTP - Parth P finished at site QVW12 - Donald M called back that he will head to site regarding well 1 issues. CMU = 11714540 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059462 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | QVETQS - Inlet Free chlorine residual HiHi switch and Hi alarms at duty start. Will monitor. Alarms cleared in 5 minutes. | FLAG | stage2_low_confidence | 0.0081463 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0081463 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NBW2 - Historian Heartbeat alarm. Checked site, the well was active when the alarm triggered which shut down the well. The alarm status changed to Normal and the well activated again in auto mode. Alarm cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.011726 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.011726 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | KSTP - Finished Water Turbidity HiHi alarm came in. Checked site. Hi lifts are interlocked. NTU is back to optimal range. Called Stephen B. for direction to clear alarm. No answer, will try again 22:15 - Stephen B. called back and directed to reset alarm as turbidity was only hihi for 1 minute. Reset alarm and hi lift pumps are now running | FLAG | stage2_low_confidence | 0.011473 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011473 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS Normal STETBR - Tower Level Hi alarm came in. Placed STW3 back to auto, as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.004165 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | STETTL- Sodium Adverse Date: March 10/26. 10:52AM Lab Contact: Mei Wang, 905-686-0041 Ex. 4318 Submission #- 2200023333 Sample Date: March 4/2026 Sample Type: Sodium Sampler Name: Jack Palmer Sample Site Location: STETTL Remote Operator: Connor S Notified Dan Z and East Ops and emailed adverse form. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0019377 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | MAPSN1- Kingsley M working on server update. 11:34- Work completed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034766 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 3 at MAPS 05:03 - all changes have been reverted | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026569 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | NBW3 - Influent Free Chlorine LoLo switch alarm came in. Well recently activated. LoLo influent locked out the well. Influent levels came back up within 2 mins. 20:47 - Restarted the well and all alarms cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.006203 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMVCBA- Placed back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054883 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | ANW23 - Sean P onsite for diesel Pm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043239 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | H1GWTPP1 - Kingsley M restarting hub server | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044799 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP- Stephen B leaving site. Site back to normal. Requested to activated duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068538 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP- GAC 4 Flow Control Valve Deviation Alarm. Disregard as per SCADA Report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0057677 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | QVW12- Influent free lo alarm came in on well start up followed by lolo lock out alarm. Well did not pass contact tank. Notified Donald M. Will attend site created CMU5 W11714768 placed both wells in man/off QVW34- Placed well 4 in man/on. QVETQS- System pressure lo alarm came in recovered after 3 mins alarm cleared NMVCBA- Placed valve in man/open at 40 L/s VNPS PD7- Placed P3 in man/off MAPS PD7- Placed P3 in auto #CMU5 | FLAG | stage2_low_confidence | 0.009983 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.009983 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | QVW34- Adjusted chlorinator 1 on well 4 from 85% to 87% as influent is below target 15:10-QVW34- Adjusted chlorinator 1 on well 4 from 87% to 89% as influent is still below target | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005868 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | VNPS PD7- Placed P2 in auto MAPS PD7 - Placed P2 man/off STW12/3- Placed P1/3 in man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040705 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather +3C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: 10C and sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004454 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | ARPS - Martin from OCWA called, Completing daily pump duty rotation. Turning off pump 7 and turning on pump 5. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061487 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | KSTP - CO2 adjusted pH lolo alarm. Checked site, plant is active. Trending shows a dip of the CO2 adjusted pH that is recovering. High lift pumps have interlocked. Shift report states that the raw water pH alarms are a disregard. Will reset alarm as it recovers above the lolo alarm setpoint. KSTP - 21:31 - Noted the conduit water level has dropped significantly due to both filters being active. Also noted the raw water turbidity alarm disregard does not apply to this reading. Contacted Jack P who will check SCADA. KSTP - 21:33 - Settl water conduit level lolo alarm. Low lift pumps interlocked due to the CO2 adjusted pH lolo alarm. On call operator has been contacted. KSTP - 2201: Jack P called back to inform that the CO2 reading recovered, the low lift pumps have activated and the conduit level has recovered. Jack stated that if the alarm triggers again the system duty can be deactivated which will result in the plant deactivating. #consult | FLAG | stage2_low_confidence | 0.065061 | ML: above threshold (no LLM available) — 0.065 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.065061 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | RHMCMD - Closed valve in manual mode YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004192 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | GWTP- Joe M backwashing GAC 4 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041978 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | MKRSMR/MKPSSA - Toronto Water has activated one COTFA pump in manual mode to fill MKRSMR as requested. Valves have rotated and reservoir is now in receiving mode. Activating one pump at MKPSSA in manual mode for fifteen minutes as directed by Dan Z. | FLAG | stage2_low_confidence | 0.0154 | ML: above threshold (no LLM available) — 0.015 |  | 0.0154 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | RHPSWA - Benson S onsite testing flood alarm, health & safety, temp, PRV | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | NMVCBA- Placed valve in man/open at 40L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044166 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | QVW12- Well pump 1 VFD not ready and speed OOR both wells in local well 2 running. Called Lee F. working on well 1 wasting valve and will m running well 2 in local | FLAG | stage2_low_confidence | 0.0078775 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078775 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP, UV Reactor 2 Critical Fault, notified Joe M, he is looking into it | FLAG | stage2_low_confidence | 0.0079421 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0079421 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | Connor Smith signing in 7C Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041865 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | SHTP- Filter 3 Post Rinse NIT High Alarm came back in. Had gone through a backwash after the first time it came in. Notified Dave T. He will take a look. 21:53- Dave T put it through another rinse. Requested a call if it comes back in. 22:07- Alarm came in again. Dave T will attend site. 02:14- Dave T leaving site. Filter 3 back in production. Reservoir 1, 2 Level Lo Alarms. Duty almost complete. Will recover once it deactivates. W11707880 CMU5 | FLAG | stage2_low_confidence | 0.0094368 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0094368 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | QVW34- Eric S onsite troubleshooting Total Cl analyzer. Requested pumps man/off for work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054958 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | GWTP - ZW3 train shutdown, turbidity fault ZW3. Informed Jack P, will look into issue | FLAG | stage2_low_confidence | 0.0086187 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure] | 0.0086187 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | SHTP- Power fail on site. Filter panel phase monitor alarm/ UV reactor1,2,3 minor faults came in. Plant not active at time of power loss. Notified David T. Directed to ack reset all alarms as power is restored. UV alarms would not clear and David T will take a look on SCADA #consult | FLAG | stage2_low_confidence | 0.021865 | ML: above threshold (no LLM available) — 0.022 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.021865 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | KCETDS, Activated D1 to help prepare for Maple to Jefferson for later tonight | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052258 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | MKRSEM- Called Toronto water (Zoran) and requested start 2 pumps to fill the res. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053195 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | STPSMR - Patrick F running generator and will change chlorine cylinders with Jack P. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070853 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | GWTP - Jackie S onsite testing eyewash alarms. Microfiltration room low temp, disregard as old alarm from gen run | FLAG | stage2_low_confidence | 0.008985 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.008985 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | KCETDS - Activated duty 1 YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0029843 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | Starting Maple to Jefferson 00:30, Maple to Jefferson Feed failed, No alarms active, VC_MV3 failed to open. Placed valve originally to 10% while waiting for RES_MV4 to close. At this time VC_MV3 did not get to the 10% mark. Once RES_MV4 was fully closed, Placed VC_MV3 to 100% to see if the valve will unstick. After waiting roughly 15 minutes, Valve failed to open with no alarms present. Reverted the maple to Jefferson feed. Will send email to operators to inform them of this issue. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; alarm [control_system]; alarms [control_system]; valve failed [infrastructure] | failed [equipment_failure]; alarm [control_system]; alarms [control_system]; valve failed [infrastructure] |  | 1 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | GWTP - Rick L working on ZW1, Joe M called, directed disregard alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0064366 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | EGMCDD - Arthur L leaving site. This meter chamber is now live, alarms should be responded to as normal. | FLAG | stage2_low_confidence | 0.0099991 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0099991 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | GWTP - Joe M draining GAC 4, directed disregard low level alarms. GAC 4 man/off for the night. | FLAG | stage2_low_confidence | 0.0072478 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0072478 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NMETIB - Activated duty 1 to help offset with NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046546 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NBW2 - Jake M on site to complete work orders including a chlorine leak detection test, chlorine analyzer maintenance, PRV inspection and silicate injection point inspection. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; leak [infrastructure] | work order [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | GWTP - Sutton header pH hi, sudden spike on trend when no flow going through line as duty not active. Informed Stephen B, appears to be a gradual slow decline on the pH. Speaking with Stephen we will monitor for now, duty 1 active now shows no change in reading as continuous its slow decline. | FLAG | stage2_low_confidence | 0.014341 | ML: above threshold (no LLM available) — 0.014 |  | 0.014341 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | BVPS - Deactivated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041052 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: 16C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004454 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water(Zoran) and requested start filling Res with 2 pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053377 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | KSTP - CO2 Adjusted pH LoLo alarm. Value is in normal range, was able to clear alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057864 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | QVW34 -Treated total chlorine residual low alarm. Well not active, no water directed to users. Value recovered in 6 minutes, cleared alarm. | FLAG | stage2_low_confidence | 0.0073576 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073576 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | STW12 - Place well 2 man/on STW3 - Place well 3 man/on. This was done as Zone 1 tower activated | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047578 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MARS- Cell1 (North) Lvl Hi Alarm RHRSTR- Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043706 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | STW3 - Place well man/on for Zone 1 tower fill | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045365 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | NMETHW - Deactivated duty 1 to maintain level offset from NMETIB. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049325 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | STRS48 - High lfit pump 1 failed to stop alarm. Checked site, system duty recently deactivated. High lift pump 1 has stopped and there is no flow being registered leaving the pumps. Cleared alarm. | FLAG | stage2_low_confidence | 0.018952 | ML: above threshold (no LLM available) — 0.019 | failed [equipment_failure]; alarm [control_system] | 0.018952 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | Adam Button signing in 0C Raining | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041938 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | AUW14- Placed wells 2/3 in auto AUW57- Placed Well 5 in auto MAPS PD7- Placed P1-3 in man/off VNPS PD7- Placed P2/3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003755 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | ARPS- Martin from Peel called ton inform ROC they will be switch from P6 to P7 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052703 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | NMETIB- Activated D1 at 65% to offset from NMETHW as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00502 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MMW1- Rob P req Terry Cs number to have them attend site to get generator running on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052271 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | AUW14, Joe D on site running the generator, he has placed the wells man/off for the time being | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053279 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS+NYWS Normal QVW12- Donald M on site to backflush and trouble shoot booster pump. Donald M notified ROC that site has some flooding issues and a transformer on site is close to being affected by the flooding. Checked All Pipes to ensure no water main is in the vicinity of flooded area. Watermain locate to the west of the flooded are but storm ditch and connecting culvert are draining into flooded area. Notified Roads Dispatch spoke with Jen who will dispatch a roads operator. Called Hydro One spoke with Scott to inquire about safety concerns if flooding of transformer on site. Scott confirmed with Hydro one lineman that there are no safety concerns. updated Donald M of situation 16:24-QVW12- Donald M placed booster P2 OOS and will backflush and start up well | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; oos [equipment_failure] | flood [critical]; oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | BLW12 - Power restored, generator stopped. Well 2 was running. Well 2 Pump VFD fault and Well 1&2 Pumps OOS alarms. ET is filling very slowly. Notified Joe M. He will attend site to reset pumps. # CMU 5 W11733508 | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | VNPS - Benson S and Tim H on site to complete work orders for the surge tanks. Benson and Tim Have requested that all VNPS pumps be deactivated. Tim H directed that PD8 can be filled using RHPSWA pumps. Swapped the PD7 supply pumps to MAPS. Estimated work duration is one hour. Activated RHPSWA pump 2 and also activated RHRSTR duty 1 to push additional flow to MARS system. | FLAG | stage2_low_confidence | 0.035103 | ML: above threshold (no LLM available) — 0.035 | work order [maintenance_action] | 0.035103 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | Carter Dunn Signing In, -7D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | NMETIB - Activated Duty 1 to offset NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044585 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | VKRSKS - Switched feed from MAPS PD7 (P2,3) to VNPS PD7( P2,3). Duty not active. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005304 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | SHTP - Jordan B leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055052 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | VNP7 - Place pump 1 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042961 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | AUW57 - Silicate pump 2 fault alarm (placed man), Silicate pump 1 fault alarm outstanding, Silicate pumps not available alarm. Placed Well 5 pump man/off. Will notify OP. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | STRS48- High lift P1 failed to stop alarm came in. Pump shutdown on D1 deactivation cleared alarm QVW12- Donald M done on site informed ROC well is running okay but residuals may be lower . Placed well 1 back in auto. Combined Cl2 lo alarm came in. Will continue to monitor QVW34- Placed well 4 in auto | FLAG | stage2_low_confidence | 0.020389 | ML: above threshold (no LLM available) — 0.02 | failed [equipment_failure]; alarm [control_system] | 0.020389 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | GWTP - Rick L on site for annual calibrations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056122 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | STPSMR- Placed pump 1 and 2 back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044852 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMVCBA- Placed valve manual 20L/s to keep NMETIB and NMETHW offset. 23:56- Placed valve back into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040996 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | NMETIB- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053242 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | KSTP - Fin Water Fluoride Res Hi alarm at duty start. Slowly dropping. Notified Joe M, he activated Duty remotely. # Consult | FLAG | stage2_low_confidence | 0.0092363 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0092363 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | BLETNL- Wes from town of Stouffville is flushing in area. Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050555 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | SHTP - Filter 1 and Filter 3 High turbidity alarm after Filter 2 backwash. Disregard as per SCADA review. Cleared alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0070904 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | QVW34- Treated total Cl2 lo alarm came in. Wells not active and no water directed to users. trends recovered after 3 mins alarm cleared | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | MKRSEM, Notified Toronto operator Medhi to start 2 pumps to fill the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049799 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | JFPS- Evgeny S rebooting OIT. Placed pumps man/off. Disregard Heartbeat Alarm. | FLAG | stage2_low_confidence | 0.0076233 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076233 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | Carter Dunn Signing In, 1D/Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041599 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | AUW57, Joe D on site, working on Cl2 booster 2. Directed to place chlorinator 2 back to auto | FLAG | stage2_low_confidence | 0.0096452 | ML: above threshold (no LLM available) — 0.01 | oos [equipment_failure] | 0.0096452 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | BLW3 - Joe W on site to complete a generator test on load with the well pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049629 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MARS, Notified Toronto operator Paul to increase the flow to MARS as the level is on the lower end | FLAG | stage2_low_confidence | 0.0074069 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074069 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | QVW12- Treated Free Chlorine HiHi Alarm. Value recovered after a couple of minutes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059168 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | KSTP, Fin Water Fluoride lolo, notified Joe M, directed to rotate Fluoride pumps, Placed Fluoride pump 2 in D1 and pump 1 in D2. If residual doesn't come back up within the hour, Joe M directed to place the highlift pumps man/off for the night 01:54, Placed high lift pumps 2/3/4 in man/off as the fluoride residual has not recovered, as per Joe M consult | FLAG | stage2_low_confidence | 0.0074912 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074912 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | KCETDS, Metering Chamber Flood Alarm, shift report doesn't say anything about this alarm, contacted Jordan B, directed to disregard, consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | QVW34 - Rick L finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042327 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | GWTP - Jackie S doing chlorine analyzer maintenance for wash water and lake | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068087 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | AUW5 - Influent free chlorine hihi on startup, came back within range next reading | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005312 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | GWTP - Jackie S. testing chlorine leak, she is aware duty just activated | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | GWTP - Rick L and Parth P finished for today and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064424 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | AUPSWS- Donald M onsite for work orders, running generator, flood alarm and low temp. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | SHTP, UV Transmittance lo alarm/Filter 1/3 turbidity hi alarm notified Jordan B of the UV alarm, he will look into it 16:21, Jordan B called back and directed to disregard, Filter 3 was back washing which cause the LO UV Transmittance alarm consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0050168 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | QVW34 - Chris I working on site, taking generator offline for the duration of the work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051605 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | STW12 - Place well 1 back in auto STW3 - Place well back in auto as Zone 1 duty 1 stopped | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046847 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | Carter Dunn Signing In. -3D/Snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042339 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | VNPS - Benson S on site to complete station checks and directed to activate the duty at RHRSTR so that BVPS activates to push flow and activate the chemical system. | FLAG | stage2_low_confidence | 0.0097077 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097077 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | Adam Button signing in 8C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041579 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MMW1- Kyle C informed ROC that Trends are working locally on the OIT, but they having issues with them on the DMZ and has reached out to Kevin W from network. May end up being outstanding until Monday if networking isn't able to establish connection. | FLAG | stage2_low_confidence | 0.011733 | ML: above threshold (no LLM available) — 0.012 |  | 0.011733 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | GWTP - GAC 4 flow control valve deviation alarm outstanding. Disregard alarm as per shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063141 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | VNP7 - Place pumps man/off MAP7 - Place pumps 3 & 1 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041504 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | NBW5 - Jake M on site to complete work orders including a generator test run. chlorine leak detection test, chlorine analyzer maintenance and chlorine/silicate system inspection and maintenance. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; leak [infrastructure] | work order [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | RHPSWA- Intrusion alarm, FMC will notify Corp security. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067058 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | 11:40 ARPS - Airport Rd discharge flow low low alarm. Called OCWA ( Benish). He is on the phone with SCADA crew, will investigate and call back. 12:01 ARPS Alarms cleared, Pump 6 started in auto. 12:12 ARPS - Benish from OCWA called with update, Electrical crew was performing UPS alarm testing, causing tank level quick drop and YR pumps interlock. Back to normal operations, pump 6 is running on auto/ Duty 1. | FLAG | stage2_low_confidence | 0.015933 | ML: above threshold (no LLM available) — 0.016 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.015933 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | NBW5 - Tim H at site for testing of well, issue with turbidity. Running well in man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054416 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | MKRSEM, Medhi from Toronto called, he is dropping 1 pump as they are having issues on their end | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056873 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-28 | ROC General | ROC | Connor Smith signing in 1C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041757 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, weather: -1C and sun. Please see attached photos of the paper logbooks. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-28 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | MKRSEM- Called Toronto and requested two pumps on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060407 | 0 | 0
2026-03 | 2026-03-28 | ROC General | ROC | Christian Van Beek signing in. Weather: -1C and sun | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045375 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | STW12- Placed well 2 into auto STW3- Placed well into auto for completion of STETBR Fill Cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004727 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | VNRSKS - Activate duty 1 to help bring down MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045831 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | SHTP - Filter 2 & 3 turbidity hi, reading came back within range | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049395 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | Connor Smith signing in 7C Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041865 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP - Parth P, Rick L and Art P finished and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063567 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | SHTP- Filter 3 Turbidity Hi Alarm. Backwash just completed. Disregard as per SCADA Report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0061155 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | NMW136 - Lee F. is on site to change the oil for well 13. Lee will be placing the well in local. Duty is not active and well is not running. Confirmed with Alex B. | FLAG | stage2_low_confidence | 0.013185 | ML: above threshold (no LLM available) — 0.013 | not running [equipment_failure] | 0.013185 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | KSETDP- Mark from Process Optimization leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060999 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | MAPS - Dave from property services leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059927 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | HLW1 - Combined Chlorine Lo alarm came in. Well is not running and water is not being directed to users | FLAG | stage2_low_confidence | 0.012369 | ML: above threshold (no LLM available) — 0.012 | not running [equipment_failure]; alarm [control_system] | 0.012369 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | JFPS - Benson S on site completing a generator run test and has directed to activate one pump to place the generator on load. Activated pump 3 in manual mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071999 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | STW3- Placed well man/on for STETBR Fill Cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045211 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | KSTKWP- Jerry Z. Working on Cl analyzers. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005807 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | Ethan U signing in Weather -0. Snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035846 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | Pest control visiting sites: VNRSKS, RHRSTR, VNPS, RHRSWA. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063201 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: 0C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044345 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | STPSMR, Dominic from Honeywell is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054642 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-11 | ROC General | ROC | Connor Smith signing in 3 C Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041948 | 0 | 0
2026-03 | 2026-03-10 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-13 | ROC General | ROC | JDSS, Stephen from AB Project management, They are draining the fuel lines to the generator, disregard alarms on site till they refuel the lines | FLAG | stage2_low_confidence | 0.011279 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011279 | 0 | 0
2026-03 | 2026-03-01 | ROC General | ROC | Adeela Khan signing in. Weather: -11C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044737 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | Christian Van Beek signing in. Weather: -3C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | KSTP - Drew from Ferguson onsite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055791 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | STETBR - Tower low level alarm. Activated STW3 as per the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057454 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | STPSMR - Drew from Ferguson Electric on site for a team meeting. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060747 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP- Gas Chlorinator 5,6 Hi Vacuum Alarms. Notified Stephen B. Requested a call if residuals start to drop. GAC 4 Flow Control Valve Deviation Alarm. Disregard as per SCADA Report KSTP- Post Chlorinator 2 Lo Vacuum Alarm. Alarm cleared. 02:00-GWTP- Contact Chamber 2 Chlorine Lo Alarm. Notified Stephen B. Requested to place KSTP High Lift pump 4 in manual to continue running and deactivate duty. Stephen B will attend site. Placed GWTP High Lifts in manual. Deactivated SUETDR as KSTKWP close to duty start. 03:55- Stephen B called and will need assistance working on the chlorinator. Requested to call Ben H. Notified Ben H. He will attend site. W11702382 For Stephen B W11702390 For Ben H CMU5 | FLAG | stage2_low_confidence | 0.024759 | ML: above threshold (no LLM available) — 0.025 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.024759 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | AUSSYS - Orlando from Property services on site for a short visit and is now leaving. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067286 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | KSTP - CO2 Adjusted pH LoLo alarm came in. Checked site. pH level is within optimal range and alarm cleared on its own | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070107 | 0 | 0
2026-03 | 2026-03-09 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-05 | ROC General | ROC | JDSS, Theodor from AB is on site, turning on generator to work on fuel lines | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064416 | 0 | 0
2026-03 | 2026-03-04 | ROC General | ROC | NMETYS - Denis from Landmark on site to complete work for new door landings. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065048 | 0 | 0
2026-03 | 2026-03-20 | ROC General | ROC | KBSP - Theodore doing some grinding work, call if fire alarm goes off (289-390-0704) | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-27 | ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-19 | ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | STPSMR - Drew from Ferguson Electric was on site earlier today and is now leaving. Site is secure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071227 | 0 | 0
2026-03 | 2026-03-24 | ROC General | ROC | KSSP - Garrick from Ferguson electric on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055882 | 0 | 0
2026-03 | 2026-03-26 | ROC General | ROC | HLPSYS- Dominic from Honeywell onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057485 | 0 | 0
2026-03 | 2026-03-22 | ROC General | ROC | Adeela Khan signing in. Weather: 0C and cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044604 | 0 | 0
2026-03 | 2026-03-17 | ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-27 | ROC General | ROC | Christian Van Beek signing in. Weather: -6C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-18 | ROC General | ROC | KSSP - Garrick and Drew from Ferguson electric leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063265 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | NMETHW - Kalid from AIM leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056855 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-16 | ROC General | ROC | AUPSWS - Kyle R from Maintenance replacing floats. Corrections/ wrong book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068149 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | QVW34 - Joe D onsite, will be running well in man/on to help locate leak. | FLAG | stage2_low_confidence | 0.0081072 | ML: above threshold (no LLM available) — 0.008 | leak [infrastructure] | 0.0081072 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | MAPS/JFRS- Initiated Maple to Jefferson Feed 03:45- Reverted changes | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035027 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | Ethan U signing in Weather 0. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | VNP7 - Place pump 1 & 3 auto MAP7 - Place pump 1-3 man/off. Done to pull more from Teston res and less from MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052018 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | KCETDS - Outlet total Cl2 res lo, reading came back within range next reading. Cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059506 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | SHTP- UV Transmittance OOR CMU5 for Cole W from Friday Night Shift. W11765112 CMU5 Chamber 2311- Chamber Entry Assistance CMU5 for Cole W from Saturday Day Shift requested by Cristina S. W11765120 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047622 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | Christian Van Beek creating a test log entry at the request of Jennifer Chung. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069174 | 0 | 0
2026-03 | 2026-03-28 | All Water System ROC General | ROC | VNPS- Placed PD7 duty 1 pumps in manual MAPS- Placed PD7 duty 1 pumps in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043899 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | HLW1 - Combined chlorine low alarm. Checked site, well was recently placed manual/off. No water being directed to users. Trending shows a dip of the combined chlorine reading following well shutdown is normal. Will continue to monitor site to ensure reading recovers. | FLAG | stage2_low_confidence | 0.013924 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system] | 0.013924 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | AURSBS- Activate duty in preparation for Maple to Jefferson Feed | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064826 | 0 | 0
2026-03 | 2026-03-29 | All Water System ROC General | ROC | SHTP - Well 2 Uncommanded start alarm. Checked site, the plant is currently active. Able to reset alarm, well activated again. | FLAG | stage2_low_confidence | 0.0072378 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072378 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | KSETDP - Gas chlorinator 2 fail to close alarm. Checked site, system duty recently deactivated. Chlorinator 2 showing 16% open following duty stop. Able to clear alarm but chlorinator still showing open. The chlorine gas injector solenoid valve is closed and the chlorine booster pump is not active meaning chlorine is not being drawn through the system. Placed chlorinator in manual mode and tried to close, chlorinator did not close. Returned chlorinator to auto mode and sent email to area operations. system duty will not activate until late morning. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | MARS - Tegbeer from OCWA called to inform that he will be completing the daily pump switch. Will switch from pump 5 to pump 6 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065666 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | SHTP - Site hydro power failure alarm and associated equipment fault alarms. Checked site, plant was active when the alarms triggered. The generator is not running and the ATS is pointing to utility hydro indicating a short power failure. High lift pumps are currently active and pushing flow to the system, reservoir level is high. No concern for system deactivation at this time. Attempted to reset alarms. Both air compressors on site have failed and are showing in local mode on SCADA, unable to clear alarms. High lift pump 1 has faulted on a VFD fault and cannot be reset. High lift flow is much lower than normal. Contacted Cole W who will attend site to reset the systems that have faulted. Created CMU5#W11768966 #consult #CMU5 | FLAG | stage2_low_confidence | 0.22034 | ML: above threshold (no LLM available) — 0.22 | sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; failed [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.22034 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | STW3 - Jack P. headed to site to assess the LoLo switch alarm and sampling CMU5 Created W11769468 #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0033317 | 0 | 0
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Maximo server down from 10-16:00. Attached are logbook entries | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-31 | All Water System ROC General | ROC | NBW3 - Influent Free Chlorine LoLo alarm came in. Checked site. Well was found man/off. Called Jacob M. who is aware and placed the well in manual | FLAG | stage2_low_confidence | 0.007923 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.007923 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | EZ Max Mobile Access Restored Mar/31/2026 04:00 - 06:45 | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-31 | All Water System ROC General | ROC | AUPSRR, Kingsley M resetting OIT on site, Disregard historian heartbeat alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071247 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | MAPS PD7, Placed pump 2 man/off VNPS PD7, Placed pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0028546 | 0 | 0
2026-03 | 2026-03-31 | All Water System ROC General | ROC | HLETYS, Rick L/Parth P on site working on the Cl2 analyzers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045098 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | ARPS, OCWA operator Martin called, he is rotating pumps on site. Turning off pump 7 and turning on pump 5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056334 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP, Rick L on site doing annual calibrations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056072 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | SHTP - David T onsite testing turbidimeter, temp, backwash tank high level, eyewash | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070803 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | QVW12 - Lee F finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042149 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW3 back to auto as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058093 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | MKETFA - Peter from Toronto Water called to inform he needs to shut down the active-duty pump to exercise a valve. Informed Peter that out tower level is on the low side, but the short duration exercise should be okay. | FLAG | stage2_low_confidence | 0.013277 | ML: above threshold (no LLM available) — 0.013 |  | 0.013277 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | MTW3 - Travis W onsite for chlorine & silicate inspections, leak detector test, running generator, health & safety, Turb and chlorine maintenance | FLAG | stage2_low_confidence | 0.011225 | ML: above threshold (no LLM available) — 0.011 | leak [infrastructure] | 0.011225 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | KCETDS - Dave T on site to complete work orders including chlorine analyzer maintenance, hi/low level alarm test and the low temperature alarm. Dave T will be completing an isolation test today, KCETDS will be isolated from the distribution system and the system will be supplied by KCETFS and the wells. | FLAG | stage2_low_confidence | 0.037421 | ML: above threshold (no LLM available) — 0.037 | work order [maintenance_action]; alarm [control_system] | 0.037421 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | AUPSRR - Ammonia pump 2 uncommanded stop alarm. Duty recently activated. Cleared alarm. System restarting. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063529 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | QVW12 - Sean P onsite to run site with generator. Deactivated duty to NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052005 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | ARPS, Binnish from OCWA is stopping pump 6 and starting pump 5 STW3, Placed well 3 man/on as STETBR is filling | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042428 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | ARPS - David from Peel informed of another switch to pumps, placing pump 6 in duty 1 NBW5 - Discharge press lolo, well shutoff. Followed up with Jacob M onsite. chlorine injector blew off, working on well now. | FLAG | stage2_low_confidence | 0.0080714 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080714 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | NBW5 - Jake M finished and leaving site. Jake is leaving the well manual/off. OCO Jordan B will decide if the well goes back into service. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006976 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | Wrong logbook | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051414 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | NMW12- Treated total chlorine and combine chlorine residual low alarms. Well not active no water directed to users. Will continue to monitor. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | NMW136- Influent Free Chlorine HiHi Alarm. Recovered next reading. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0056026 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | QVW34 - Will M onsite testing chlorine leak | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | AUPSOH - Joe D onsite running generator and chlorine analyzer, placing pumps man/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070992 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | NMW136 - Christian B onsite w Ben H to work on chlorine, silicate, and ammonia system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054027 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | GWTP - ZW2 membrane tank level hi alarm. Checked site, filter 2 is going through a cleaning process. Trending shows the tank level is slightly above the tank high level alarm. Will monitor site, tank level should drop and cleaning sequence progresses. | FLAG | stage2_low_confidence | 0.013031 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.013031 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | MMW1, Dan B called, informed ROC that the power has been restored on site, Dan B switching generator off to go back to utility power | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063766 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | YWS + NYWS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004717 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated in schedule mode. Trending shows a sharp dip of the influent free chlorine reading which interlocked the well pump. The influent free chlorine reading recovered quickly after the interlock. Placed the well manual/off, rotated the chlorinator duty back to chlorinator 2. Placed the pump back in auto mode and cleared alarms. Monitored well start. | FLAG | stage2_low_confidence | 0.028415 | ML: above threshold (no LLM available) — 0.028 | alarm [control_system]; alarms [control_system] | 0.028415 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | YWS + NYWS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039302 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | STW12 - Place well 1 back in auto STW3 - Place well back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004151 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | GRTPLL - Low Lift Surge Relief Valve Open alarm at duty shutdown, was able to clear alarm. | FLAG | stage2_low_confidence | 0.0081364 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081364 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | QVW12, Donald M is leaving site, requested that the well run for a few hours after it clears the contact tank. When it reaches 21:00, will place the well back to auto QVW34, While Donald M was leaving site, notified Donald M that QVW3 is currently man/off, directed to leave it off at this time, directed to rotate duty so well 3 is in D5 and well 2 is in D2. | FLAG | stage2_low_confidence | 0.011147 | ML: above threshold (no LLM available) — 0.011 |  | 0.011147 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | BVOPLAM Server- Kingsley M rebooting server | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058986 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | KSTP - Carbon Dioxide HiHi alarm came in. Checked site. Duty recently deactivated. Value was still within hihi levels. Called Stephen B. Levels went back to optimal range and alarm cleared on its own. Stephen B. directed to give a call back if this alarm comes back in. GWTP - High Lift Free Chlorine Lo alarm came in. Stephen B. directed to disregard alarm as there may be an issue with the analyzer. Would like a call back if the clearwell is affected #CONSULT | FLAG | stage2_low_confidence | 0.021863 | ML: above threshold (no LLM available) — 0.022 | alarm [control_system] | 0.021863 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MMW1- Terry C and Sean P done on site generator should have enough fuel until tomorrow afternoon. Terry C has truck with fuel and will refuel tomorrow. If generator fails due to lo fuel Terry C will attend site | FLAG | stage2_low_confidence | 0.0091749 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091749 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | YWS+NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048245 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | STRS48 - Hi lift pump 1 failed to stop alarm came in. Checked site. Both pumps are off. Ack/reset alarm and alarm cleared | FLAG | stage2_low_confidence | 0.01344 | ML: above threshold (no LLM available) — 0.013 | failed [equipment_failure]; alarm [control_system] | 0.01344 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | MTW12- Travis W on site for turbidity analyzer maintenance | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044813 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | NBW5 - Turbidity hi alarm came in. Checked site and well is running. Noticed turbidity levels trended upwards and then rapidly came back down. Still within hi limits. Called Jacob M. who informed he is on site flushing and triggered this alarms | FLAG | stage2_low_confidence | 0.011726 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.011726 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | VNPS- Placed PD7 Pump 2 in manual MAPS- Placed PD7 Pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041696 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | KSTP, Raw Water Turbidity Fault, as per Jack P shift report, directed to disregard | FLAG | stage2_low_confidence | 0.011068 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure] | 0.011068 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | VNRSKS - Switched feed from MAPS PD7(pumps 2,3 man/off) to VNPS PD7 (pumps 2,3 to auto). | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055067 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | NMW15- Influent free chlorine residual low alarm, quick dip at duty start . Alarm cleared. NMW136 - Influent free chlorine Hi alarm, quick spike at duty start. Alarm cleared. | FLAG | stage2_low_confidence | 0.0072216 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072216 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | JFRS - Deactivated duty 1 and 2 in preparation for MAPS to JFRS Feed run | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051294 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | KSETDP- Post Injection Free Chlorine Lo Alarm. Tower is offline and isolated. | FLAG | stage2_low_confidence | 0.0075889 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075889 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP - Parth P, Rick L and Art P on site to start annual calibrations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062967 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | ARPS- Jerry from Peel called. Communication alarm shut down their pump. Working on getting it back up and running. He will call back with an update. | FLAG | stage2_low_confidence | 0.010616 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010616 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | HLW2 - Treated total chlorine lolo, combined chlorine lolo. Well is man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051299 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | AUW14 and AUW57 - Placed all well man/off to let AURSBS drain due to higher levels at MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055837 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | MKETFA - Toronto Water (Brett) called and informed that they are turning pump off and testing PRV in their system. | FLAG | stage2_low_confidence | 0.0081781 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081781 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | RHRSTR - Deactivated duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041621 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | NMW12 - Influent free chlorine residual HiHi alarm at duty start up. Value back to normal, cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0062544 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NBW2 - Influent chlorine residual low alarm, Well 2 pump stopped and restarted right away. Influent chlorine residual low on start up, Value recovered, alarm cleared. | FLAG | stage2_low_confidence | 0.008712 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.008712 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NMMCBR - Upstream Pressure LoLo alarm came in. Checked site. Trends show a steep drop in pressure. No flow through the flowmeter. Not indicative of flushing. Called Rob P. but no answer. Will try again. 23:20 - Called Rob P. again who informed there is a WM break for East Gwillimbury and needed to close a valve which triggered this alarm. 00:18 - Rob P. called back to inform that the WM repair is complete and Rob has reopened the valve. Rob informed that all alarms can be cleared #CONSULT | FLAG | stage2_low_confidence | 0.017325 | ML: above threshold (no LLM available) — 0.017 | repair [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.017325 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | STW12 - Place well 1 man/on for Zone 1 fill cycle STW3 - Place well 3 man/on Stouffville - Lane W from town of Stouffville flushing at hydrant zone (2416-366-6675) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045478 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060672 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | Connor Smith signing in -12 C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042384 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | NMVCBA - Placed valve in man/open at 30 L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004472 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | SHTP - Tim H and Murray from Honeywell on site to complete a hydro meter change. Tim H directed to place the well 2 pump in manual and then off and to placed well pump 3 in auto and duty 1. | FLAG | stage2_low_confidence | 0.0084875 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084875 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | GWTP - John D. noted him and Yash S. still working on network. Plant is currently not active but HLP in auto. Placed HLP man/off. John and Yash on site, they will notify ops | FLAG | stage2_low_confidence | 0.009881 | ML: above threshold (no LLM available) — 0.01 |  | 0.009881 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | QVETQS - Inlet free chlorine hihi alarm. Checked site, tower is currently draining. Trending shows a steady increase of the inlet free chlorine over the past couple of days. The inlet free chlorine reading has dropped below alarm setpoint. Cleared alarm and sent an email to area ops. 07:38 - QVETQS - inlet free chlorine hihi alarm. Alarm would not clear as it is a switch alarm. Area ops are aware. | FLAG | stage2_low_confidence | 0.014562 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.014562 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | VNPS PD7 - Pump 2 man/off MAPS PD7- Pump 4 to auto, to help with RHRSTR level. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044134 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | YWS + NYWS Normal MKRSEM, Notified Toronto operator Paul to start 2 pumps to fill the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036711 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP, ZW5 Shutdown/turbidity hihi alarm, contacted Jack P, directed to place filter in the off position, he will go on to SCADA to investigate further consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0058177 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP - Jack P called nack, leaving train 5 off for the night | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048595 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MKETFA, Paul from Toronto called, they will be circulating water from one of their pipes/valves. They will be turning off one of their pumps to do this work. The work should only take 15 minutes, once completed, pumps will go back to normal operation | FLAG | stage2_low_confidence | 0.011707 | ML: above threshold (no LLM available) — 0.012 |  | 0.011707 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: 2C and rain. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045651 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | GWTP - GAC 4 flow control valve deviation alarm. Checked site, GAC 4 flow control valve is open and operations appear normal. Shift report states that the GAC 4 effluent valve deviation alarm is a disregard. After carefully reviewing the valve name on SCADA it was clear that the effluent valve and the flow control valve are the same valve and this is the alarm that is a disregard on the shift report. | FLAG | stage2_low_confidence | 0.026404 | ML: above threshold (no LLM available) — 0.026 | scada [control_system]; alarm [control_system] | 0.026404 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | ARPS- Jerry from Peel changing pumps from 6 to 1. Then at noon will be changing from pump 1 to 12. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058272 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | NMETHW - Arthur L completing work on the OIT and has directed to disregard the historian heartbeat alarm. | FLAG | stage2_low_confidence | 0.0086669 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086669 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | SHTP - John D. informed that he will be conducting minor upgrades to the site and requested the pumps be placed in manual. Called Jen S. who directed to deactivate the plant. Called John D. and relayed this information and he informed that he will start his upgrades when the plant shut downs. John will give the ROC a call back when he is finished 12:45 - John called back to inform that he is finished working on SHTP | FLAG | stage2_low_confidence | 0.014969 | ML: above threshold (no LLM available) — 0.015 |  | 0.014969 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | KSTP - CO2 Adjusted pH LoLo alarm came in. Shift report directs to disregard Raw Water pH alarms. After checking site, noticed that the plant is active but the CO2 Adjusted pH has taken a dip and the pH is recovering. This alarm triggered the high lift pumps to interlock. Will continue to monitor 04:16 - Settled Water Conduit Level LoLo alarm came in along with Filter 1 and 2 Level Called Jack P. who directed to ack/reset alarms. CO2 Adjusted pH alarm cleared which lifted the interlock on the low lifts. Jack P. informed it will take some time for the water to reach the filter and then to the conduit. Jack P. would like a call back if any other alarms come in for KSTP 04:40 - Alarms have cleared #CONSULT | FLAG | stage2_low_confidence | 0.037471 | ML: above threshold (no LLM available) — 0.037 | alarm [control_system]; alarms [control_system] | 0.037471 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | STW12- Communication Failure. Alarm cleared after a few minutes. | FLAG | stage2_low_confidence | 0.010241 | ML: above threshold (no LLM available) — 0.01 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.010241 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | KSTP - CO2 adjusted pH LoLo alarm. Checked site, plant is currently active. Low lift pumps interlocked on the low low pH alarm. Trending shows the CO2 adjusted pH reading is increasing. Reset alarm when the reading recovered above the lolo alarm setpoint. Monitored low lift pump start up. | FLAG | stage2_low_confidence | 0.015533 | ML: above threshold (no LLM available) — 0.016 | alarm [control_system] | 0.015533 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | KSTP - Post chlorinator 2 low vacuum alarm. Checked site, post chlorinator 1 rotated into duty 1 and is operating. Able to clear alarm. | FLAG | stage2_low_confidence | 0.007571 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.007571 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | ANW23 - Dave T on site to complete work orders including a generator test, chlorine analyzer maintenance and turbidity analyzer maintenance. Dave directed to disregard associated alarms. | FLAG | stage2_low_confidence | 0.030948 | ML: above threshold (no LLM available) — 0.031 | sso [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.030948 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | AUPSRR - Post-injection free chlorine hihi alarm. Checked site, trending shows a sudden spike of the post injection free chlorine reading which returned to normal within one reading interval. Reset alarm. | FLAG | stage2_low_confidence | 0.013173 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.013173 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | HLETYS- Noticed that Pre Injection Total and Combined Chlorine has significantly dropped lower than normal during drain cycle causing an abnormal trend. Currently reading Combined 0.43mg/L. Post Injection readings appear normal. No alarm triggered. Notified Benson S. He will log onto SCADA and take a look. 15:01- Benson S called back. Duty now active and Post Injection Combined Chlorine HiHi alarm came in. He will call ORO and call back if attending site. 15:22- Benson S requested a call if Post Injection stays above 4.0Mg/L for several minutes or if Pre Injection combined stays below 0.45 for several minutes. 15:30- Pre-Inj Combined value still dropping, Post Injection Combined HiHi Alarm coming in and out. Notified Benson S. he will attend site. Requested to deactivate duty and change duty start from 35 to 25% W11697567 CMU5 | FLAG | stage2_low_confidence | 0.0577 | ML: above threshold (no LLM available) — 0.058 | scada [control_system]; alarm [control_system] | 0.0577 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | MKRSEM- Called Toronto water(Zoran) and requested to stop filling Res. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066423 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | VNRSKS - Deactivated duty due to low levels at RHRSTR. Placed all pumps at VNPS PD7 man/off and placed pumps 1-3 at MAPS PD7 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067886 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | KSTP - Jason G on site to complete a generator test, turbidity analyzer maintenance, treated water analyzer maintenance and will complete the raw water analyzer maintenance if time allows. | FLAG | stage2_low_confidence | 0.010824 | ML: above threshold (no LLM available) — 0.011 |  | 0.010824 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | STW3 - Placed in manual/currently running for STETBR fill cycle. STW12 - Jack P directed to place wells 1 and 2 pumps man/off and use well 1 only in emergency until farther notice. Hypo tank 1 has a leak. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; leak [infrastructure] | emergency [critical]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | STW12, STW3- Placed wells back into auto for completion of STETBR Fill cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052155 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | AUETAD, Jerry Z on site testing lo temp alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061916 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | MAPS Server, Kingsley M restarting the server | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059534 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | MKMCTA - Building security intrusion alarm. Checked site, alarm system is armed and security intrusion status is active. Acknowledged and reset alarm, alarm cleared. | FLAG | stage2_low_confidence | 0.011462 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.011462 | 0 | 0
2026-03 | 2026-03-08 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | SHTP - Reservoir chlorine low alarm. Checked site, plant and high lift pumps are active. Trending shows a dip of the reservoir chlorine residual reading which recovered to normal range within ten minutes. Cleared alarm. | FLAG | stage2_low_confidence | 0.014095 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system] | 0.014095 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | SHTP - Reservoir total chlorine fault alarm. Jen S on site replacing tubing that may trigger alarms. | FLAG | stage2_low_confidence | 0.014937 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.014937 | 0 | 0
2026-03 | 2026-03-07 | All Water System ROC General | ROC | MKRSEM, Notified Toronto operator Peter to stop pumping to the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063713 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | SCADA - Incident report came through via email. Medium priority. Informed Ian w, forwarded email. Ian following up with Network on-call Evgeny S 17:39 - Ian W called back and results were a false positive. | FLAG | stage2_low_confidence | 0.013259 | ML: above threshold (no LLM available) — 0.013 | scada [control_system]; incident [safety] | 0.013259 | 0 | 0
2026-03 | 2026-03-10 | All Water System ROC General | ROC | MKPSSA - Sean P on site to complete a generator load bank test. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060997 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | AUW57 - Influent free chlorine hi, influent free chlorine hihi, treated free chlorine hi. Issue rose during start up of well. monitored. Rotated ammonia pump 2 duty 1. Dropped chlorinator 1 dosing from 109 to 103. chlorinator 2 OOS. Monitored influent reading coming back down slowly. Dosing factor kept adjusting as influent remained hi slowly dropping and dosing came down all the way to 90. effluent free and combined chlorine were picking up on the other end of contact tank. Placed well 5 man/off to prevent hihi alarm on effluent. Informed Joe D | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-02 | ROC General | ROC | STRS48 - Dominic from Honeywell on site to complete maintenance on the security system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051505 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | Connor Smith signing in -16C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042123 | 0 | 0
2026-03 | 2026-03-02 | ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to one MAPS and one VNPS pump to equalize demand on MARS and RHRSTR. | FLAG | stage2_low_confidence | 0.0076362 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076362 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | NMETHW - Deactivated duty 1 to maintain level offset from NMETIB. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049325 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | YWS + NYWS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038512 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | STETBR - Low level alarm. Duty activating soon. Placed STw2 and STW3 manual/on as per the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066683 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | Connor Smith signing in -16C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042123 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | ARPS- Jerry from OCWA called to inform will be rotating from pump 6 to pump 5. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052767 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | AUW14 - Security intrusion alarm, FMC will notify Corp security. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053085 | 0 | 0
2026-03 | 2026-03-12 | ROC General | ROC | STETBR - Security intrusion alarm, FMC will call Corp security. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071572 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | NMVCBA - Placed back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005522 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | SHTP - Well pump 2 uncommanded start alarm. Plant is not active. Well pump 2 recently stopped. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064737 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | MKRSEM - Called Toronto water (Puria ) and requested to start filling Res. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067743 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | STETBR- Tower level Hi alarm. Placed STW3 back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052166 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | MARS - High level alarm, deactivated RHRSTR duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051199 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | VNPSCD - Sani Sump pumps 1&2, Sump Pumps 1&2 Fault alarms. No High level alarms. Emailed area, disregard as per SCADA report. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | AUPSRR - Post-injection Free chlorine Hi and HiHi alarms. Quick spike for one reading. Duty recently activated. Alarms cleared. | FLAG | stage2_low_confidence | 0.011034 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011034 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | Ethan U signing in Weather 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-23 | ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | MARS- Cell1 (North) Lvl Hi Alarm. AURSBS- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043514 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | KSTP - Clearwell Influent Free chlorine residual Low alarm. Plant is not running. Will monitor. Placed High lift P3/duty 1 man/off. Will notify OP first thing in the morning. 05:30 Clearwell influent Free chlorine residual slowly dropping. Notified Joe M. He will check SCADA. # Consult | FLAG | stage2_low_confidence | 0.016061 | ML: above threshold (no LLM available) — 0.016 | not running [equipment_failure]; scada [control_system]; alarm [control_system] | 0.016061 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | SHTP- Filter 2 Turbidity Hi, Filter 3 Turbidity Hi. Backwash just completed. Disregard as per SCADA Report. | FLAG | stage2_low_confidence | 0.0076561 | ML: above threshold (no LLM available) — 0.008 | scada [control_system] | 0.0076561 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | ANW23, Discharge Pressure lolo alarm, Notified Tim H of these observations, directed to place pump 2 into D2, Will contact Jordan B of these changes. | FLAG | stage2_low_confidence | 0.007887 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.007887 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | AUW14, Placed wells 2/3 in manual/off so that more water can be moved from AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053383 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | yws + nyws normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | KSTKWP- Total Chlorine Low Low Sw Alarm. Tower Filling. Value recovered. Cleared alarm. | FLAG | stage2_low_confidence | 0.0076341 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076341 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | Carter Dunn Signing In, -2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: 0C and snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044729 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | GWTP - Eric S. called to inform that he and Rick L. are finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063376 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | MAPS PD7, Placed pumps 2/3 to auto VNPS PD7, Placed all pumps back to man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036341 | 0 | 0
2026-03 | 2026-03-06 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | NMETIB - Activated D1 to offset NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043767 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | SHTP - Res total chlorine lo. Informed Jen S, is aware due to changeover of cell. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070334 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | NBW5 - Noticed turbidity increasing, reduce pump 1 & 2 max flow from155 to 145. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053106 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | MARS - Reservoir lo level AURSBS - Deactivate duty 1 JFRS - Activate duty 2 as duty 1 active but duty 2 was not triggered on down cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047989 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | AURSBS, Activated D1 to help draw water from MARS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045768 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | ARPS, David from OCWA called, he is rotating his pumps so pump 7 is now the lead pump. (From pump 5) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005888 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-01 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | NMVCBA - Placed valve back to auto MKRSEM - Called Toronto Water (Paul) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056547 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | GWTP - Low Lift Flood alarm came in. Called Joe M. who will take a look. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | HLETYS - Tower mixer VFD fault, mixer uncmd stop. Able to clear but returns shortly after. Informed David T who will attend site later | FLAG | stage2_low_confidence | 0.014209 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure] | 0.014209 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | MKRSEM, Contacted Toronto operator Paul to start 2 pumps at the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050129 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | MTW12 - Silicate pump 2 fault. Unable to clear fault, silicate pump 1 running duty 1 okay. Placed silicate pump 2 man/off | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | VNPS- Benson S onsite. Requested to activate BVPS. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060597 | 0 | 0
2026-03 | 2026-03-09 | All Water System ROC General | ROC | JFPS - RES temperature alarm. Checked site, no temperature reading available. Alarm triggered this past weekend and was a disregard by the on call operator. Disregard again and sending email to area ops. | FLAG | stage2_low_confidence | 0.013201 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.013201 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | HLW1- Treated Free Chlorine Hi Alarm. Notified Jordan B. Requested to rotate Ammonia pumps so pump 2 running and place pump 1 in manual | FLAG | stage2_low_confidence | 0.0073726 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073726 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | STW1/3, Placed wells man/on, STETBR currently filling | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046568 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-05 | All Water System ROC General | ROC | STPSMR, Patrick F on site, testing Cl2 leak/scrubber alarms and doing health and safety alarms | FLAG | stage2_low_confidence | 0.010998 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.010998 | 0 | 0
2026-03 | 2026-03-11 | All Water System ROC General | ROC | QVW12 - Treated Free chlorine residual Hi alarm. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053718 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | MAPS PD7, Placed pump 2 back to man/off VNPS PD7, Placed pump 2 to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035537 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | NMETHW - Activated Duty 1 @ 42% to offset NMETIB. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045908 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | Carter Dunn Signing in, 3D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | KSTP - Settle water turbidity hi. Conduit level dropped to lolo level. CO2 adjusted pH lolo, locking out low lifts feeding to settle tank. Deactivated duty to stop highlifts as near duty stop. Found raw water turbidity value sporadic on trend reading (email con-call operator). Filter 1 & 2 hit lo but went to normal after low lifts came back on with CO2 adjusted pH going back within range. Deactivated duty 1 as duty near stop | FLAG | stage2_low_confidence | 0.026633 | ML: above threshold (no LLM available) — 0.027 |  | 0.026633 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | VNP7 - Man/stop pump 3 & 2 MAP7 - Place pump 2 & 3 auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040208 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | GWTP - Contact tank 1 free chlorine lolo, Joe M called and is aware of alarm informed he will deactivate duty and put highlift pump 1 or 2 duty 1 | FLAG | stage2_low_confidence | 0.008041 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.008041 | 0 | 0
2026-03 | 2026-03-14 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | ARPS - Peter from OCWA called, OP on site for chemical system maintenance/ system in maintenance mode for 30 - 40 minutes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060508 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | STW3 - Jack P called to inform he would like to be contacted if the halogen valve system activates. VNRSKS - Swapped supply pumps from ONE VNPS and one MAPS pump to two MAPS pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059079 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040295 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | GWTP - Joe M backwashing GAC3, requested disregard alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0060929 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AUVCBS - PAC communication failure alarm. Notified Artour L. He will troubleshoot # CMU5 W11762057 | FLAG | stage2_low_confidence | 0.012315 | ML: above threshold (no LLM available) — 0.012 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.012315 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STPSMR - Lee F will attend site, requested to assign P1 to Duty 1, P2 to Duty 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053324 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP - GAC 4 Flow Control Valve Deviation Alarm came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060645 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | NMETIB- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053242 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | MKETFA- Toronto (Puolia) called and is shutting down pump for 5 minutes, then will start back up. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057565 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMETIB- Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053728 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | KCETDS- Tim H onsite placing tower back online. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060075 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AUVCBS- PAC Communication Alarm. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066171 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | KSTP - Chlorine gas leak alarm and chlorine emergency valve closure alarms. Jason G called to inform he completed the chlorine leak test and everything is okay. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; gas leak [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | emergency [critical]; gas leak [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NMW12 - Silicate pumps 1&2 OOS. Duty deactivated recently. Christian B and Ben H on site troubleshooting silicate pumps. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | HLETYS - Kevin W rebooted cellular APN modem using backup communication. | FLAG | stage1_keyword | 0.95 | Critical keyword match: backup [infrastructure] | backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | KSTKWP - Jerry Z. is on site and will be testing the chlorine leak alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | HLW2 - Influent chlorine residual HiHi alarm. Adjusted chlorinator dosing factor from 179 to 169%. Influent chlorine residual still HiHi. Rotated chlorinators, 1 on duty 1. Notified Jordan B, he will check SCADA. Influent chlorine residual value back to normal. Was able to clear alarm. | FLAG | stage2_low_confidence | 0.012311 | ML: above threshold (no LLM available) — 0.012 | scada [control_system]; alarm [control_system] | 0.012311 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMVCBA-Placed valve manual 30L/s to assist in NMETHW and NMETIB offset | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050486 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Connor Smith signing in -3C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00423 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | KSETWB - Phil D. is on site and will be testing the Chlorine Leak alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMTKKC - Ammonia Pump 1 speed signal/leakage alarms. Eric S working on it. | FLAG | stage2_low_confidence | 0.010782 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system]; leak [infrastructure]; leakage [infrastructure] | 0.010782 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | NMTKKC- Valve Chamber Eyewash 1,2 Flow Switch Alarms. Called Joe W. He is onsite testing. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0070345 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | STPSMR - Patrick F. is on site and will be completing chlorine analyzer maintenance 11:40 - Patrick called back to inform he is now at BVPS and will be running the diesel generator under the load of two pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052627 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | QVW34 - Well 3 pump uncommanded stop alarm. Notified Ben H. He is on his way to site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058868 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | JFPS- Lee F requested to place pump 2 man/off. Place pump 3 back in auto. After running pump 1 for one hour place in duty 2 and place pump 4 as second duty 1 pump. 11:08- Placed pump 1 man/of and switched to auto duty 5. Placed pump 4 in auto duty 1. | FLAG | stage2_low_confidence | 0.0084075 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084075 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | JFPS- Tyler ZJ onsite working on pump 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044157 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | AUETFC - Joe D on site to deactivate duty for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058587 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | STW3 - Jack P heading to site, will work on silicate system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048246 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | RHPSPA- Dan B called. He and Ernie H are exercising surge valves which triggered alarms PD7 Surge Valve 1,2 Open Alarms on SCADA. Work is completed. Cleared alarms. | FLAG | stage2_low_confidence | 0.010022 | ML: above threshold (no LLM available) — 0.01 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.010022 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | NRETCR - Activated duty 1 to drawdown JFRS in preparation for the Maple to Jefferson Feed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055561 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | AURSBS - Activated duty 1 to fill the reservoir in preparation for the Maple to Jefferson Feed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056853 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | Reverting Maple to Jefferson Feed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005654 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | MKRSEM - Request TO (Zoran) to drop both pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059903 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | ARPS - Peel Ammonia Analyzer B (AIT 1B, AIT 4B, AIT 5B) Airport Rd discharge alarms. Notified Peter from OCWA, he confirmed with OP/instrumentation that alarms from Backup unit, no effect to system. They are performing maintenance on the unit. Requested disregard alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; backup [infrastructure] | alarm [control_system]; alarms [control_system]; backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NRETCR - Lee F called to inform he finished his work on the altitude valve. Lee F requested that the valve be placed in auto mode and the system duty activated to test the valve opening sequence. Made the necessary adjustments, the valve opened. Lee F leaving site. Swapped controlling tower back to NRETCR | FLAG | stage2_low_confidence | 0.019908 | ML: above threshold (no LLM available) — 0.02 |  | 0.019908 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | HLW2- Ammonia Pump 1 Fault Alarm. Pump 2 took over in duty 1. Cleared alarm Treated Free Chlorine HiHi Alarm. Cleared alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NMW136 - Alex B on site to complete an ammonia system inspection. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004663 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | VNPS- Placed PD7 pump 1 man/off MAPS- Placed PD7 pump 2 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041083 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | JFPS- Chris I called and notified will be placing pump 2 OOS and locking out for repairs. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action] | oos [equipment_failure]; repair [maintenance_action] |  | 1 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | HLW2- Well 2 Pump Failed to Stop. Came in on duty stop. Alarm cleared. Well 2 Pump Waste Valve Open Alarm. Interlocked well. Alarm cleared after a few minutes and interlock was cleared. | FLAG | stage2_low_confidence | 0.029463 | ML: above threshold (no LLM available) — 0.029 | failed [equipment_failure]; alarm [control_system]; pump failed [infrastructure] | 0.029463 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: 0C and cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044604 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STETTL - Activated duty 1 to top up the tower for the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051203 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MKRSEM - Toronto Water (Peter) called to state that Toronto Operations would like two pumps to push flow to MKRSEM for thirty minutes to complete sampling. Informed Peter that this is acceptable and that the reservoir has room to accommodate this flow. | FLAG | stage2_low_confidence | 0.015605 | ML: above threshold (no LLM available) — 0.016 |  | 0.015605 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | GWTP - Clearwell 2 chlorine low alarm. Patrick F on site, made chlorine adjustments. Alarm should clear. Microfiltration room low temperature alarm. Patrick F checked site/normal. Requested disregard alarm. | FLAG | stage2_low_confidence | 0.0094633 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0094633 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STW3- Yash S called and requested well man/off for network shutdown work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051177 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | MKRSEM - Called Toronto water(Paul) and requested to stop filling Res. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066362 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | GWTP- Parth P finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005522 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NMTKKC- Valve Chamber Eyewash 1 Flow Switch Alarm. Called Jason G. No answer. Will follow up. 13:51- Jason G will take a look | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0050711 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | STW12- Placed well 1 man/on STW3- Placed well 3 man/on for STETBR fill cycle Interim Procedure | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0032613 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | KSTKWP - Site Hydro Power Failure and CL2 Emergency Closure system fault alarm came in. Checked site. Tank is draining. Likely a power blip. CL2 Emergency Valve Closure system fault alarm is outstanding. Called Patrick F. who informed that this alarm should clear on its own. 17:58 - Alarm did not clear and chlorine system has been running. Called Patrick F. who informed it can be disregarded until tomorrow. #CONSULT | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; fault [equipment_failure]; failure [equipment_failure]; alarm [control_system] | emergency [critical]; fault [equipment_failure]; failure [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | KCETDS, Khalid from IAM is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052888 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | SHTP - Filter 2 turbidity. Checked site, filter 1 is completing a backwash sequence. Trending shows a turbidity spike in filter 2 which quickly dropped to normal range. Alarm has been cleared. | FLAG | stage2_low_confidence | 0.009477 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.009477 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | ARPS- Tegber from OCWA called and will switch from pump 5 to pump 6. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050418 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | MKRSEM- Called Zoran from Toronto and requested two pumps on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063564 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS PD7 - Benson S requested Pump man/off. Deactivated Duty 1, Placed Pump 2man/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054154 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | BLW3- Patrick F and Jack P onsite changing Cl injectors. Disregard related alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0068201 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | BLW3 - Travis W working on chlorine, silicate systems. Backflushing. He placed Well 3 pump local/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00582 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | GWTP- Jackie S testing multiple flood and sump alarms including chemical room. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS- Called Benson S to inquire if able to start running PD8 Pumps. Finished with power transfer. Placed PD8 pumps 1 and 3 back into auto. Pump 2 is OOS with "Pump 2 Not Ready Alarm". Currently Man/off. Benson will look into it. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | STPSMR- Ian W working on OIT. Has repointed the tags and bypassed the HRBT alarm so pumps will keep running during work | FLAG | stage2_low_confidence | 0.015258 | ML: above threshold (no LLM available) — 0.015 | bypass [critical]; alarm [control_system] | 0.015258 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | STETTL-Outlet Free chlorine Low alarm. TWR is filling. Jack P cleaning chlorine analyzer. | FLAG | stage2_low_confidence | 0.0079913 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079913 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | VNRSKS, Kingsley M resetting OIT on site VNPSAP, Chris S is leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043813 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | AURSBS - Ben H. called to inform that he is on site with Chris S. and Donald M. and will be working on the chlorine system. In this time, Ben will need AUVCBS in man/closed. Placed the valve man/closed | FLAG | stage2_low_confidence | 0.011505 | ML: above threshold (no LLM available) — 0.012 |  | 0.011505 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | STW2/3, placed wells back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042623 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | Angelica Chepiga signing in,weather -11C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043101 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMTKKC- Chris S onsite for chemscan work. Notified Ben H. Requested to place NMW13 in manual, adjust duty stop from 75-85% activate duty and place chemical pumps man/off. Ammonia Pump 1 was already man/off in duty 3. | FLAG | stage2_low_confidence | 0.0096835 | ML: above threshold (no LLM available) — 0.01 |  | 0.0096835 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP - ZW1 membrane tank level hi alarm. Checked site, filter 1 is going through a cleaning process. Filter 1 level should return to normal range as the filter continues through the cleaning sequence. Will monitor. | FLAG | stage2_low_confidence | 0.010927 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010927 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | MKRSEM- Called Toronto (Puria) and requested pumps off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062081 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | SHTP- UV Reactor 2 Critical Fault Alarm, Inlet Vlv 2 Fault Alarm, UV Reactor 2 Major Fault Alarm. UV is not running, UV 1 and 3 in service. Notified Tim H. He will take a look. | FLAG | stage2_low_confidence | 0.017262 | ML: above threshold (no LLM available) — 0.017 | fault [equipment_failure]; not running [equipment_failure]; alarm [control_system] | 0.017262 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | QVW34, Ian W working on the OIT, disregard historian alarm GWTP, Parth P is finished on aite | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0042962 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS- Benson S requested PD7 and PD8 Pumps man/off to switch power back over to utility. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055048 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MARS - North cell level low alarm. Activated RHRSTR duty 1 to push flow from BVPS. Swapped the supply pumps for VNRSKS from one VNPS and one MAPS pump to two VNPS pumps to allow MARS level to recover. Informed Jack P that BVPS will be starting. | FLAG | stage2_low_confidence | 0.012705 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.012705 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NMW15 - Alex B on site for ammonia and chlorine systems inspection, cleaning chlorine analyzers. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053401 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | GWTP - Gas chlorinator 5/6 Hi vacuum alarms. Plant is off (Memo). Jackie S and Joe M on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0068219 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | ARPS- Peter from OCWA called. They are performing maintenance on HACH total, and free ammonia. Will not impact operations. Can disregard ammonia alarms that come in as these alarms are for the backup system. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; backup [infrastructure] | alarm [control_system]; alarms [control_system]; backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NMETHW - Deactivated Duty 1 @73% to offset NMETIB | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045868 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | AUPSRR - Metro valve man/closed no flow indication from yesterday 12:45, notified Ben H. Donnald M on site working on it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049059 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | KSTP- Eric S onsite working on low lift turbidimeter 09:47- Finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036094 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STETBR/STETTL- Yash S work completed. Requested to place all pumps back into auto. STETBR duty already active. Activated STETTL. STW12- Placed well 1 into manual STW3- Placed well 3 into manual STPSTL- Pump 1, 2 Low Flow. Both pumps failed. Reset alarms. Pump 2 started up in duty 1. | FLAG | stage2_low_confidence | 0.018984 | ML: above threshold (no LLM available) — 0.019 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.018984 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NMETIB - activated duty 1, offset NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043969 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | AUVCAD - Valve chamber flood alarm, notified Gary R, will attend site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | QVW12 - William M returned well 1 pump back to auto, | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046895 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS PD8- Benson S requested to start up 2 pumps for generator run. He will call back to place off when switching back to utility power. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068924 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | KSTP - Place highlifts back in auto GWTP - Rick L & Parth P finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057564 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS PD7 - Man/started P2 for Benson S, generator running . | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048016 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | SHTP - Well pump 2 uncommanded start alarm. Checked site, recently shut down. Able to reset alarm. GWTP - GAC 2 Level fault alarm and low/lolo alarms. Checked site, plant is not active. GAC 2 level reading is within normal range. Trending shows an abnormal dip of the GAC2 level reading which returned to normal range. Cleared alarms. | FLAG | stage2_low_confidence | 0.024756 | ML: above threshold (no LLM available) — 0.025 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.024756 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | Initiating Maple to Jefferson Feed changes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058919 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NMW12. - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows a spike of the influent free chlorine reading which returned to normal range within two reading intervals. Reset alarms. | FLAG | stage2_low_confidence | 0.011076 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011076 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | GWTP - Rick L and Parth P on site for annual calibration, Joe M and Jackie S on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067697 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MAPS- PD7 P2 Uncmd Stop, P2 Disch. Valve 1 Uncmd Close. Pump 1 took over in duty 1. Placed pump 2 in manual and cleared alarms. | FLAG | stage2_low_confidence | 0.0082311 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0082311 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMETIB- Activated duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053481 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MTETNL - Travis W leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055562 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | BLW3 - Dan Z and Travis W on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040555 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | BVPS - Activated duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040663 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | SHTP - Deactivate highlifts to let res fill | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059014 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | MKRSEM - Request TO (Zoran) to run 2 pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044732 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | RHPSPA - Surge Valve 1 and 2 Open, came in 3 times since 9:30. Coincides with MKVCMM Reverse flow HiHi. Inquired with Cristina S. of any work, she will follow up. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065604 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NRETBR - Joe D testing Hi/Low ET level alarms. | FLAG | stage2_low_confidence | 0.0076347 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0076347 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | SHTP - Gas analyzer 3 methane fault alarm. Checked site, plant is active. Able to clear alarm. | FLAG | stage2_low_confidence | 0.011786 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system] | 0.011786 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | MKRSEM, Reservoir 1 Level lo alarm, notified Medhi from Toronto Water to start filling the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.006082 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | MAPS PD7, Placed pump 3 to auto VNPD PD7, Placed pump 2 man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034194 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | KCETDS - Yash S. is on site to replace a UPS Battery Replacement | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061333 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | Ethan U signing in Weather 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to one VNPS pump and one MAPS pump to equalize the demand on MARS and RHRSTR. | FLAG | stage2_low_confidence | 0.0079798 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079798 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | SHTP, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040013 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MKRSEM- Free Chlorine Residual Fault Alarm. This alarm was disregarded yesterday. Informed Patrick F that it has come back in. | FLAG | stage2_low_confidence | 0.017909 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.017909 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | MTW12 - Well 1 silicate, hypo and well 1 and 2 pumps OOS alarms. Checked site, well pump 1 is running in local. These are consistent alarms that trigger on Wednesdays when operators sample. Well is run to waste during sampling with the chemical systems offline. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal VNRSKS - Placed all pumps at MAPS PD7 man/off and placed all available pumps at VNPS PD7 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043006 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | VNPS7 - Man/stop pump 1 man/off. MAP7 - Place pump 3 auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040127 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | SHTP- Reservoir 2 Level Lo Alarm. Deactivated high lift duty. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053566 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | AURSBS- Ammonia Pump 1,2 Failed to Start, Chlorine Pump 2 Uncomm Stop Alarm. Alarms cleared. Chlorine Pump 2 Uncomm Stop alarm came back in. Notified Donald M. He will take a look. W11760331 CMU5 | FLAG | stage2_low_confidence | 0.011192 | ML: above threshold (no LLM available) — 0.011 | failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011192 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | HLW1 - Treated free cl hi, came in 09:00. Rotated ammonia pumps from P1 to P2 at 09:15. Noticed Treated Free HiHi alarm is disabled. Notified Jordan B., he is headed to site | FLAG | stage2_low_confidence | 0.0073744 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073744 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | AURSBS - Donald M. and Tyler Z. working on chlorine booster pumps, chemical system. Placed AUVCBS man/closed. Donald M. will place in auto when work complete. AU central duty currently not active. | FLAG | stage2_low_confidence | 0.021697 | ML: above threshold (no LLM available) — 0.022 | oos [equipment_failure] | 0.021697 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | NMW12, Influent Free Cl2 hihi, abnormal spike occurred. After 2 readings, residuals went back to normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058363 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | STW12, Comm Loss alarms, notified Artour L as the issue continues to happen, he will look into it CMU5: W11760480 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0056374 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | ARPS- Tegbeer from OCWA called and will switch from pump 6 to pump 5. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050633 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | STPSMR - Jack P performing w/o including - temp alarms test and chlorine analyzers maintenance. | FLAG | stage2_low_confidence | 0.0095388 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0095388 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AURSBS - Chlorine pump 2 uncomm stop alarm. Donald M and Chris S working on chlorine pump 2, disregard alarms for the duration of the work. | FLAG | stage2_low_confidence | 0.0077553 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0077553 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | SHTP - Chlorine system alarms. OP on site for chlorine system maintenance. Disregard alarms for the duration of the work/ Interim memo. | FLAG | stage2_low_confidence | 0.010797 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010797 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | GWTP - Parth P and Rick L on site for annual calibrations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005949 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Linear Water System - Received a call from York Region corporate contact center (Bonnie S) regarding a client call in for a meter/valve chamber cover that needs to be adjusted. Dispatched Dwayne L to site. Created CMU5#W11760219 #CMU5 | FLAG | stage2_low_confidence | 0.0074819 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074819 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NMW16 - Christian B. under direction of Ben H. addressed low temp alarm, reset for him as he doesn't have SCADA permissions. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0072206 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | SHTP- Chlorine Room Gas Leak Alarm. Called Benson S. Operators are onsite for chlorine system maintenance. Can disregard. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AUW57 - Ian W working on OIT, disregard Historian Heartbeat alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054847 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | SHTP- Tim H called and requested to place well 2 back into auto. He is heading to site and will look into UV Minor Fault alarms. | FLAG | stage2_low_confidence | 0.014008 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.014008 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MAPS PD7, Placed pump 2 in man/off VNPS PD7, Placed pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034754 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | NBW7- Jacob M onsite for Cl and Turbidity analyzer maintenance NBW5- Diesel Tank Sump Hi Level Switch. Notified Jacob M. He will look into it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057222 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | KCETDS - Cole W. called to inform that he will start filling the tower but it will not be online as sampling still needs to be done | FLAG | stage2_low_confidence | 0.0089074 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089074 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | AUPSRR- Donald M onsite for generator run, Cl analyzer maintenance and adjusting metro valve. | FLAG | stage2_low_confidence | 0.0074007 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074007 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STW12 - Jack P with instrumentation team on site replacing Hypo tanks. Wells 1/2 pumps man/off for the duration of the work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061282 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | QVW12- Will M onsite for analyzer maintenance. Disregard alarms while onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0066017 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | RHRSTR - Deactivated Duty 1 to maintain MARS level. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046275 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMTKKC- Eric S finished onsite. Ammonia pump 1 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048269 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MTETNL- Travis W onsite for work orders including Cl analyzer maintenance, health and safety and low temp. | FLAG | stage2_low_confidence | 0.013163 | ML: above threshold (no LLM available) — 0.013 | work order [maintenance_action] | 0.013163 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | MKRSMR- Artour L onsite changing out UPS batteries. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061136 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | MAPS PD7 - PD7 pump 3 discharge valve uncommanded close alarm and uncommanded stop alarm. Checked site, pumps recently activated to fill system. Pump 3 is interlocked due to the alarms. Able to clear alarms. Duty 1 rotated to pump 1 when the alarm triggered. Placed pump 3 back in duty 1 and monitored start up. | FLAG | stage2_low_confidence | 0.017284 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system]; alarms [control_system] | 0.017284 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | ARPS - Peel/OCWA (Peter) called to inform he is completing the daily pump rotation at ARPS. | FLAG | stage2_low_confidence | 0.0073751 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073751 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MKRSMR - Toronto Water (Peter) called to inform he would like to run each of the COTFA PD6 pumps for thirty minutes for maintenance. Placed the valves at MKRSMR in manual for receiving mode and informed operations of the pump exercising. No concerns from Patrick F. KSTP - CO2 Adjusted pH LoLo alarm. Checked site, low lift pumps have interlocked. The conduit level also triggered the lolo alarm. Called Jason G who directed to clear the CO2 adjusted pH lolo alarm and call if any other issues arise from the temporary reduction in flow. | FLAG | stage2_low_confidence | 0.034012 | ML: above threshold (no LLM available) — 0.034 | alarm [control_system] | 0.034012 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | QVW12 - High Treated Free chlorine residual alarm. OP man/started well 1 pump. Alarm cleared in 5 minutes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065624 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | SHTP- Raw Water Tank Level 1,2 HiHi Levels. Tim H onsite. He will look into it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052907 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | GWTP- Ric L onsite for chlorinator rebuild. He will coordinate with operators onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071215 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MKETFA - Toronto Water (Peter) called to inform he would like to test the PRV for the Miliken system. Peter stated he would like to stop the active duty pump, test the PRV and then return the pump to active duty. Informed Peter he can completed the test as needed. | FLAG | stage2_low_confidence | 0.016531 | ML: above threshold (no LLM available) — 0.017 |  | 0.016531 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMW136 - Ian W working on OIT, disregard HRBT alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051349 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -2C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | STETBR - Deactivated duty 1 and placed STW1 and STW3 back to auto, in preparation for interim 22:46 - Activated duty 1 and placed STW1 and STW3 in man, in preparation for interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048651 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | Gluzen Ramos Ong signing in JFPS - man/open VC_MV3 to test after valve failed to open during Maple to Jefferson Feed run attempt on March 8th. Confirmed valve opened to 100% and registered flow. Placed back in Auto. Will notify West Water and ROC. | FLAG | stage2_low_confidence | 0.023112 | ML: above threshold (no LLM available) — 0.023 | failed [equipment_failure]; valve failed [infrastructure] | 0.023112 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | AUW57 - In fluent free chlorine hihi alarm. Checked site, well recently activated. Trending shows a spike of the influent free chlorine reading which dropped to normal range within two reading intervals. Reset alarm. SHTP - Well 2 pump uncommanded start alarm. Checked site, plant is currently off. Trending shows that well pump 2 recently shut down. Cleared alarm. | FLAG | stage2_low_confidence | 0.014682 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.014682 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | BLW34- Ian W working on OIT. disregard heartbeat alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052123 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | STRS48- Scrubber Running Status. Called Jack P. He was testing alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055569 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | AURSBS - Chlorine pump 2 fail to start. Able to clear and get pump to start | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | JFPS - Rotate pump 3 & 4 to duty 1. Pump 1 was previously duty 1, rotated out due to interim to run pump 1 in man/on for 1 hr daily. As they wanted to ease pump 1 into service to monitor. | FLAG | stage2_low_confidence | 0.0090132 | ML: above threshold (no LLM available) — 0.009 |  | 0.0090132 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | MAP7 - Place pump 3 man/off VNP7 - Place pump 3 auto GWTP - ZW7 35.5 kPa MIT-press decay test failed. Train 7 shutdown 8:00 - Informed Patrick F, will look into issue, disregard for now | FLAG | stage2_low_confidence | 0.0077709 | ML: above threshold (no LLM available) — 0.008 | failed [equipment_failure] | 0.0077709 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | STW3 - Jack P on site to take the chlorination system out of service so that the instrumentation team can complete a replacement of chlorinator 2. Jack has directed that STW3 is to remain offline until the work is completed and he has primed the chlorine lines. QVW12 - Well pumps not available alarm. Checked site, treated chlorine analyzers showing in calibration mode. Will M logged into facility log book and his log entry for today includes analyzer maintenance. Will monitor site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; alarm [control_system] | out of service [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | MAPS - MAEP emergency eyewash activated alarm. Notified Benson S. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system] | emergency [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | SHETCS - Activate duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053511 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | MKRSEM - Request TO to drop both pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057759 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | GWTP - Microfiltration room low temp alarm, notified Patrick F. He will check. | FLAG | stage2_low_confidence | 0.0074444 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0074444 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | HLW2- Combined Chlorine Hi Alarm. Notified Jordan B. He is onsite and will take a look. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005887 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | KCPSDS - Talha H. requested to reboot the OIT. Confirmed with Cole W. that this is okay as he is on site 12:25 - Talha H. is finished rebooting OIT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039989 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | KCPSDS - Place pumps 1 & 2 man/off as tower is to be drained today. Informed West Ops. Will call for pressure related alarms, disregard lo/lolo. David T will be on site later turning off analyzers. | FLAG | stage2_low_confidence | 0.010994 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010994 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | VNP7 - Place pump 2 & 3 man/off MAP7 - Place pump 1-3 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042088 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | ARPS - Peel (Jerry) infomred of daily pump switch over. Rotating pump 5 to pump 6 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053901 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | SHTP- Reservoir 1, 2 Level Lo Alarms. Notified Benson S. Requested to change duty setpoints to 15/45% and deactivated duty | FLAG | stage2_low_confidence | 0.0079775 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0079775 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Aurora, Emergency Locate, Sent email out to Tom H (Locate on call) and gave a call but no response, left a voice message. Waited for roughly 10 minutes then called again, but still no response. If no response on the third call, will escalate 22:44, Notified Tom H of the emergency locate, he will look into it | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NMW15 - Treated Total chlorine Hi alarm. Adjusted chlorinator 1 dosing factor from 48 to 47%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0062039 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | STETBR - Tower Level Lo alarm came in. Placed STW1 and STW3 man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058735 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | KSTP- CO2 Adjusted pH LoLo. Interlocked Low Lift Pumps. Ben H directed to clear alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060328 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | VNPS- Placed PD7 Pump 3 Man/off MAPS Placed PD7 Pump 3 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040912 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMETHW - Deactivated duty 1 while NMETIB fills to maintain level offset between the two towers. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056893 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | MKRSEM - Low level alarm. Called Toronto Water (Zoran) and requested two pumps on to fill the reservoir. | FLAG | stage2_low_confidence | 0.0086412 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086412 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | BLW34 - Influent free chlorine low and lolo alarms. Checked site, well was active when alarms triggered. Trending shows a steady decline of the influent free chlorine reading. Placed well manual/off for the night. | FLAG | stage2_low_confidence | 0.012483 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012483 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MKRSEM, Notified Toronto operator Brent to stop filling the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062815 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | MTW3 - Ernie H working on generator ventilation system. Disregard alarms for the duration of the work. | FLAG | stage2_low_confidence | 0.0075011 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0075011 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | COTFA- PD5 Discharge Pressure LoLo Alarm. Quick dip. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053024 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | STETBR - High level alarm. Placed STW12 and STW3 in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054137 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | Ethan U signing in Weather 2c. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | VNRSKS - Placed all pumps at MAPS PD7 man/off and placed all available pumps at VNPS PD7 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057966 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | STETBR - Tower Level Lo alarm came in. Placed STW1 and STW3 man/on as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058735 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | NMTKKC - total chlorine lo, trends show no dip, able to clear right away as reading within range | FLAG | stage2_low_confidence | 0.0075077 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075077 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | NMVCBA/NMVCIB - Reverted valve setpoint changes made earlier in the day by Ben H. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070404 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | Adeela Khan signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052508 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | STPSMR, Free Cl2 Res lolo, Duty is active, tower is draining, trends show a staircase drop, contacted Patrick F, he is heading to site STETBR, Deactivated D1 CMU5: W11756650 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041084 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | SHTP - Deactivate highlifts for interim to assist in filling res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064839 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | KCETDS - Tim H finished on site. Tower is isolated, waiting for the sample results. KCETFS controlling tower. | FLAG | stage2_low_confidence | 0.0075066 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075066 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | AUW57 - Historian Heartbeat alarm. Notified Ian W, he will check. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053096 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | BVPS - Lee F completed work on site. Placed P4man/off. Placed P3 back to auto. Pump 4 back to auto/ duty 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057045 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | NMVCBA - Placed valve man/open at 40 L/s 23:18 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030115 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | ARPS - Peel Ammonia Analyzer B Airport Rd Discharge B (AIT4B, AIT5B, AIT11B). Called OCWA (Binesh) who informed these alarms are from the backup system and can be disregarded. 02:18 - Peel Ammonia Analyzer A (AIT5A) Airport Rd Discharge alarm came in. As this is not part of the previous alarms that came in, called OCWA (Tegbeer) who informed there were no alarms on his end and made sure that the pump is working and the flow is okay. Tegbeer also informed that the ammonia system is running normally. Tegbeer also informed that he will give the ROC a call back in case any issue does arise | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system]; backup [infrastructure] | alarm [control_system]; alarms [control_system]; backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | JFPS - Deactivated pump 2. Placed pump 3 in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047384 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | GWTP - Rick L working on zebra mussels chlorinator rebuild. Jackie S and Joe M on site to assist. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071191 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | KSTP - Raw water turbidity Fault alarm, disregard as per Shift report. | FLAG | stage2_low_confidence | 0.013832 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system] | 0.013832 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STETTL - Activated duty in preparation for interim NMTKKC - Activated duty in preparation for interim YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047404 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MARS - Hi level alarm came in. Activated duty 1 at VNRSKS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052613 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | RHRSTR - Deactivated duty 1 so the reservoir does not overfill during low morning demand. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055367 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | NBW3 - Influent Free Chlorine LoLo switch alarm came in. This occurred on well startup. After 2 mins, influent free levels came back to optimal range. Will wait 10 mins before resetting alarm 08:18 - Alarms have cleared and well is running | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0070901 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | VNPS- Placed PD7 Pump 3 man/off MAPS- Placed PD7 Pump 1 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041083 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | KSTP - Raw water turbidity fault alarm. Disregard as per shift report. | FLAG | stage2_low_confidence | 0.013832 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system] | 0.013832 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | MARS - High Level alarm came in. Activated duty 1 at VNRSKS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053081 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | QVW12 - Chlorine leak detection alarm, and cl2 emergency valve closure fault alarms came in. Checked site, wells were not running when the alarm triggered. Trending shows a short spike of the chlorine gas detection reading which returned to normal range. Called Will M who will head to site to reset the valve interlock. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; fault [equipment_failure]; not running [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | emergency [critical]; fault [equipment_failure]; not running [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | EGMCDD - PAC Control Panel Power Failure alarm, checked Hydro one website, power outage in the area, ETR 19:45. | FLAG | stage2_low_confidence | 0.010755 | ML: above threshold (no LLM available) — 0.011 | failure [equipment_failure]; alarm [control_system] | 0.010755 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | MKRSEM, notified Toronto operator peter to start filling the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063112 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | GWTP- UV Reactor 2 Dosage Hi Alarm. Notified Jackie S and Joe M, GWTP- Gas Chlorinator 5,6 Hi Vacuum. Jackie S informed instrumentation working on it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065837 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | NBET27 - Outlet Total CL2 Hi alarm came in. Checked site. NBET is the controlling tower. Trends indicate the total chlorine level is trending upwards. NBET, NBW2, NBW3 and NBW5 chlorine analyzers are reading within normal range. Will continue to monitor 22:17 - Total chlorine levels are continuing to rise. Called Jordan B. who informed to refer to NBET for tower total chlorine readings. Jordan informed that once that tower stops filling, levels should come down. Jordan B. would like a call back if it reaches hihi levels #CONSULT | FLAG | stage2_low_confidence | 0.019473 | ML: above threshold (no LLM available) — 0.019 | alarm [control_system] | 0.019473 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | GWTP - High Lift Tank 1 and 2 Level Lo alarms came in. Checked site. Hi lift is running. Called Patrick F. who will take a look on SCADA. 17:15 - Called Patrick F. for an update. Patrick informed that he placed GAC2 OOS so that it would not be called for. The other GAC's increased flows to compensate for the loss of GAC2. All Hi lift tank alarms have been cleared #CONSULT | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | KLMCIA - Meter Chamber Flood and Security Intrusion alarms came in. Shift report indicates that site is OOS. Called Dwayne L. but no answer. 15:13 - Dwayne L. called back and informed that this can be disregarded until tomorrow | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | flood [critical]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | MKVCSA - Building security Intrusion alarm. Notified Rob P. He will attend. # CMU5 W11743940 10:45 Rob P attended site, alarm cleared, leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057267 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | QVW34 - Will M on site to complete some well testing. Will has requested that alarms be disregarded from site. | FLAG | stage2_low_confidence | 0.0073109 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0073109 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | SHTP - Gas analyzer 3 methane fault alarm. Checked site, all methane alarms sensors reading normal. This alarm has triggered several times and has cleared each reset. No known impact to operations. Will leave alarm outstanding to be inspected by area operations on Monday. | FLAG | stage2_low_confidence | 0.026713 | ML: above threshold (no LLM available) — 0.027 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.026713 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP - Multiple communication alarms came in along with UV Reactor 1 and 2 Start/sequence fault alarms. Checked site. Duty recently activated. Called Patrick F. who will take a look on SCADA #CONSULT | FLAG | stage2_low_confidence | 0.013238 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.013238 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | BLETNL- Travis W onsite for Cl analyzer maintenance, low temp and valve exercising. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070595 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | STW3 - Parth P and Rick L finished and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046658 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | QVETQS- TIe Valve Failed to Open. Alarm cleared. QVW34- Will M placed wells man/off for injector work. Disregard low pressure alarms. | FLAG | stage2_low_confidence | 0.019081 | ML: above threshold (no LLM available) — 0.019 | failed [equipment_failure]; alarm [control_system]; alarms [control_system]; valve failed [infrastructure] | 0.019081 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | HLPSYS - Dan B finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052475 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | VNPS- Placed PD7 duty 1 pumps in auto MAPS- Placed PD7 duty 1 pumps in manual | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043899 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NMW15- Alex B onsite for Cl system inspection. Will be backflushing. Disregard vacuum alarm if it comes in. 14:21- Eric S onsite troubleshooting Treated Total Cl analyzer | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061775 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | GWTP - Jackie S and Joe M on site to complete maintenance of the outfall chlorine analyzer and the sedimentation tank chlorine analyzer. Jackie directed that associated alarms be disregarded. | FLAG | stage2_low_confidence | 0.022748 | ML: above threshold (no LLM available) — 0.023 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.022748 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | BVPS- Historian Heartbeat Alarm. Notified Chris S. He will look into it. | FLAG | stage2_low_confidence | 0.0072337 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072337 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP - Rick L on site for annual calibrations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056122 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMTKKC - Parth P finished and leaving site. Ammonia pump 1 will remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | GWTP, Parth P on site doing annual calibrations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056329 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | MKRSEM - Free chlorine residual fault alarm. Patrick F called to inform he is on site completing sampling. AUW57 - Joe D called and requested that AUW57 be activated in manual mode for sampling. Made the necessary change. | FLAG | stage2_low_confidence | 0.013781 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; alarm [control_system] | 0.013781 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | STW3 - Rick L called to inform he is on site to troubleshoot the chlorine leak detection system and replace chlorinator 2. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | ARPS - Peter from OCWA called, chemical system maintenance completed, back to normal. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071015 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | SHETCS - Hypo P1 uncomm start/ hypo pumps 1&2OOS alarms. Called Tim H, Jenn S will attend site. | FLAG | stage2_low_confidence | 0.013788 | ML: above threshold (no LLM available) — 0.014 | oos [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.013788 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | KLMCIA, KLPSWL - Aaron CM working on APN network configuration. 15:05 Aaron CM completed work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039622 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | EGMCDD - Pressure low alarm, quick spike. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068941 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | GWTP - Derek from Aquazition is flushing in Keswick from 8:30 -1Pm. Emailed East OP team. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046393 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | GWTP, UV Reactor 2 Intensity lo (HMA). plant currently running, trends show a small gap with low intensity, notified Patrick F, directed to disregard as the intensity is back to normal consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059811 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMW15 - Donnald M and Alex B , cleaning silicate tank. Disregard silicate tank level alarms for the duration of the work. | FLAG | stage2_low_confidence | 0.0082501 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0082501 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NMPSKC - Jason G running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056706 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | STETBR - Tower level Hi alarm. Placed STW3 pump back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053901 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | GWTP- Patrick F onsite working on MIT for Train 6. Disregard all train 6 alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.006777 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Mehdi) and requested two pumps on 02:22 - Called Toronto Water (Paul) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053221 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MTW12- Historian Heartbeat Alarm. Notified Artour L. He will look into it. 11:17- Artour L unable to reset remotely. He will attend site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051791 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Pooriyah) and requested to stop pumping to reservoir | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070578 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | QVW34- Influent Free Chlorine HiHi. Quick spike, then recovered, cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055687 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | QVW34 - Well 3 pump running in manual/recently started. Influent chlorine residual LoLo alarm. Well 3 pump interlocked. Notified William M will attend site. | FLAG | stage2_low_confidence | 0.0080954 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080954 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | YWS + NYWS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038512 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | ARPS- OCWA called to inform they are switching pumps from pump 7 to pump 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051857 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | AUPSRR - Historian Heartbeat alarm, cleared when acknowledged. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070894 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | Carter Dunn Signing In, 0D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | RHRSTR, Deactivated D1 to have more water move from MARS to RHRSTR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049607 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | KCETFS, Isolation Valve Fault/Control Panel Power Fail, Tower @ 68%, Draining. KCETDS, Control Panel Power Fail, Tower currently isolated KCPSDS, PAC Control Panel Power Fail/Site Power Fail/Discharge FCV Fault. Pumps currently interlocked Notified Jen S, she is heading to site 01:26, Contacted Hydro 1 and spoke with Operator Abby, Informed her of the outages, Abby informed the ROC that this was a planned outage and work is currently being done to their system. Power outage should last from 1AM-4AM. Passed on this new information to Jen S 02:20, Notified Jen S that we have lost communication to the king city sites CMU5: W11756686 | FLAG | stage2_low_confidence | 0.015543 | ML: above threshold (no LLM available) — 0.016 | fault [equipment_failure] | 0.015543 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | KSETDP- Phil D onsite with PCS working on chlorine system. Disregard all related alarms. | FLAG | stage2_low_confidence | 0.009198 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.009198 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | JFPS - Man/start P2 as per Interim Memo. 07:24 Man/stop P2, back to auto. As per Interim Memo. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039493 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | VNRSKS - Placed all pumps at VNPS PD7 man/off and placed all available pumps at MAPS PD7 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057966 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | AURSBS - Activate duty 1 as MARS reaching high level | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046546 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | AUPSRR - Ian W working on OIT, disregard historian heartbeat alarm. 15:27 Ian W completed work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0043887 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NRETCR- Donald M onsite for work orders including chlorine analyzer maintenance, building low temp and valve exercising. | FLAG | stage2_low_confidence | 0.013967 | ML: above threshold (no LLM available) — 0.014 | work order [maintenance_action] | 0.013967 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | SHTP, Adjusted Tower Duty 1 from 15/45% to 50/80% as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049023 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMW15- Well 15 Emergency Stop Alarm. Lee F onsite. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system] | emergency [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: 3C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | HUB3SVR- Communication to H4AUSSP1 Server Alarm. Notified Artour L. He will take a look. 09:52- Artour L called back. There was an accidental restart. All old H4AUSSP1 Alarms came back in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0065589 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | RHRSTR- Activated duty as MARS approaching low level alarm setpoint | FLAG | stage2_low_confidence | 0.0072373 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072373 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | STW2/3, Placed wells 2/3 in manual/on to help fill STETBR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047638 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | SHETCS, Activated D1 to top up the tower | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044075 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AUW2/3/5, Placed wells 2/3/5 man/off to take more water from AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049729 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NMW15 - Eric S finished on site. Placed well 15 pump back to auto as per Joe D. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004994 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AUVCBS - Artour L called with update. Communication restored, slow. Network team troubleshooting. VC opening slow. | FLAG | stage2_low_confidence | 0.0082208 | ML: above threshold (no LLM available) — 0.008 |  | 0.0082208 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | STETBR - Tower Level Lo alarm came in. Placed STW2 and STW3 man/on, as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058955 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MAPS PD7 - Pump 3 to auto. VNPS PD7 - Pump 1 man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039263 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -6C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | KSTP - Fin water tot CL2 res fault, Fin flouide water res lolo. Disregard as per shift report | FLAG | stage2_low_confidence | 0.0089197 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure] | 0.0089197 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | MTETNL, Travis W on site, disregard intrusion alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063385 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | Connor Smith signing in 9C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | EGMCDD, Motorized Valve 1/2 Fault, Power has come back to site, tried resetting fault but no success, notified Gary P, he is looking into the issue 19:57, Gary P directed to disregard for the night, if any low pressures come in, Gary would like a call consult | FLAG | stage2_low_confidence | 0.0076131 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0076131 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS PD8 - Benson S running generator, he placed pumps man/off to switch to gen. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052929 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | NMW15 - Treated total chlorine hi, able to clear but looking a little hi. Seeing influent higher than target range, dropped chlorinator 2 dosing from 52 to 50 | FLAG | stage2_low_confidence | 0.0075946 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075946 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MTW12 - Historian Heartbeat alarm cleared, Artour L leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054357 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MKRSEM- Called Toronto (Zoran) and requested two pumps on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062729 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | KCETFS- Valve Room Eyewash Flow Alarm, Valve Room High/Low Temp Alarm. Called Jen S who is signed in onsite. No answer, will try again. 09:35- Called Jen S. She is onsite testing these alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0069039 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS PD8 - Placed pump 3(currently running ) man speed setpoint 30%. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050271 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | ARPS - Peter from OCWA called, completed P2 test, switching back to P7. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050885 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | AUPSRR- Donald M running generator and doing chlorine cylinder change. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066422 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | JFPS - Man/start Pump 1 as per Interim memo. 07:20 Man/stop Pump1, back to auto/duty 2 as per Interim memo. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041986 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | GWTP- Darek from Aquazition on his way to Keswick for flushing. Notified Patrick F, he will contact Darek. (Memo from Aaron W. to have system full for Linear/area/town work). | FLAG | stage2_low_confidence | 0.010509 | ML: above threshold (no LLM available) — 0.011 |  | 0.010509 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | QVW12 - Kyle R replacing lights/controls on well 2 pump. Placed Well 2 pump man/off for the duration of the work. HLPSYS - Dan B on site for generator maintenance. Disregard generator alarms. | FLAG | stage2_low_confidence | 0.0073964 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0073964 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | MTW3, NMMCWA- Aaron CM working on network. May briefly lose comms. No impact to operations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055754 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | KSTP - Backwash pump 1 uncmd stop. Alarm cleared, filters backwashing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055899 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | MTETNL - Intrusion alarm. Travis W on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061374 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | STW3 - Ian W working on OIT. 14:00 Ian W completed work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033376 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | NMVCIB - Adjusted flow from 80 to 40l/s to help with NMETHW level. NMVCBA - Adjusted flow from 40 to 80l/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050065 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMTKKC - Eric S working on Ammonia pump 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044626 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NRETCR - Lee F working on altitude valve. Requested altitude valve man/close. Deactivated Duty 1 and man/closed altitude valve and switched controlling tower to NRETBR | FLAG | stage2_low_confidence | 0.0079459 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079459 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water and requested they activate two pumps to push flow to MKRSEM | FLAG | stage2_low_confidence | 0.0073135 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073135 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AURSBS - Donnald M and Chris S finished on site. Chlorine pump 1 on duty 1 , chlorine pump 2 man/off. STW12 - Jack P finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044751 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | KSTP - Eric S. called to inform that he is on site to replace the flow sensor on the raw water turbidimeter 11:34 - Eric S. is finished on site and is now headed to GWTP | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044434 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | HLW1- Treated Free Chlorine Hi Alarm. Tim H requested to rotate Ammonia Pumps, and disable duty rotate. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065001 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two MAPS pumps to one VNPS and one MAPs pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.007042 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | VNPS - Benson S on site for station checks. Benson directed to activate the duty for RHRSTR so that BVPS activates. Made necessary changes. | FLAG | stage2_low_confidence | 0.0086022 | ML: above threshold (no LLM available) — 0.009 |  | 0.0086022 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | 12:30 MKRSMR - Res low level alarm. Duty active, pump 10 is running, no flow. Notified Mehdi from Metro, he will investigate. 12:37 Confirmed flow , res filling. As per Mehdi Pump 10 is running for gen test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NBW2- Ric L finished onsite. Cole W still onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045902 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NBW3- Influent Free Chlorine LoLo Alarm. Interlocked well on schedule mode start up. Influent recovered. Cleared alarm and well started back up. | FLAG | stage2_low_confidence | 0.0075439 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0075439 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | KCETFS - Historian Heartbeat. Evgeny S. working on OIT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006185 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STPSMR- Free Residual (sim) LoLo Alarm. Recovered next reading. Cleared alarm. | FLAG | stage2_low_confidence | 0.0073186 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073186 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMW12 - Influent Free chlorine residual quick spike on duty start. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058475 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | EGMCDD - Artour L. on site testing valves 09:37 - work completed, confirmed all alarms cleared. Leaving site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.005049 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | NMETIB- Deactivated duty NMVCBA- Adjusted from 80 back to 40L/s NMVCIB- Adjusted from 40 back to 80L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040573 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | VNPSAP - Dave T on site to complete work orders including flood alarm test, low temperature alarm test and chlorine analyzer maintenance. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | KSTP - Finished Water Fluoride Residual LoLo, Fin Water Fluoride and Total CL2 alarms came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0083124 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0083124 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | VNPS - Benson S on site for a station check and has requested that BVPS be activated. Activated duty 1 at RHRSTR to activate the BVPS pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065727 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | NMETDD - Site hydro power failure, UPS supply power failure, PAC control panel power failure. No outage showing on Newmarket outage map. Informed Chris S to confirm we are now running on UPS for communication as although site is offline and empty we still monitor pressure which may be powered by UPS battery temporarily. CMU = 11749865 13:10 - Confirmed we are on UPS power. Called Donald M to update of situation, will head to site CMU = 11749873 | FLAG | stage2_low_confidence | 0.025997 | ML: above threshold (no LLM available) — 0.026 | failure [equipment_failure] | 0.025997 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | MARS - Low level alarm came in. Deactivated VNRSKS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066733 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | RHPSPA - Parth P working on Pump 3 pressure switch replacement. Placed P3 man/off and assigned P1 to duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060477 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | KLET27 - Aaron CM from PCS will be switching the network cellular connection. The tower is almost full, deactivated the duty so that the pumps shut down and tower drains during this work. No impact to operations expected. | FLAG | stage2_low_confidence | 0.010245 | ML: above threshold (no LLM available) — 0.01 |  | 0.010245 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | BVPS- Jack P and Patrick F onsite for work orders. Testing sump floats, hihi alarm and running generator. | FLAG | stage2_low_confidence | 0.015006 | ML: above threshold (no LLM available) — 0.015 | work order [maintenance_action]; alarm [control_system] | 0.015006 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | STW3 - Influent chlorine residual low, man/started well 3 pump. Increased chlorinator 1 dosing factor from 250 to 253%. 12:42 Influent chlorine residual value recovered. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063656 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | MTW12- Gen tank 1 level Hi alarm, disregard as per Shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054288 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | SHTP, Kathryn D from Public health called, notified ROC that she got a call from a Liam A (King Bylaw Officer) that the doors to the building are wide open. Notified YR security, they will send one of their guards over to lock the site up. Notified Jen S of this call as well. Kathryn Damas ? 2893382495 (Public Health Inspector) Liam Audette ? 9058334053 (Bylaw) | FLAG | stage2_low_confidence | 0.011177 | ML: above threshold (no LLM available) — 0.011 |  | 0.011177 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | KSTP - Raw water turbidity fault alarm. Checked site, plant is currently not active. Shift report states this alarm is a disregard. | FLAG | stage2_low_confidence | 0.018344 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.018344 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | Connor Smith signing in -12C Windy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042119 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | QVW34 - PAC minor fault, monitor site as not active. Email on-call PCS Chris S | FLAG | stage2_low_confidence | 0.0083466 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0083466 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | KCETFS - Activate duty 1 for interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004336 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | KSETDP - Phil D and Chris S working on chlorine system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062044 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | VNPSAP- TIm H requested to place pumps in manual. Will be performing some valving as a test to float VNETAG tower today. | FLAG | stage2_low_confidence | 0.0084297 | ML: above threshold (no LLM available) — 0.008 |  | 0.0084297 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | MTETNL - Travis W on site for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054385 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two MAPS pumps to two VNPS pumps to reduce demand on MARS. | FLAG | stage2_low_confidence | 0.0074616 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074616 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: 2C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMVCBA - Placed back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005522 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | YWS + NYWS Normal NMVCBA, Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041247 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | NMETIB - Activated Duty 1 to offset NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044585 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | QVW12 - Chlorine gas leak alarm. Eric S called to inform that there is a chlorine odour in the room which is causing the chlorine gas leak alarm. Eric contacted Joe D to return to site to investigate the chlorine leak source. Created CMU5#W11764741 for Joe D. #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | VNPS- Benson S onsite for work orders. Requested to activate BVPS. | FLAG | stage2_low_confidence | 0.010963 | ML: above threshold (no LLM available) — 0.011 | work order [maintenance_action] | 0.010963 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | VNPSCD - Chemscan OFFLINE status alarm, Benson S working on it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071557 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | RHRSTR - Deactivated duty 1 to prevent overfilling in early morning low demand period. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054438 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | GWTP - Backpulse tank 2 level hi alarm. Checked site, backpulse tank 2 reading is high. Trending shows that the level has been slowly climbing but the fill valves are showing as closed and interlocked. If the HiHi alarm triggers will call OCO as the valves may be passing. | FLAG | stage2_low_confidence | 0.014393 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system] | 0.014393 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | STW12 - Jack P flushing silicate system. He placed Wells 1,2 pumps man/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051552 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | STRS48- Jack P onsite for Cl analyzer cleaning. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004536 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | HLW1 - Tim H on site, ammonia pump 1 was airlocked, back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046832 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | NBW3 - Influent free chlorine lolo on startup, analyzer came back within range and cleared alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060327 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | STETBR - Tower level lo STW12/STW3 - Place well 1 & 3 man/on for zone 1 tower NMETIB - Communication alarm, able to clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0049523 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | STW12- Placed well 2 man/on STW3- Placed well man/on for STETBR Fill Cycle | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042856 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | JFPS - Placed pump 1 Man/on as per Cole W's interim procedure 07:42 - Placed pump 1 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033454 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | Carter Dunn Signing In, 2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | MAPS PD7, Placed pump 3 in auto VNPS PD7, Placed pump 1 man/off 22:08, Reverted the changes so MAPS PD7 pump 3 is back to man/off and VNPS PD7 pump 1 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031955 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STETTL- Wes from Town of Stouffville called to inform of flushing in Zone 2 for a couple of hours. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057902 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | GWTP - Parth P and Rick L finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055439 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | VNRSKS - Placed all pumps at VNPS PD7 man/off and placed all available pumps at MAPS PD7 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057966 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | AUPSRR - Free chlorine hihi, trend show spike in reading but drops within range next reading. Able to clear alarm | FLAG | stage2_low_confidence | 0.0089941 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0089941 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | MKRSEM - Request TO (Zoran) for 2 pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044077 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | STW3, STETBR- Jack P onsite running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045103 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | BLW12- Station Turbidity Hi Alarm. Rotated silicate pumps so silicate pump 2 in duty 1. Notified Joe M. He will take a look 17:51- Joe M placed well man/off and will attend site. W11740913 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.004104 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: -7C and Cloudy MAP8 - PD8 P1 Pump 1 failed to stop alarm came in. Checked site and noticed that AURSBS recently deactivated. Ack/reset and alarm cleared. Will monitor | FLAG | stage2_low_confidence | 0.013136 | ML: above threshold (no LLM available) — 0.013 | failed [equipment_failure]; alarm [control_system] | 0.013136 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Peter) and requested two pumps on | FLAG | stage2_low_confidence | 0.0083662 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0083662 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | ARPS- Peter from OCWA called to inform they are rotating from pump 6 to pump 7 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052813 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MKRSEM- Peter from High Level finished running pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061387 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NMW15 - Alex B called requesting CMU for Eric S/ Treated Total chlorine analyzer motor issue. # CMU5 W11761894 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006385 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STPSMR - Lee F finished on site. Assigned P1 to Duty 1, P2 to Duty 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047681 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | RHPSPA- Disch. Header Flow 1 LoLo. Duty just deactivated. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054264 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | MKETFA - Peter from Toronto Water caleld to inform that he would like to exercise a valve but would require the pump be turned off for 10 mins. Peter will call back once the valve exercise is complete 10:33 - Peter called to inform that he is finished exercising the valve and pump 3 is now running again | FLAG | stage2_low_confidence | 0.0088191 | ML: above threshold (no LLM available) — 0.009 |  | 0.0088191 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | NMTKKC - Donald M. called to inform that he is on site topping up the ammonia system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066858 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | ARPS - Martin (OCWA) informed switching from P5 to P6. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047098 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | MARS - Noticed Toronto Water Pushing higher than usual flow for 1 hour. Called Toronto Water (Pooriyah) who will place the flow back to optimal range YWS + NYWS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052875 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP- Ric L finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054719 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | STPSMR- Jack P called. He will attend site and coordinate with Patrick F regarding high lifts interlocked | FLAG | stage2_low_confidence | 0.0078183 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078183 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps to one VNPS pump and one MAPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065724 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | JFPS - Lee F finished on site. Pump 2 man/off, assigned P3 to duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047547 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | STW3- Ric L onsite to trouble shoot hypo tank LIT 10:02- Finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035828 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS- Dave T onsite for work orders including chemscan maintenance, ammonia system maintenance, Cl leak detection test, and Cl analyzer maintenance. | FLAG | stage2_low_confidence | 0.025763 | ML: above threshold (no LLM available) — 0.026 | work order [maintenance_action]; leak [infrastructure] | 0.025763 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | YWS + NYWS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004717 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | AUPSRR - post injection free chlorine hi and hihi alarms. Checked site, trending shows an abnormal spike of the post injection free chlorine reading which returned to normal range within one reading interval. Reset alarms. | FLAG | stage2_low_confidence | 0.017156 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system]; alarms [control_system] | 0.017156 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | QVW34 - Power failure alarms came in along with generator running status. Checked site. Likely a power blip and site is still running on hydro power. All alarms cleared | FLAG | stage2_low_confidence | 0.019148 | ML: above threshold (no LLM available) — 0.019 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019148 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | SHTP - Res total chlorine lolo, trend shows reading have sudden drop within lolo range. Monitored for next reading, no sign of analyzer reading changing, possible fault. Informed Jen S, will head to site CMU = 11750153 | FLAG | stage2_low_confidence | 0.013221 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure] | 0.013221 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | BLW12 - Joe M. called back to inform that he is finished on site and the well 1 is running. Joe informed that if the hi turbidity levels come back in, the wells can be placed man/off | FLAG | stage2_low_confidence | 0.0080453 | ML: above threshold (no LLM available) — 0.008 |  | 0.0080453 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS PD8 - Pump 2 not ready alarm came in. Checked site. Pump was left man/off with same alarm earlier in the day. Pump 2 is a duty 3 pump. Placed pump back to auto and alarm cleared. Will continue to monitor 23:32 - Alarm came back in and stayed outstanding. Placed pump man/off and will send an email to the central/west team | FLAG | stage2_low_confidence | 0.010483 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010483 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | STW3 - Jack P on site and will be completing the chlorine leak detection alarm test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | RHRSTR- Deactivated duty as MARS approaching high level. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062229 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMTKKC - Deactivated duty in preparation for interim procedure | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064147 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two MAPS pumps to one VNPS and one MAPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.007042 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP - Sutton header fluoride low alarm. Checked site, Sutton system duty is not active. Trending shows a slow dip of the fluoride reading for the Sutton header line. Will monitor this value when the Sutton header opens for duty 1. | FLAG | stage2_low_confidence | 0.011882 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system] | 0.011882 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STW12/STW3/STRS48/STPSMR - placed all wells and pumps in manual/off for the duration of the PCS/Network scheduled upgrades. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064993 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | VNPSAP - Chris S. is on site and will be replacing the UPS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059483 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | Angelica Chepiga signing in, weather +4C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | STW3 - Influent chlorine residual low alarm. Duty just deactivated. Will monitor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058447 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | MKRSEM - Pouria from Metro running generator, will run 2 pumps , one in a time, 30 minutes each. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057344 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | HLETPR- Tim H onsite running generator, chamber flood and low temp alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STPSTL- Yash S requested pumps man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057391 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | NMETDD - Tyler Z will be attending site, & contacted Newmarket Hydro regarding hydro power failure. Donald M leaving site CMU = 11749890 | FLAG | stage2_low_confidence | 0.010457 | ML: above threshold (no LLM available) — 0.01 | failure [equipment_failure] | 0.010457 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | NMETIB, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040018 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP- Jackie S performing backwash on GAC2. Disregard related alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0064165 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STETTL- Yash S finished with work. Requested to clear all communication alarms. Will be performing work on STETBR in one hour. | FLAG | stage2_low_confidence | 0.011007 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.011007 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | RHRSTR, Deactivated D1 so water is moved from MARS to RHRSTR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048183 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | Angelica Chepiga signing in,weather -7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | SHTP - Jen S called, Jen S and Dan B on site, constructor working on UVs. Plant will be off for the day. Disregard alarms for the duration of the work. | FLAG | stage2_low_confidence | 0.011846 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.011846 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | RHPSPA - Parth P finished on site. Placed Pump 3 back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | Newmarket Water System- Received a call and email from Traci from roads regarding a broken valve lid in the road at 16775 Leslie just North of Mulock. Appears to be York Region 750mm Water Main according to All Pipes. Notified Dwayne L. He will have someone replace it at some point today. | FLAG | stage2_low_confidence | 0.013722 | ML: above threshold (no LLM available) — 0.014 |  | 0.013722 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | MKRSEM - Low level alarm. Called Toronto Water (Zoran) and requested two pumps on to push flow to MKRSEM. | FLAG | stage2_low_confidence | 0.0086914 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086914 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | GWTP - GAC 2 level fault, low and lowlow level alarms. Checked site, the GAC 2 level sensor has faulted and is reading an abnormal value resulting in the low and lowlow level alarms. The plant is currently off as the system is full. Will monitor these alarms and contact the OCO closer to duty start later in the morning. | FLAG | stage2_low_confidence | 0.034134 | ML: above threshold (no LLM available) — 0.034 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.034134 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | NMW136 - Alex B testing chlorine leak alarm and troubleshooting influent chlorine analyzer. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | Adeela Khan signing in. Weather: 8C and raining | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044658 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | MTW12- Travis W onsite for turbidimeter maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046543 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | QVETQS - Site power failure and site heat trace fault alarms came in. Tower is draining. Likely apart of the power blip. All alarms have been cleared and site is operating normally | FLAG | stage2_low_confidence | 0.023253 | ML: above threshold (no LLM available) — 0.023 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.023253 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | NMETDD - Site back online, Tyler Z leaving site, informed Chris S of outstanding heartbeat alarm and UPS/battery with UPS offline. 16:40 site back in normal operation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060765 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | NMTKKC, Jason G on site, doing a hot water flush to the chemical systems, he is placing the analyzers in calibration mode and turning off the chemical system, directed to disregard at this time | FLAG | stage2_low_confidence | 0.011089 | ML: above threshold (no LLM available) — 0.011 |  | 0.011089 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | MTW3 - Travis W. is on site with Phil D. and will be completing a chlorine system inspection | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052594 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | BVPS- Jack P requested to place pumps back into auto RHPSPA- Jack P heading to site to assist with surge valve work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006904 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | QVW12- Will M onsite. Isolated station for injector work. Disregard low pressure alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0069862 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MKMCAP - PRV chamber flood alarm. Gary P testing alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMW15, Station Turbidity Hi alarm, Rotated Silicate pumps so pump 2 is in D1. Will continue to monitor the site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067893 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | VNETAG - Dave T on site to complete work orders including a generator test run, a flood alarm test and a low temperature alarm test. NBW2 - Rick L on site to complete work on a silicate LIT sensor and a chlorinator. Placed the well pump manual/off for Rick. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | SHTP - Filter 2 turbidity hi alarm. Checked site, filter 1 completed a backwash. Shift report states that post backwash NTU spikes can be disregarded if they reset. Able to reset alarm. | FLAG | stage2_low_confidence | 0.0095539 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0095539 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | MKRSMR - Toronto Water called to inform they have completed their pump testing for COTFA PD6 and the valves at MKRSMR can be returned to normal operations. Made the necessary changes. | FLAG | stage2_low_confidence | 0.0085648 | ML: above threshold (no LLM available) — 0.009 |  | 0.0085648 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | NMETHW, Activated D1 to have towers offset | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044396 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | RHRSTR, Deactivated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040424 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STW2, STW3 - Placed man/start for STETBR fill cycle. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046557 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | NBW5 - Discharge Press LoLo alarm. Well 5 Local off. Cole W signed in station logbook. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060729 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STW5- Received a call from YD Lab Tasmeem Karimgee (905-686-0041 ext. 4300) requesting a resample. Forwarded email to East Ops and informed Patrick F, acting team lead. Resample will be taken tomorrow. | FLAG | stage2_low_confidence | 0.0078712 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078712 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | Connor Smith signing in 0C Snowy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041992 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | MTW3- Travis W onsite for turbidimeter maintenance | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046116 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | MTW3, NMMCWA APN- Aaron CM Completed work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044763 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0060919 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | MKRSEM, Notified Toronto operator Medhi to stop filling the res | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006281 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | ARPS - Peter (OCWA) confirmed ops finished work on HACH ammonia analyzers. No alarms, will check trending | FLAG | stage2_low_confidence | 0.0095961 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0095961 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | SHTP- KMNO pump 2 uncommanded stop alarm. Plant just deactivated. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058607 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | RHRSTR, Deactivated D1 to allow water to move from MARS to RHRSTR | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049389 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | KCETDS, Historian Heartbeat Alarm, power has been restored on site, notified Chris S, he will look into it. CMU5: W11756711 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.004778 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | JFPS - Deactivated pump 1 and placed back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | STETBR - Tower high level alarm. Called Jack P to ensure he is completed sampling at STW12 and STW3 and that those well pumps can be placed into auto mode. Jack stated he is finished with the sampling at those wells and is currently at STETBR for sampling. Jack requested that the duty for STETBR be deactivated so the tower can drain for his sampling. Made the necessary changes. STRS48 - Jack P has requested that the high lift pump 2 be placed in auto mode. made the necessary change. | FLAG | stage2_low_confidence | 0.027239 | ML: above threshold (no LLM available) — 0.027 | alarm [control_system] | 0.027239 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | VNPS- Benson S onsite for PMs including generator run, health and safety, air valve flush, and chemical system inspection. | FLAG | stage2_low_confidence | 0.0085034 | ML: above threshold (no LLM available) — 0.009 |  | 0.0085034 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | NMTKKC- Joe W onsite testing flood alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | GWTP - GAC 4 flow control valve deviation, disregard as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050846 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | BLW34 - Placed well pump 3 in auto as directed by Patrick F. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048763 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | VNRSKS - Placed pump 1 at MAPS PD7 into man/off and placed pump 3 at VNPS PD7 into auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055444 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | JFPS- Placed pump 2 in man/on for 1 hour 07:32- Placed pump 2 man/off Interim Procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0026697 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | VNRSKS - Swapped supply pumps from two MAPS pumps to one MAPS pump and one VNPS pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0072185 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | KCETDS - Outlet pressure lolo, tower finished draining to 0% around 10am this morning as its now offline. Notified Jen S of pressure alarms, okay to disregard for weekend and okay with pressure dropping to 0 Consult | FLAG | stage2_low_confidence | 0.010284 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010284 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038512 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | JFPS - Man/stop pump 1 and put pump 3 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046879 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | STPSMR - Free chlorine res lolo, came in during startup. Infomred Patrick F, will head to site. STETBR - Deactivate duty 1 to assist with Tenth Line tower STW12/STW3 - place wells 1 & 3 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063717 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMW15 - Ben H onsite working on silicate, will run well later AUPSOH - Rick L finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047194 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | Adeela Khan Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | ARPS - Peter from Peel/OCWA transmission control called to inform he is completing the daily pump rotation. | FLAG | stage2_low_confidence | 0.0079279 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079279 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | AUPSRR - Donald M. turning chem system off for analyzer maintenance | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065752 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMTKKC - Hypo tank 1 HiHi alarm. Jason G on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0048084 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | NMETIB- Activated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053242 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | MKRSEM - Free chlorine residual fault alarm. Patrick F on site sampling and triggered this alarm. Cleared alarm. MTW12 - Hypo pump 1 and Silicate pump 1 failed to start alarms. Well pump 1 is running in local mode, operators likely on site for sampling. Well has interlocked due to hypo pump 2 and silicate pump 2 were placed in manual mode. Travis W is on site and well is being pumped to waste during sampling. No flow being directed to users. | FLAG | stage2_low_confidence | 0.039418 | ML: above threshold (no LLM available) — 0.039 | fault [equipment_failure]; failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.039418 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | STW3 - Noticed that the well was turned off. Called Jack P. who informed he noticed high turbidity that did not trigger an alarm and shut the well off. Jack informed he will try to determine the cause of high turbidity | FLAG | stage2_low_confidence | 0.010797 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010797 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | QVW34 - William M on site performing chlorine analyzers and turbidity meter maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005152 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | QVW12- Kyle R finished onsite. Placed well back into auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004779 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AUPSRR- Donald M onsite doing Cl analyzer maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061708 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AUVCBS - Site back to normal. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005473 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | GWTP - Parth P. and Ric L. doing annual calibrations on membrane LIT and PITs. They will notify ops on site. | FLAG | stage2_low_confidence | 0.0073034 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073034 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040295 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AUW14- Joe D and Donald M working on Ammonia System and placed wells man/off 14:59- Finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040343 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | VNP7 - P1 and 3 man/stop MAP7 - P2 and 3 back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039585 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | JFPS - Activated pump1 in manual mode for one hour as per the interim procedure | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052875 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | JFPS - Placed pump 1 Man/on as per Cole W's interim procedure 10:20 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0033143 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | NMVCBA - Placed valve man/open at 40 L/s | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044121 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | HLW1 - Treated Free Chlorine Hi alarm came in. Checked site. Duty recently activated. Free chlorine value did not recover. Rotated ammonia pumps so that pump 2 is now running in duty 1. Will continue to monitor | FLAG | stage2_low_confidence | 0.010667 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010667 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | GWTP- Ric L finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054719 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | QVW12, QVW34- Noticed that all wells were in manual/off. Nothing noted on SCADA Report or e logs. Placed all wells back into auto. | FLAG | stage2_low_confidence | 0.0085643 | ML: above threshold (no LLM available) — 0.009 | scada [control_system] | 0.0085643 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP - UV 1 and UV 2 comm alarms and UV 1 uncommanded stop alarms. Contacted Jackie S who directed to deactivate the duty so she can investigate. | FLAG | stage2_low_confidence | 0.0092666 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0092666 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMW15 - Silicate pump 1 working in good condition now dropping turbidity, rotates to silicate pump 2 as requested by Ben H to test silicate pump 2. | FLAG | stage2_low_confidence | 0.007268 | ML: above threshold (no LLM available) — 0.007 |  | 0.007268 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | GWTP - Backpulse tank 2 level hihi alarm. Called Patrick F to inform. Patrick directed to initiate a backwash sequence for membrane tank 1 to drawdown the backpulse tank. #consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064507 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | BLW3 - Influent free CL2 lolo, Patrick F attending site CMU = 11749880 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042045 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | NMETIB - Activated duty 1 to maintain level offset from NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048893 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | JFPS - Benson S requested to run pump 1. Rotated pump 1 to duty 1. place pump 3 duty 5. Pump 1 & 4 active | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060965 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | VNP7 - Place pump 1 & 2 auto. MAP7 - Place remaining pumps man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041746 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | Carter Dunn Signing In, 3D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | NMETIB - Deactivate duty 1 to help offfset NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045905 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | KCETDS - Metering Chamber Flood Alarm came in. Shift report does not indicate to disregard alarm. Called Cole W. who directed to disregard alarm until tomorrow #CONSULT | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | RHPSPA- PD6 Surge Valve 1,2 Open Alarms. Alarms cleared MKVCMM- Reverse Flow 2 HiHi Alarms. Alarms cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.00612 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | AUPSWS - Kyle R /maintenance replacing floats. Testing flood alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | HLW2 - Well 2 pump failed to stop alarm at duty stop. Alarm cleared in a few minutes. | FLAG | stage2_low_confidence | 0.018907 | ML: above threshold (no LLM available) — 0.019 | failed [equipment_failure]; alarm [control_system]; pump failed [infrastructure] | 0.018907 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STW12 - Jack P and instrumentation team completed Hypo tanks replacement. Site back to normal. Jack P is running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064391 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STETBR - Level Hi alarm, placed STW12 pump 1 and STW3 pump back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057036 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | MTW12 - Travis W performing PM's including: Turbidity meter, chlorine analyzers cleaning, chlorine and silicate systems maintenance, working on silicate pump 2, generator test, VLVs exercising, Hi/Low temp alarms testing. | FLAG | stage2_low_confidence | 0.013059 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.013059 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | NMVCBA - Placed valve man/open at 40 L/s 00:09 - Placed valve back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0030115 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | MARS - Level Hi alarm came in. Activated AURSBS | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065891 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | BLW34 - Dan Z called to inform that BLW34 will be offline for tonight. Dan Z and a contractor will be on site tomorrow to address a leak in the chlorine system. | FLAG | stage2_low_confidence | 0.011499 | ML: above threshold (no LLM available) — 0.011 | leak [infrastructure] | 0.011499 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | BLW3 - Travis W on site to complete turbidity analyzer maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046879 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | YWS + NYWS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | QVW34- Will M onsite working on chlorine analyzers and running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050779 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | NMVCBA, Placed flow set point to 80L/sec from 40L/sec NMVCIB, Placed flow set point to 40L/sec from 80L/sec. Both NMETIB and NMETHW are active | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034016 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | AURSBS, Activated D1 AUW2/3/5, Placed well 2/3/5 in man/on. 02:27, Placed wells 2/3/4 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0023071 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Newmarket, Leslie Street & Stellar Drive, Karen from Dispatch called, informed ROC of a main break, after checking all pipes, notified Karen to get in contact with the Town of Newmarket. Reviewed Newmarket trends, no abnormalities on YRs end | FLAG | stage2_low_confidence | 0.014427 | ML: above threshold (no LLM available) — 0.014 |  | 0.014427 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | ARPS- OCWA called (Peter) and informed will be shutting down pump 7 and starting pump 5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055086 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | ARPS, Tegbeer from OCWA is rotating pump on site so pump 5 is man/off and pump 6 is in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005318 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | KCPSDS - Dan B. is on site for a work order for the hot water at the eyewash station. | FLAG | stage2_low_confidence | 0.012912 | ML: above threshold (no LLM available) — 0.013 | work order [maintenance_action] | 0.012912 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | AUW14 - Joe D. is on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038653 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | AUW2/3/5, Placed wells back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042998 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | AUW14, Placed wells 2/3 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043272 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS Normal Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039286 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | AUETFC - Joe D on site to complete work orders including deplox analyzer maintenance, temperature alarm tests and eyewash alarm test. | FLAG | stage2_low_confidence | 0.017044 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action]; alarm [control_system] | 0.017044 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | GWTP- Ric L finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054719 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | QVW34 - Ben H directed Man/start well 3 pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045164 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | MAPS- Placed PD7 Pump 2 in manual VNPS- Placed PD7 Pump 2 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041696 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | MARS - Jerry from OCWA called to inform that he will be completing the daily pump transfer. Will be switching from pump 6 to pump 5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067546 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | MKVCAP. Rob P on site, working on the valve chamber disregard alarms from site | FLAG | stage2_low_confidence | 0.0082957 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0082957 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | JFRS - Man/stop pump 3, place pump 1 man/on for interim | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047381 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | AURSBS - Chlorine pump 2 fail to start alarm. Checked site, Aurora central system duty recently activated which opened AUVCBS and triggered the chemical system at AURSBS. Chlorine pump 2 failed on start, cleared alarm twice. Chlorine pump 1 and chlorinator 1 are currently Manual/off and able to run in an emergency. Called Donald M who will check SCADA. 22:02 - AURSBS - Chlorine pump 2 fail to start. Donald M called back to inform he was able to get chlorine pump 2 running. If the chlorine pump fails on later fill cycles Donald directed to use chlorinator 1 and reduce the flow setpoint of AUVCBS to 400L/s. If chlorinator 1 is maxed out at this flow setpoint Donald directed to reduce the combined chlorine target setpoint. # consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; failed [equipment_failure]; scada [control_system]; alarm [control_system] | emergency [critical]; failed [equipment_failure]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP - GAC 4 Flow control valve deviation alarm, disregard as per shift report. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059835 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NRETBR - Christian B and Joe D on site performing PMs including Temp alarms test and chlorine analyzers maintenance. | FLAG | stage2_low_confidence | 0.0098686 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0098686 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | JFPS - Lee F performing vibration pump testing, switched P1 to Duty 1 and P4 to duty 5. Man/stopped P3 and Man/started Pump 2 . Lee F confirmed with Cole W , ok to run P2. | FLAG | stage2_low_confidence | 0.015128 | ML: above threshold (no LLM available) — 0.015 | vibration [equipment_failure] | 0.015128 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMTKKC - Parth P on site to verify the analyzers following the scheduled chemical analyzer work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0070619 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | NMTKKC - Joe W working on site, placing all chemical pumps man/off for 30 minutes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050249 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | BVPS- Lee F onsite. Requested Pump 3 off and Pump 2 on. Pump 1 already running in duty. Confirmed okay with Benson S. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006341 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | MKRSEM - Called Toronto Water (Brett) and requested they deactivate the pumps pushing flow to MKRSEM. | FLAG | stage2_low_confidence | 0.0076901 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076901 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | MARS - Hi level alarm came in. Short cycled VNRSKS to help lower levels at MARS | FLAG | stage2_low_confidence | 0.0077116 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077116 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | GWTP - Called Patrick F. to address the outstanding GAC 2 Level LoLo and fault alarms. Patrick informed he will take a look #CONSULT | FLAG | stage2_low_confidence | 0.0098091 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0098091 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA report | FLAG | stage2_low_confidence | 0.013702 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.013702 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | RHPSPA- Patrick F onsite for work orders including generator run, flood alarm and surge valve. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | KSTP - Place highlifts in manual. with highlift pump 3 man/on GWTP - Deactivate duty 1 as per Aaron W for instrumentation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053373 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | QVW12 - Kyle R finished on site, Placed Well 2 pump to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045524 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | VNPS7 - Place pumps 1 & 3 auto MAP7 - Place pump 1, 2 & 3 man/off, done to conserve MARS water and drawdown from Teston | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053651 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | GWTP - Rick L onsite for annual calibrations | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059125 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMW15- Alex B onsite working on turbidimeter. NMW13- Placed well back into auto for completion of NMTKKC work. Confirmed ok with Alex B. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005719 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | AUPSOR - Joe D onsite, requesting CMU for Parth P who is attending site for crack in probe for deplox. CMU5 = 11749594 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052834 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMETIB- Activated duty to keep offset with NMETHW | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060388 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | VNETFD- Dave T onsite for work orders including flood alarm, low temp, hi/low level and eyewash. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | NMW136 - Alex B finished on site. NMW15 - Alex B heading to site, will test chlorine leak alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMW136- Alex B working on silicate system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004412 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NMW15 - Ben H finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042176 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | QVW34 - Eric S finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039791 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | NMW15- Alex B onsite working on silicate system | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045305 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | RHPSPA- PD6 Surge Valve 1,2 Open Alarms. Alarms cleared MKVCMM- Reverse flow hihi alarm. Alarm cleared 09:42- PD6 Surge Valve 1,2 Open Alarms came in again and cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0049008 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMTKKC - Chris S finished and off site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057829 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | Christian Van Beek signing in. Weather: -2C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMETIB - Activated duty 1 to maintain level offset from NMETHW. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048893 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | RHRSTR- Activated duty as MARS approaching low level alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069764 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | RHRSTR - Adjusted D1 start from 70 to 65% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044171 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | BLW12- Dan B called. He is onsite assisting with construction project. Power will be shut off onsite. Placed wells man/off 13:06- Dan B finished with work. He will coordinate with Patrick F about running a Well. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067731 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | HLW1 - Treated free chlorine residual HiHi, rotated ammonia pumps, placed P1 man/off, P2 is running on duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060483 | 0 | 0
2026-03 | 2026-03-21 | All Water System ROC General | ROC | NMETHW - Deactivated duty 1 while NMETIB fills. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004545 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | STPSMR- Patrick F requested a CMU5 for Jack P and himself for Free Chlorine Res LoLo W11749627 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003519 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | GWTP- Jackie S finished with Outfall and Sedimentation Tank Chlorine analyzer maintenance. | FLAG | stage2_low_confidence | 0.0072972 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072972 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | GWTP - Comm alarm and UV reactor 1 fault alarms. Called Jackie S who stated the communication alarm interrupted the normal operation of the UV reactor at GWTP. Jackie deactivated system duty and will let the plant shut down. When the system drains the plant will start again. | FLAG | stage2_low_confidence | 0.027343 | ML: above threshold (no LLM available) — 0.027 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.027343 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | BLW12 - Silicate Pump 1 Failed to start alarm came in. Checked site and found that silicate pump 2 has rotated to duty 1. Reset alarm. Will monitor | FLAG | stage2_low_confidence | 0.015208 | ML: above threshold (no LLM available) — 0.015 | failed [equipment_failure]; alarm [control_system] | 0.015208 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | MKVCMM- Reverse Flow 2 HiHi Alarm. Alarm cleared after a few minutes MKVCEM- Forward Flow HIHI Alarm. Alarm cleared after a few minutes | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063205 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | KSETDP- Post injection Total Chlorine HiHi Alarm. Tower is filling, value recovered. Cleared alarm | FLAG | stage2_low_confidence | 0.0080279 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080279 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | RHAMF1 - Unit 1 recirculation pump 1 and pump 2 overload alarms. Checked system, Unit 2 recirculation pumps still active and both AMF fans active. Shift report states that all alarms can be disregarded as long as atleast one fan is running and there is no power outage. Disregard alarms. | FLAG | stage2_low_confidence | 0.017132 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system]; alarms [control_system] | 0.017132 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | SUSP - UV Ch .1 common critical, high level, system critical failure. Status went to normal, known issue upon startup | FLAG | stage2_low_confidence | 0.011494 | ML: above threshold (no LLM available) — 0.011 | failure [equipment_failure] | 0.011494 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 and 2 high level alarm, UV channel 1 and 2 common critical alarm and UV system critical alarm. Checked site, trending shows flow to the UV system recently started. All alarms changed to normal status immediately after triggering. Shift report states that these alarms are disregard if flow to the UV system recently started, such as in this instance. Cleared alarms. | FLAG | stage2_low_confidence | 0.023426 | ML: above threshold (no LLM available) — 0.023 | alarm [control_system]; alarms [control_system] | 0.023426 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | KBSP - Aeration basin 2 suspended solids fault alarm. Checked site, trending shows an abnormal spike of the suspended solids reading which returned to normal range quickly. Able to clear the alarm. | FLAG | stage2_low_confidence | 0.018935 | ML: above threshold (no LLM available) — 0.019 | fault [equipment_failure]; alarm [control_system] | 0.018935 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | NBSP - Vortex 2 air scour uncommanded close alarm. Shift report states this alarm is a disregard if it can be cleared. Able to clear alarm. | FLAG | stage2_low_confidence | 0.0074718 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0074718 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | NBSP - Mechanical barscreen OOS and general alarm. Lauren S called back and will attend site. Created CMU5#W11765387. #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | MTSP - Clarifier 1 no RAS pump running. Clarifier 1 OOS noted on shift report. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | SUSSWB- Ventilation H2S OOR Alarm. Disregard as per SCADA Report. | FLAG | stage2_low_confidence | 0.0085297 | ML: above threshold (no LLM available) — 0.009 | scada [control_system]; alarm [control_system]; h2s [safety] | 0.0085297 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather 10C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | NBSP - Secondary system general alarm on autodialer. No issues on SCADA site, Will monitor | FLAG | stage2_low_confidence | 0.0080526 | ML: above threshold (no LLM available) — 0.008 | scada [control_system]; alarm [control_system] | 0.0080526 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | KBSP - Thick'd sldg pmp 2 pres switch hi, called to inform Lauren S, will take a look on SCADA Consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0063012 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | NMSSHS - PAC communication failure, status went to normal, no issue w trends or site. CLeared alarm | FLAG | stage2_low_confidence | 0.015845 | ML: above threshold (no LLM available) — 0.016 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.015845 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 0. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | KSSSQW - Pump 2 uncommanded stop alarm. Checked site, pump 3 is currently duty 1 and running. Trending shows that pump 2 was running and recently shut down. Able to clear alarm. | FLAG | stage2_low_confidence | 0.0092492 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0092492 | 0 | 0
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | Connor Smith signing in 1C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041757 | 0 | 0
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, Weather: -1C and sun. Please see attached photos of the paper logbooks. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | NBSP - Mechanical barscreen general and out of service alarms. Checked site, barscreen showing local/off. Unable to clear alarm. Will monitor the screen differential level, and call out if it climbs. 01:46 - NBSP - Mechanical barscreen OOS and general alarms. Channel inlet level and barscreen differential continued to climb. Called Lauren S who directed to place the barscreen in the continuous override mode. Made the change, barscreen still in local and unable to clear alarms. Lauren will check SCADA and call back if she goes to site. #consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | out of service [equipment_failure]; oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | Christian Van Beek creating a test log entry at the request of Jennifer Chung. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069174 | 0 | 0
2026-03 | 2026-03-29 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 4. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal KSSP - ZW1 TMP high alarm. Alarm status changed to normal immediately after alarm triggered. Alarm reset on acknowledgement. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0050892 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | NBSP - Mechanical Bar Screen General and OOS alarm came in. Checked site. Mech screen is showing local. Called Lauren S. who will reset alarm on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Adeela Khan signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052508 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Maximo down between 10:00 and 16:00. Attached is pictured of logbook entries | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: 18C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | RHAMF - Eric from NAC onsite to reset pump 1 & 2 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046184 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | QVSSSC - Channel Grinder Emergency Stop Alarm came in. Checked site. Channel Grinder was showing in Local/off. Called Chris C. who informed that the maintenance team will need to attend site. Chris informed that all channel grinder and hi/hihi inlet and level alarms can be disregarded for the time being until Maintenance can attend site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system]; alarms [control_system] | emergency [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | QVSSSC - Chris C. called back to inform that he is finished on site. Chris informed that if any channel grinder related alarms come in, they can be disregarded. Chris would like a call back if there are any issues with the pumps. | FLAG | stage2_low_confidence | 0.016879 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system]; alarms [control_system] | 0.016879 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDOC - Terry C. generator maintenance KBSP - Lauren S. testing plant 2 influent chamber flood alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | HLSSBR - Sewage pump 2 E-stop & speed OOR alarm. Followed up with Darren B, expected maintenance to be there. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | NMSSHS - Intermittent PAC communication fails come in. Called Artour L. who will take a look 11:42 - Artour L. called back to inform that he has spoken to the network team who has restarted the cell modem. A ticket is open with Bell due to ongoing issues | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0069669 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | QVSSSC - Chris C called to inform that any alarms related to the inlet channel grinder and inlet channel level hi/hihi are a disregard for the nigh.t Chris also stated that sewage pump 2 has bene having issues and he would like to be contacted if this pump faults and cannot be returned to service. | FLAG | stage2_low_confidence | 0.05751 | ML: above threshold (no LLM available) — 0.058 | fault [equipment_failure]; alarm [control_system]; alarms [control_system]; pump fault [infrastructure] | 0.05751 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 high level, common critical and UV system critical failure alarms. Trending shows that flow to the UV system recently started. Shift report states these alarms are a disregard in this scenario. Alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.027648 | ML: above threshold (no LLM available) — 0.028 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.027648 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | SUSP - SBR storm alarm. Checked site, SBR cycle operation mode showing as storm. EQ tank level is normal but filter feed pump speed and filter has increased. Will monitor. While watching site the SBR cycle operation mode returned to normal status. | FLAG | stage2_low_confidence | 0.016808 | ML: above threshold (no LLM available) — 0.017 | alarm [control_system] | 0.016808 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | SEBR - S2 humid chamber lolo level switch alarm. Disregard as per the shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059383 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | MTSS - communications loss to MTSS. Heavy thunderstorm impacting operations across the Region. No visual of site on SCADA. Checked the influent flow meter at the MTSP, trending shows no flow from the MTSS pumping station since communications lost. Contacted Arthur L to determine if communications can be revived and contacted Phil R to head to site to determine if operations have been impacted. Created CMU5#W11768975 for Arthur and CMU5#W11768982 for Phil R. MTSP - Grit system 1 and 2 uncommanded stop alarm, barscreen uncommanded stop alarm and dewatering press uncommanded stop alarm. Able to reset all alarms. #consult #CMU5 | FLAG | stage2_low_confidence | 0.039352 | ML: above threshold (no LLM available) — 0.039 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.039352 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | AUSS - Wet well hi level alarms. Placed Pump 5 with a manual setpoint of 60% | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0067186 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | KBSP - Christian from Ferguson Electric is finished on site. Christian informed that "Stella" generator failed and remained local/off. Both generators power different parts of the plant. Called Lauren S. to get more information as this is not noted in the shift report. Lauren will look into this. 16:57 - Drew from Ferguson Electric called back and requested to know if the generators were in auto as Dan H. contacted him. Informed that the "Stella" is Local/off and "Bertha" has a Remote-control status. Drew from Ferguson informed that Christian will head back to site 17:24 - After checking site, noticed that the "Stella" generator is now in auto. Lauren S. called back and informed that Christian from Ferguson is finished on site. Lauren also informed that one generator can power the whole plant but it is best to have both available. #CONSULT | FLAG | stage2_low_confidence | 0.088506 | ML: above threshold (no LLM available) — 0.089 | failed [equipment_failure] | 0.088506 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | HLSSBS - Gen still running, outage map has team responding to site. Informed Chris C of situation that gen may be running prolong for the night. Consult SUSP - UV critical, high level, alarm on startup, cleared right after NMSSBP - Wet well 1 & 2 hihi switch/level/overflow. See pump 2 & 4 man/off, Phil R on SCADA looking at site | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; scada [control_system]; alarm [control_system]; overflow [infrastructure] | overflow [critical]; scada [control_system]; alarm [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | AUSS/NMSSBP - Terry R. called back to inform that the pumps are back to normal operations as the high flows have subsided for the time being. Terry also informed that NMVCBP will be off for the night | FLAG | stage2_low_confidence | 0.012144 | ML: above threshold (no LLM available) — 0.012 |  | 0.012144 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | Contingency Log, March 31, 0400 to 0645, eLogs were down. Attached are the paper logs for that time stamp | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Adeela Khan Signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | KSSP - ZW2 Permeate Pump Speed Signal Error Alarm came in. Neil O. informed that Satnam M. is on site working on train 2 and all train 2 related alarms can be disregarded for the next 2 hours | FLAG | stage2_low_confidence | 0.0093643 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0093643 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | SHSP - Site hydro failure alarm. Checked site, generator is not running and ATS is pointing to utility hydro indicating a short power failure. Able to reset all alarms. Trending shows that the UV system did not deactivate or lose power. All duties appear normal on site. SHSSDK - Control panel power failure. Checked site, operations appear normal. No fault on pumps. Cleared alarms. | FLAG | stage2_low_confidence | 0.038229 | ML: above threshold (no LLM available) — 0.038 | fault [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.038229 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | SECC - Chris R. called to inform he is on site and will be running sump pumps. Directed to disregard all hi/lo level alarms until work is complete | FLAG | stage2_low_confidence | 0.01142 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.01142 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | MTSS - Communications loss alarm. Arthur L called to inform that he and the Network on call operator are unable to connect to the station. Arthur will attend site. KSSSQW - Wet well 1 hydrostatic level hihi alarm. Checked site, duty 1 and 2 active. Duty 3 not yet active. Heavy rainfall causing increased levels of flow. Will monitor site. | FLAG | stage2_low_confidence | 0.013541 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system] | 0.013541 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | AUSSSR - Noticed Line 3 Overtorque Alarm is outstanding. Only 1 line is available. Called Phil R. who directed to disregard alarm and he will attend site in the morning. Phil requested a call if line 3 goes down. MTSS - Phil R. informed that site is back to normal operations and all operators have left site. Phil would like a call back if any issues arise #CONSULT | FLAG | stage2_low_confidence | 0.010747 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010747 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | NMSSHS - Pump 1 VFD fault from this morning outstanding, placed pump 1 man/off. Pump 3 shows interlock and running in ultrasonic mode, appears partially on at 0% speed. Informed Phil R of site alarm NMMC - Manhole 2 level hihi, informed Phil R AUSS - Reached hihi level, informed Phil R as well Consult | FLAG | stage2_low_confidence | 0.0181 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.0181 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | MTSS - CMU5 created for communication loss at 02:26 for Christian S. W11769413 #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003327 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | NMSSHS - Pump 1 VFD Fault alarm came in. Checked site. Unable to clear. Called Chris R. who will attend site later today. Chris would like a call back if another pump goes down | FLAG | stage2_low_confidence | 0.017465 | ML: above threshold (no LLM available) — 0.017 | fault [equipment_failure]; alarm [control_system] | 0.017465 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | KBSP - Christian from Ferguson Electric is on site and will be completing a load bank test for the generator. | FLAG | stage2_low_confidence | 0.0074712 | ML: above threshold (no LLM available) — 0.007 |  | 0.0074712 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | HLSSBS - Gen shut off. Chris C called to inform to disregard current reading on we well overflow as small flow going though analyzer due to heavy rainfall and rising level from connecting lake in area | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure] | overflow [critical]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | NMSSHS, PAC Comm Fail Alarm, Terry R contacted Matt S for him to look into it | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | NMSSBP, Dan K notified ROC that they are overflowing into the EQ tank. MTSS, 2 Operators are still on site working on the issue | FLAG | stage2_low_confidence | 0.011003 | ML: above threshold (no LLM available) — 0.011 | overflow [critical]; overflow [infrastructure] | 0.011003 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | KBSP - UV Ch2 dosage lo, plant 2 influent flow hihi | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046636 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | AUSS - Found pump 1 in manual speed setpoint, placed back in auto. EGSSSC - Inlet channel level hihi, disregard as per area shift report KSSSQW - Wet well ultrasonic level hihi. Heavy rainfall in area. Will monitor site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.007026 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | NBSSJA - Lauren S finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056563 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | MTSS - Historian Heartbeat alarm came in. Called Artour L. who is looking into it | FLAG | stage2_low_confidence | 0.007767 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.007767 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | NBSSJA - Wet well 1 hydrostatic backup mode,, ultrasonic back up mode, wet well hihi level for both modes, LIT2 controlling on hydrostatic,. Informed Lauren S. During call wet well hihi level and overflow was triggered. Overflow is set to 7.64m while hydrostatic trend shows still below 3m and climbing at this time. Lauren S will head to site CMU = 11770082 AUSS - Activate duty 5 as seeing flows increase and will be triggered shortly KCSSKR - Discharge pressure hi, screen fail to stop. Able to clear screen alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; alarm [control_system]; overflow [infrastructure]; backup [infrastructure] | overflow [critical]; alarm [control_system]; overflow [infrastructure]; backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Carter D signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038155 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | BLSS - Screen diff lvl hi, monitored site and able to reset bar screen alarm. level came back within range | FLAG | stage2_low_confidence | 0.0088293 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0088293 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 14. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | HLSSBS - Generator running, fuel pump control panel power fail, PAC control panel power failure. PAC control alarm cleared. Monitoring site EGSSSC - Site hydro power failure, fuel pump control panel power fail, forcemain reverse flow hihi. Able to clear alarms. Pump 3 active | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; alarms [control_system] | failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | RHAMF - AMF fan 1 fail to start, odor control system emergency mode, system offline for odor control, unit 2 recirculation pump 1 overload, station power failure, control panel utility power failure. Able to reset alarms but fan 1 fail to start. Fan 2 running, disregard as per area shift report | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | emergency [critical]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SUSP- Basin 1 High Level. Decant phase just beginning and level will start lowering. Notified Tyson C. Can disregard. Requested a call if HiHi comes in. UV System Critical Failure, UV Ch.1,2 High Level. Alarms cleared upon acknowledgement. Known issue on SCADA Report. CONSULT | FLAG | stage2_low_confidence | 0.017704 | ML: above threshold (no LLM available) — 0.018 | failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.017704 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | QVSSSC - Darren B on site to complete work orders including a generator test run, JHSC checks and a dry well flood alarm test. Darren has requested that the associated alarms be disregarded. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | sso [critical]; flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NBSP - UV System Minor fault alarm. Checked site, UV 1A and 1B running. UV duty switching over from Bank 1A to 1B. Disregard alarm as per shift report. | FLAG | stage2_low_confidence | 0.015467 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; alarm [control_system] | 0.015467 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | AUSS - Generator 1, 2. 3 Not in Auto alarms came in. Checked site. Alarms cleared upon acknowledgement. Generators are not running and site is still connected to utility power | FLAG | stage2_low_confidence | 0.019048 | ML: above threshold (no LLM available) — 0.019 | not running [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019048 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SEOC4 - Terry R finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042554 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SEOC 9 - Shaft 9 O2 monitor OOR, HiHi alarms. Disregard as per SCADA review. NMSSBP - Kevin S still on site. Will call when leaving. 2 pumps remain in man/off for now. Stopped diverting to EQ. | FLAG | stage2_low_confidence | 0.0075069 | ML: above threshold (no LLM available) — 0.008 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0075069 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | NBSP, Aer Basin 2 Back DO lo/lolo, contacted Dan H as the original interim couldn't be found, suspected that it is expired, notified Dan H that the trends have been up and down but are now holding on the lower end, directed to place a second blower on to help with the DOs 19:14, Placed Blower 2 back to auto 20:22, Dan H is heading to site CMU5: W11714790 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056102 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | GRSSWA- Mechanical Screen Overload Alarm. Mechanical Screen Power Not Avail Alarm. Notified Mike B. Directed disregard alarm until morning. # Consult. | FLAG | stage2_low_confidence | 0.010082 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010082 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NBSP - Influent Flow HiHi and Influent High float alarms came in. After checking site, influent flow levels are slightly above hihi due to higher temperatures and melting snow. Will continue to monitor 19:02 - Mechanical Bar Screen Fail to Stop and OOS alarms came in. Checked site. Called Dan H. who directed to ack/reset. Unable to clear alarms. Dan H. will head to site. CMU5 Created W11714953 20:25 - Dan H. called back to inform that he was able to clear alarm and will not be heading to site. Dan informed that if the alarm comes in again to try and reset, but if unable to reset, Dan would like a call back #CONSULT #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | AUSSYS - Chris R on site and will be completing work orders including the dry well flood alarm test and hi/low temp alarm test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NBSP - Inlet channel level high float, influent flow hihi. Plant is currently experiencing high inlet flows from NBSSJA and heavy rain. Monitoring situation and levels SHSP - Aeriation blower fan 1 overload. Still running 6:37 - Informed Dan H. Expected levels to continue to climb due to weather. Will monitor Consult | FLAG | stage2_low_confidence | 0.0078194 | ML: above threshold (no LLM available) — 0.008 |  | 0.0078194 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | SHSSDK - Marcus R on site to complete a generator test and JHSC checks. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063209 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SUSP- UV Ch.2 Common Critical Alarm, UV Ch. 1,2, High Level. Alarms cleared upon acknowledging. Known issue on SCADA Report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0072086 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | AUSS - Pump 2 Disch header MV3 failed to close alarm. Cleared alarm/disregard as per shift report. | FLAG | stage2_low_confidence | 0.011984 | ML: above threshold (no LLM available) — 0.012 | failed [equipment_failure]; alarm [control_system] | 0.011984 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | KBSP- Marcus R and Harie R onsite changing UV bulbs. Disregard related alarms. | FLAG | stage2_low_confidence | 0.0088524 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0088524 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SUSP- UV system critical failure/ CH 1 high level/ common critical alarms. UV CH 2A is running. Flow to the UV system recently started. All alarms cleared when acknowledged. Disregard on shift report. | FLAG | stage2_low_confidence | 0.02217 | ML: above threshold (no LLM available) — 0.022 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.02217 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | LSSS - Spoke with Terry R and placed pump 1 and pump 5 in manual/off for the night. Four pumps available. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060276 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | KCSSKR - Marcos R onsite as well testing dry well flood, sump pit high level, diesel float, leak, and hi/low temp. Checking bar screen and headworks | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; leak [infrastructure] | flood [critical]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | AUSS- P5 MV# failed to open alarm came in. Reset alarm | FLAG | stage2_low_confidence | 0.0098542 | ML: above threshold (no LLM available) — 0.01 | failed [equipment_failure]; alarm [control_system] | 0.0098542 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KBSP - Sludge Tank Level HiHi alarm came in. Checked site. Scum Pumps are interlocked. Called Dan H. who directed to disregard alarm until tomorrow. SHSP - Spoke to Dan about the Sludge tank level hihi alarm. Dan directed to disregard alarm until tomorrow #CONSULT | FLAG | stage2_low_confidence | 0.008713 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.008713 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | KSSP - ZW4 Permeate Turbidity and Shutdown alarms. Disregard alarms until morning as directed by Tyson C in previous conversation. He will investigate in the morning. Emailed area. | FLAG | stage2_low_confidence | 0.010758 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010758 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | SUSP- UV System Critical Failure, UV CH. 1 Common Critical, UV Ch. 1 High Level. Alarms cleared upon acknowledging. Known issue on SCADA Report. | FLAG | stage2_low_confidence | 0.017216 | ML: above threshold (no LLM available) — 0.017 | failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.017216 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KSSP - Neil O tasting Admin Bld Sump HiHi level alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068932 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | Connor Smith signing in 7C Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041865 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | SUSP- Influent Flow HiHi Alarm. Quick Spike. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0067146 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | MTSP - Phil R on site to complete a generator test run. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058686 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | AUSSSR - Line 3 fail to close, overtorque alarm. Informed Kevin S, will head to site CMU = 11730458 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.005372 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | LSSS- Communication Failure Alarm. Alarm cleared. | FLAG | stage2_low_confidence | 0.012545 | ML: above threshold (no LLM available) — 0.013 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.012545 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | NMSSBP - Placed all pumps speed back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059776 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | KCSSKR - Marcus R running generator onsite, health & safety | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063265 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | SUSP- UV System Critical Failure, High Level. Alarms cleared. Known issue on SCADA Report. | FLAG | stage2_low_confidence | 0.017558 | ML: above threshold (no LLM available) — 0.018 | failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.017558 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | KSSP - Aeration tank 1 inlet/outlet DO Hi alarms. Will monitor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.006308 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046808 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SUSP - Tyson has completed work on the UV system ad is leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066425 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | KBSP, Scum Tank level hihi/Sludge tank hihi, Dan H called in, directed to disregard for the weekend | FLAG | stage2_low_confidence | 0.0076412 | ML: above threshold (no LLM available) — 0.008 |  | 0.0076412 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SUSSHS - Mike B on site to complete a generator test run. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059281 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | KCSSKR, Marcus R called requesting a CMU5. King received a odour complaint and got in contact with Marcus CMU5: W11711498 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046893 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | BLSS - Terry C onsite. Greasing off drive shaft | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006019 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | KSSP - UV channel 1 Bank 1A low UV intensity fault. Checked site, UV channel 1 is active. Trending shows the dosage is within normal range and the intensity does not show any abnormal dips. Alarm status changed to Normal during site inspection, alarm cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.027604 | ML: above threshold (no LLM available) — 0.028 | fault [equipment_failure]; alarm [control_system] | 0.027604 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: 16C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004454 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | NBSP - Young J on site to complete a generator test run. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059008 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | MTSS - Generator running status alarm. Checked site, operations appear normal. The generator is active but the ATS is pointing to town hydro indicating a short power failure. Will monitor site. MTSP - Compressor 1 motor overload alarm. Checked site, duty rotated to compressor 2. Will contact area operators on site. | FLAG | stage2_low_confidence | 0.041783 | ML: above threshold (no LLM available) — 0.042 | sso [critical]; failure [equipment_failure]; alarm [control_system] | 0.041783 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | AUSSYS - Terry R on site to complete pump tests. Terry will be allowing the wet well to fill above the normal range so he can complete all of the pump tests in sequence. Terry stated that the wet well hi/hihi alarms may be triggered but he is on site and watching. | FLAG | stage2_low_confidence | 0.019976 | ML: above threshold (no LLM available) — 0.02 | alarm [control_system]; alarms [control_system] | 0.019976 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | NMSSHS - PAC communication failure alarm. informed Ian W of outstanding alarm, will take a look | FLAG | stage2_low_confidence | 0.015628 | ML: above threshold (no LLM available) — 0.016 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.015628 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | GRSSWA- Wet Well H2S Sample No Flow Alarm. Disregard as per SCADA Report | FLAG | stage2_low_confidence | 0.008855 | ML: above threshold (no LLM available) — 0.009 | scada [control_system]; alarm [control_system]; h2s [safety] | 0.008855 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | SUSP - UV system critical failure, UV channel 1 common critical alarm and UV channel hi level alarm. Checked site, trending shows that flow through the UV system recently started. These alarms are disregards on the shift report when flow starts. Alarm status immediately changed to Normal and alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.034445 | ML: above threshold (no LLM available) — 0.034 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.034445 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | Connor Smith signing in -12 C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042384 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | KSSSQW, Pump 2 lo flow, rotated pump dudty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044851 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, 16D/Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041783 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | KSSSQW - Kevin K on site to complete some pump testing and has requested all alarms be disregarded on site. | FLAG | stage2_low_confidence | 0.009553 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.009553 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | KSSSQW, Pump 2 flow lolo//Pump 2 wire to water lolo/Efficiency lolo, contacted both Mike B/Chris C, both didn't answer, left a voice message, will call again in 10 minutes | FLAG | stage2_low_confidence | 0.0081249 | ML: above threshold (no LLM available) — 0.008 |  | 0.0081249 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | SUSP - UV Critical alarms came in. Plant just started and alarms cleared upon acknowledgment. Disregard as per shift report | FLAG | stage2_low_confidence | 0.010809 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010809 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | MTSP - Compressor 1 and 2 E.stop alarms came in. Checked site. Both are interlocked. Checked Barry M's MTSP Logbook post which states compressor 1 and 2 cleaning and inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; alarm [control_system]; alarms [control_system] | sso [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | KSSSQW - Neil O. called to inform he will be completing a backflush of pump 1 to increase the flow | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057989 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038155 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | KSSP - ZW2 shutdown alarm. Checked site, all other trains are either in production or going through an M-clean process leaving no filters on standby. Called Niel O to inform. | FLAG | stage2_low_confidence | 0.0090694 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0090694 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | SUSP- UV system critical failure/ CH 1 high level/ common critical alarms. UV CH2 is running. Alarms cleared when acknowledged, disregard on shift report. | FLAG | stage2_low_confidence | 0.017877 | ML: above threshold (no LLM available) — 0.018 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.017877 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | NMSSBP - Wet Well 1 and 2 Hi alarms. Alarms cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0059873 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | AUSSYS - Terry R finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056302 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | AUSSMP - Wet Well 1/2 High alarms. Placed Pump 2 man/currently running 60%-man speed , Pumps 5 and 6 manual speed - 60% to pump down wet well. | FLAG | stage2_low_confidence | 0.009167 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.009167 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather +7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SUSP - Woodriver Bend flow fault /OOS alarms. Two pumps running at SUSSWB. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046808 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather +7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | Harvest Hills Blvd and Old Field Cres, Kevin J from Paramedic Services called, informed the RO that a car took out a green box on the location provided, when checking all pipes, location shows a wastewater pumping station on site however no info about said pumping station. Took down Kevin J information to pass on to an operator. Contacted Kevin S and informed him of the situation, Kevin directed to contact ORO Marcus R as he isn't aware of any wastewater sites in that area. Marcus R is looking into it. Marcus R suggested calling Central Water Operator as it may be one of their sites, Will contact Central Operator Ben H just incase this is a water site 10:10, Talked with Ben H, its not a central water site. After digging further into all pipes and adjusting a few settings, the pumping station belongs to East Gwillimbury. Contacted EG After hours support operator Martin and passed on the information Kevin J: 2897163243 (YR Paramedic Services) Martin (East Gwillimbury After Hours Support) | FLAG | stage2_low_confidence | 0.11496 | ML: above threshold (no LLM available) — 0.115 |  | 0.11496 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | MTSP, Aeration Tank 2 DO lo alarm, Placed blower 2 man/on as per shift report 13:09, Placed blower 2 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0040044 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NMSSBP - Wet well 1 & 2 overflow, hihi level. Pumps 1 & 2 were left man/off. Followed up with Dan K. Leaving those pumps off to divert to EQ and lessen load to AUSS as high flows coming in | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure] | overflow [critical]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | HMSS - Security intrusion alarm on the dialer. No alarms on SCADA, trends normal. Marcus R on site. # Consult | FLAG | stage2_low_confidence | 0.0079863 | ML: above threshold (no LLM available) — 0.008 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0079863 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | MTSP, DO between the 2 aerations tanks is quite drastic. Tank 2 is alot higher than tank 1. contacted Kevin S about this observation as D2 wont be stopping for a bit, got no response, left a voice message, will call again in 15 minutes 19:38, Called 2 more times but no response, will call one more time at 20:00, will continue to monitor the DOs on site 19:55, directed to disregard at this time, If DOs remain the same in an hour, Kevin S will call back and will make some changes to the system 21:50, Kevin S called back, notified him that the DO range is still in the same spot, directed to place both blowers 2/3 man/off for the time being. If the DO lo comes in, directed to place the blowers back to auto and leave it for the night, will send email to operator 22:09, Placed blowers 2/3 back to auto as the DO dropped off consult | FLAG | stage2_low_confidence | 0.02313 | ML: above threshold (no LLM available) — 0.023 |  | 0.02313 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | EGSSSC - Inlet channel level HiHi, quick spike, alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071323 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | RHAMF1 - Unit 2 Recirculation Pumps 1 and 2 overload alarms came in. Low priority alarms. Shift report directs to make sure a fan is running. Both fans are still running Unit 1 Recirc Pump 1 is still running | FLAG | stage2_low_confidence | 0.012344 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012344 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | NBSS - Young J testing eyewash alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063496 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | GRSSWA - Wet well 1 and 2 ultrasonic and hydrostatic levels Hi alarms. All 3 pumps running on Hydrostatic mode. Wet well level slowly increasing. Notified Mike B. # Consult 05:59 Wet well 1/2 HiHi switch alarms. Notified Mike B. He will check SCADA. # Consult | FLAG | stage2_low_confidence | 0.010587 | ML: above threshold (no LLM available) — 0.011 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.010587 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | QVSSSC - Generator running status alarm. Checked site, generator is running but ATS is pointing to town hydro indicating a power blip scenario. No impact to operations, will monitor site. | FLAG | stage2_low_confidence | 0.012669 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.012669 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | SUSP - UV channel 2 high level and common critical alarm, UV channel 1 high level and common critical alarm and UV system critical failure alarm. Checked site, UV channel 1 is active. Trending shows that flow to the UV system recently started. Shift report states these alarms are triggered when flow starts and can be disregarded in these circumstances. Cleared alarms. | FLAG | stage2_low_confidence | 0.042128 | ML: above threshold (no LLM available) — 0.042 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.042128 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | KSSP - UV channel 2 Bank 2 A lamp fail and adjacent lamp fail alarms. UV channel 2 is active. Alarm disregard as per shift report. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | BLSS - Marcus R testing temperature and Drywell flood alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | LSSS - Pump 1 Motor/Bearing Hi Temp and Hi Temp Trip alarms. Phil R on site. | FLAG | stage2_low_confidence | 0.01038 | ML: above threshold (no LLM available) — 0.01 | trip [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.01038 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SHSSDK - Generator fault alarm. Lance J on site, contractor changing the Hydro meter. Lance J will clear alarm. | FLAG | stage2_low_confidence | 0.015811 | ML: above threshold (no LLM available) — 0.016 | fault [equipment_failure]; alarm [control_system] | 0.015811 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | SEOC4 - Shaft 4 O2 Monitor 2 OOR and HiHi alarms came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0070886 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | EGSSSSC- Inlet Channel Level HiHi Alarm. Alarm cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068557 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | EGSSSC- Satnam M onsite for soft start work on pump 2 and placed in Local. Pump 3 is available in duty 1. 11:35- Satnam M finished onsite. Pump 2 is back in auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055048 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | SUSP - Filter hi level alarm. Checked site, trending shows that the filter flow rate is higher than normal due to to the EQ tank pump speed being higher than normal. Called Tyson C who will relay the message to his team. | FLAG | stage2_low_confidence | 0.014942 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system] | 0.014942 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | AUSS, Generator 1 Warning Alarm/engine battery low voltage alarm/Gen1Engine (Warning) alarm Shift report doesn't mention generator alarms, notified Kevin S, he is looking into the issue. Alarm was able to be cleared however it did come back in a second time. Kevin S is heading to site 16:04, Kevin S called back, has asked for Electrical on call to give him a call as he believes one of the batteries may be burning. Contacted Dan B, he will give Kevin S a call 16:10, Dan B is heading to site CMU5: W11733335 (Kevin S) CMU5: W11733345 (Dan B) | FLAG | stage2_low_confidence | 0.012224 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012224 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical alarm, UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 2 is active. Trending shows that flow through the UV channel recently started. Shift report states these alarms trigger when flow starts and are a disregard. Cleared alarms. | FLAG | stage2_low_confidence | 0.031893 | ML: above threshold (no LLM available) — 0.032 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.031893 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | LSSS - Phil R on site to complete pump valve exercising. Phil stated all associated alarms can be disregarded until the work is done. | FLAG | stage2_low_confidence | 0.017729 | ML: above threshold (no LLM available) — 0.018 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.017729 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | NMSSHS, Kevin S on site, doing wet well testing, testing dry well flood/Auto dialer alarms and testing temp alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | NBSP - UV System Minor Fault alarm came in. Checked site. Bank 1B is running. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.01262 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.01262 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | AUSS - Wet wells Hi and HiHi alarms in and out. 3 pumps constantly running, 4th pump on and off. 1 extra pump available. High flows. Monitoring. | FLAG | stage2_low_confidence | 0.0092164 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0092164 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | NBSSJA - Young J informed contractors onsite and they are doing sewer cleaning, running wells on low level while cleaning in progress | FLAG | stage2_low_confidence | 0.0089176 | ML: above threshold (no LLM available) — 0.009 |  | 0.0089176 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | LSSS - Emily B from EME on site to take samples. Emily requested that pump 6 be activated to draw a sample. Made the necessary pump duty change. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067454 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | NMSSHS - Kevin S on site to complete a generator test run. Associated generator alarms will be triggered. | FLAG | stage2_low_confidence | 0.015419 | ML: above threshold (no LLM available) — 0.015 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.015419 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical and high level alarm and UV system critical alarm. Checked site, UV flow recently started. Disregard as per the shift report. Alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.010027 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010027 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 0. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | AUSS - Dan B & Kevin S finished at site, replaced 2 batteries for gen 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051335 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | SUSP- UV system critical failure/ CH 1+2 high level/ common critical alarms. Flow to the UV system recently started. All alarms cleared when acknowledged. Disregard on shift report. | FLAG | stage2_low_confidence | 0.020233 | ML: above threshold (no LLM available) — 0.02 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.020233 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | NBSSJA - Young J onsite testing generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058183 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | NBSP- Inlet Channel High Float. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066202 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | SEOC Shaft 6/7 - Terry R. is on site and will be running the diesel generator 11:26 - Terry R. is finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034126 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | KSSP - Membrane Operating Area MUA-10 Temp Switch Lo alarm came in. Disregarded as per shift report KSSP- Makeup Air Unit 5 Temp Switch Lo alarm came in. Disregarded as per shift report KSSP - Alum Chem Room MUA - 11 Differential Pressure Switch Hi alarm came in. Will email Cam B. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0072099 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | SUSP - Influent flow hihi alarm. Checked site, multiple sewage pump[ing stations pushing flow to the headworks resulting in high flows. Flows dropped while monitoring. Cleared alarms. | FLAG | stage2_low_confidence | 0.012021 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012021 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: 2C and rain. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045651 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | Adam Button signing in 0C Raining | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041938 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | NMSSHS - Aaron M. from the Network team is on site to check the cell modem due to the intermittent PAC communications that have been coming in. Aaron informed that communication will be lost for 5 mins but will repopulate shortly. Aaron informed that this should not affect operations. Confirmed with Kevin S. 14:31 - Aaron called back to inform he is finished on site | FLAG | stage2_low_confidence | 0.011067 | ML: above threshold (no LLM available) — 0.011 |  | 0.011067 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | AUSS, Rotated pump duty for Terry C, Terry C on site working on the pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063923 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | BLSS - Marcus R testing wet well levels and sump pit alarms. | FLAG | stage2_low_confidence | 0.0081941 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0081941 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | MTSP- Terry R heading to site to drain clarifier 1. Directed to place RAS P3 in man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054644 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | SUSP - UV system critical failure alarm, UV channel 1 high level alar and UV Channel 1 common critical alarm. Checked site, UV system is active. Trending shows that flow to the UV system recently started. Shift report states these alarms will trigger when flow activates and can be disregarded under these circumstances. Alarm status changed to Normal, alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.045351 | ML: above threshold (no LLM available) — 0.045 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.045351 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | Ethan U signing in Weather -0. Snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035846 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | QVSSSC- Sewage pump 2 VFD fault alarm, notified Mike B. He will check SCADA. # Consult 15:30 Mike B will attend site. # CMU5 W11714918 | FLAG | stage2_low_confidence | 0.010265 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.010265 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | KSSP - ZW2 MDF Flow TMP Delta Low and High Alarms, cleared when acknowledged. ZW2 in backwash. | FLAG | stage2_low_confidence | 0.0072541 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0072541 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NBSP - Inlet channel High Float alarm and Mech Bar screen OOS , failed to stop alarms. Was able to clear all alarms. Influent flow HiHi alarm outstanding. High flows. Monitoring. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | AUSS - 4 pumps running constantly, twin forcemain is active, wet well level increasing. Notified Terry R. Requested Run Pump 2(duty 5) in manual. Placed pump 2 in man/on. Pump not starting. Left man/off. Placed Pump 5 manual (currently running) increased speed to 60%. Terry R will check SCADA. # Consult Placed Pump 6 manual 40% speed and decreased Pump 5 speed from 60 to 40%. Placed Pump 1 man/on 40% speed. | FLAG | stage2_low_confidence | 0.028683 | ML: above threshold (no LLM available) — 0.029 | scada [control_system]; pump not starting [infrastructure] | 0.028683 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | AUSS - Increased Pump 6 speed from 40 to 60%. Requested NMSSBP Pumps 2,3,4 man/stop and send flow to EQ. Terry R not able to login to SCADA. He will contact Kyle C and call back. | FLAG | stage2_low_confidence | 0.010435 | ML: above threshold (no LLM available) — 0.01 | scada [control_system] | 0.010435 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical/channel 1 high level alarms and UV system critical failure alarm. UV channel 1 is active, flow through the UV channel recently started. Disregard alarms as per shift report. Alarms cleared when acknowledged. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; alarms [control_system] | failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | SUSP - UV Ch. 1 common critical, high level, critical failure. Alarm cleared upon acknowledgment as UV alarm came in during startup. | FLAG | stage2_low_confidence | 0.014046 | ML: above threshold (no LLM available) — 0.014 | failure [equipment_failure]; alarm [control_system] | 0.014046 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | LSSS - Wet well screen 1 differential level hihi, monitored level and saw it come down | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054951 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in,weather -4C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, 1D/Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041599 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | KSSP - UV Ch.1 Bank 1A low UV intensity. Checked site, UV1 running showing intensity | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054213 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | Carter Dunn Signing In. -3D/Snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042339 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | LSSS - Terry R onsite to reset fault on pump 1. Running pump 1 duty 1 to help break down build up. Disregard pump 1 fault when it comes it as triggered due to bearing temperrature. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | NBSSJA- Young J testing hi/lo temp/drywell flood and sump hi alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003864 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | LSSS - Generator 3 warning and DGC not in auto alarms. Notified Phil R, he will investigate. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0067253 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | KBSP - Historian Heartbeat and PAC Communication Failure alarm came in. Checked site. Flatlining. Called Yash S. who will take a look. CMU5 created W11697421 02:55 - Yash S. called back to inform that he is unable to access and redirect the site to be able to trend again. Yash explained that there is a power issue with the sludge building and requested to give Young J. a call. 02:58 - Called Young J. who will look at SCADA 03:01 - Yash S. called back and informed he will speak to Network On Call 03:05 - Young J. called back informed that he will attend site (CMU5 Created W11697431) and requested for Yash S. to meet him there. 03:08 - Called Yash S. who is headed to site. 04:28 - Yash S. called to inform that he and Young J. are both finished on site. Yash informed that the issue was a blown fuse. All alarms have been cleared, and site is now back to normal operations #CONSULT #CMU5 | FLAG | stage2_low_confidence | 0.032972 | ML: above threshold (no LLM available) — 0.033 | failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; communication failure [control_system] | 0.032972 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | EGSSSC - River Bridge Heat Trace Alarm came in. Low Priority alarm. Checked site. Trending is okay. Will send an email to On call North WW operator. | FLAG | stage2_low_confidence | 0.010602 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system] | 0.010602 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | KSSP - UV Ch1 bank 1A Low UV intensity fault alarm, UV 1 running, alarm cleared upon acknowledgement. | FLAG | stage2_low_confidence | 0.012275 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system] | 0.012275 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | SEOC OCF - FAN1 and FAN2 uncommanded stop alarms. ACK/reset alarms. FAN1 and FAN2 restarted. Will monitor. | FLAG | stage2_low_confidence | 0.0076369 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0076369 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | KSSP - Garrick remove batteries for generator temporarily for work | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065657 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | LSSS - Pump 1 fault alarm. Checked site, pump duty rotated to pump 5. Phil R logged into the facility logbook to complete work orders. Will monitor site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; work order [maintenance_action]; alarm [control_system] | fault [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | KSSP - UV CH.1 Bank 1A Low UV Intensity Fault alarm. UV CH1 is running. Notified Cam B. He directed disregard alarm until tomorrow. He will inform Kevin K to create w/o with instrumentation. # Consult. | FLAG | stage2_low_confidence | 0.013181 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.013181 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | SUSP - Eric S. informed that he is finished working on the lagoon flowmeter and no alarms remain | FLAG | stage2_low_confidence | 0.0092631 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0092631 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | PVSS- P1 in a ultrasonic mode/ discharge flow hi alarms came in. Lauren S on site performing valve exercises and had P2/3 in man/off. Lauren S not sure why P1 went into ultrasonic mode but will investigate on site | FLAG | stage2_low_confidence | 0.011843 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.011843 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | KBSP - Harie R. called to inform that he will be conducting an inspection to the sump pits in both the tertiary and headworks building. Harie informed that he will be tipping floats making sure that pumps are working | FLAG | stage2_low_confidence | 0.013165 | ML: above threshold (no LLM available) — 0.013 |  | 0.013165 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | YDSS+YNSS normal Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046291 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS+ YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048651 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal NBSP, Placed BLower 2 back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031547 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | SUSP- SBR storm alarm came in notified Mike B. Will take a look on SCADA 12:00-SUSP- Mike B notified ROC to disregard SBR storm alarm but call for super storm alarm #consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0051157 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS+YNSS normal AUSS- wet well 1/2 Lit 1/2 hi alarms. D4 active will continue to monitor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0054921 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | GRSSWA- P1/3 in ultrasonic mode. Wet well slowly pumping down. Will continue to monitor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054691 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | LSSS - Surge tank 1 level High alarm. Duty just reassigned and pumps started. Quick spike. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066044 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | SUSP- UV system critical failure/ CH 1+2 high level/ common critical alarms. Flow to the UV system recently started. All alarms cleared when acknowledged. Disregard on shift report. | FLAG | stage2_low_confidence | 0.020233 | ML: above threshold (no LLM available) — 0.02 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.020233 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | NMSSBP- Kevin S called , Locking out Pump 4. Local/off until farther notice. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052287 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | GRSSWA - Mechanical Screen Power Not Available and Overload alarms came in. Mechanical Screen 1 is stopped and in local. Called Mike B. who will take a look on SCADA 20:57 - Mike B. called back to inform that he is headed to site. CMU5 Created W11719346 #CONSULT #CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0069496 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | NBSP - UV Minor Fault alarm. Checked site, UV bank 1B is active. Trending shows the duty recently rotated. Shift report states this alarm is a disregard as long as one UV bank is active. | FLAG | stage2_low_confidence | 0.018274 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.018274 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | MTSP - Clarifier 1 no RAS Pump running alarm. Checked site, clarifier 1 showing as manual/off. Shift report states that clarifier 1 is OOS so RAS pump 3 is also manual/off. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | KBSP - PAC communication failure, historian heartbeat. Informed Yash S of outstanding alarms PAC4 to PAC3 comm fail. PAC3 comm fail | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system] | failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system] |  | 1 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | GRSSWA - Chris C finished at site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056301 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | Christian Van Beek signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054296 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | YDOC - Terry R onsite running generator rotating fan 9:15 - Finished at site SEOC - Terry R continuing work with generator and fan rotation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004063 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | KSSP- MUA2 Low Temp alarm. Disregard as per SCADA report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0052483 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | GRSSWA- Mechanical Screen Overload Alarm. Mechanical Screen Power Not Avail Alarm. Notified Chris C. He will look into it. | FLAG | stage2_low_confidence | 0.0088405 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0088405 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | KSSP - Neil O onsit. Testing chem flood alarm, & membrane sump pit | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | AUSS - Wet well 1 level High alarm. Man/start Pump 6 to pump down wet well / help with high flows. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064754 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | EGSSSC- Inlet channel hihi alarm came in. High flows and D1 active pumping both wet well and inlet channel down. Cleared alarm when level dropped below setpoint | FLAG | stage2_low_confidence | 0.0081792 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081792 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS+YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | MTSS, Philip R on site, doing a generator test | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056074 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS+YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | MTSP - Clarifier 2 Failed to Start and Fault alarms came in. Checked site. Called Phil R. who is headed to site. CMU5 Created W11697603 23:27 - Phil called back to inform that he is finished on site as he was able to get clarifier 2 up and running again. Phil requested a call back if that fault comes back in #CONSULT #CMU5 | FLAG | stage2_low_confidence | 0.01413 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.01413 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SUSSWB - Ventilation H2D high/fault, hihi. Disregard wetwell gas alarms afterhours as per shift report. Able to clear alarms | FLAG | stage2_low_confidence | 0.021123 | ML: above threshold (no LLM available) — 0.021 | fault [equipment_failure]; alarm [control_system]; alarms [control_system]; gas alarm [safety] | 0.021123 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | EGSSSC - Inlet channel Level HiHi alarms at duty start up, alarms cleared shortly after. | FLAG | stage2_low_confidence | 0.0092918 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0092918 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NMSSBP, AUSSMP, NMSSHS - Kevin S called. All pumps back to auto, auto speed. NMEQBP - Marcos T man/started Dewatering pump 1 to pump down EQ tank. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060535 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | KSSP - ZW4 Permeate Turbidity HiHi / Shutdown alarms. Notified Tyson C. He will check SCADA. # Consult QVSSSC - Sewage pump 2 VFD Fault alarm. Pump 1 running ok. Disregard until tomorrow as per Tyson C. 23:03 QVSSSC - Tyson C checked SCADA, He will attend site to reset pump. # CMU5 W11726656 | FLAG | stage2_low_confidence | 0.014895 | ML: above threshold (no LLM available) — 0.015 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.014895 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | QVSSSC - Pump 2 back to auto. Tyson C leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046588 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | AUSS - Placed P2 back to auto/ auto speed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044676 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NMSSBP - Wet well level HiHi alarm. EGSSSC and NMVCBP duty deactivated. NMSSBP HiHi level alarms cleared. | FLAG | stage2_low_confidence | 0.0086656 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0086656 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NMSSBP - Placed Pump 3 back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043514 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | AUSS - Terry R. called back to inform that he spoke with Kyle C. and determined that there was an issue with the programming which was able to be resolved. Terry informed that pump 2 is up and running now. Terry also informed that all pumps can go back to auto at both AUSS and NMSSBP. Terry would like a call back if any other issues arise AUSS and NMSSBP - All pumps have been placed back to auto | FLAG | stage2_low_confidence | 0.016508 | ML: above threshold (no LLM available) — 0.017 |  | 0.016508 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | KSSP - ZW1 MDF Flow Incycle TMP Low alarm came in. Alarm cleared upon acknowledgement | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059704 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | AUSS - Wet Well 1/2 High level alarms. Placed Pump 2(currently running) to 60% manual speed. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0071844 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SEOC4 - Shaft 4 O2 Mon HiHi alarm, disregard as per SCADA review. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0054878 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NMSSBP - Wet well Level Hi alarms. Duty 3 about to start. AUSSMP - All pumps running. Called Kevin S to stop dewatering pump at EQ tank. Will empty EQ tank later, when flows slow down. # Consult | FLAG | stage2_low_confidence | 0.0081294 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0081294 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather +3C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, -2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | BLSS- Screen 1 Emergency Stop. Christian S onsite for PMs. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | LSSS- Ubah (Student) onsite and requested pump 6 in duty 1 for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051286 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SHSP - Lance J on site to complete work orders and will be testing e-stop alarms in the headworks building. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; alarm [control_system]; alarms [control_system] | work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KSSSQW - Chris C leaving site. All pumps now available. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062361 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | HLSSBS - Darren B onsite testing drywell flood autodialer, and running generator | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SHSP - Sludge holding tank level hihi alarm. Checked site, sludge holding tank level has been steady since early this morning. Alarm triggered due a small increase in level registered by SCADA which could be due to the sludge blowers "lifting" the surface level. Will monitor site, if the level shows signs of increasing will call OCO. | FLAG | stage2_low_confidence | 0.025511 | ML: above threshold (no LLM available) — 0.026 | scada [control_system]; alarm [control_system] | 0.025511 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SUSSWB - Pump fail alarm on the dialer. Checked SCADA, quick dip in flow trend/recovered right away. Pump 2 is running. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system] | scada [control_system]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | QVSSSC - Test alarm on the dialer. Checked site, duty just deactivated. All trends normal. | FLAG | stage2_low_confidence | 0.0080302 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080302 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | NBSP - UV System Minor fault alarm. Checked site, UV 1A running. Disregard alarm as per shift report. | FLAG | stage2_low_confidence | 0.012162 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system] | 0.012162 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | SUSP- Influent free Cl2 hihi alarm came in. Flow returned to normal reset alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055391 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | SUSSWB - Mike B onsite running diesel | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057294 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | KSSP - ZW5 TMP control low alarm. Disregard alarm as per the shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057001 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SEOC4- Terry R onsite to run diesel generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045246 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | MTSP - Final Effluent Flow LoLo alarm came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0076256 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076256 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | KSSP - Niel O on site to complete maintenance on the Alum system and directed that all associated alarms can be disregarded. | FLAG | stage2_low_confidence | 0.016964 | ML: above threshold (no LLM available) — 0.017 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.016964 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SHSP - RAS pump 2 speed deviation alarm. Checked site, RAS pump is still pushing floe. Reset the alarm once and it trigged again. Called Gavin W who will check the pump. | FLAG | stage2_low_confidence | 0.0090097 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0090097 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -11C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044737 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | NBSP- Inlet Channel High Float. Alarm cleared. Mechanical Bar Screen Fail to Stop. Alarm Cleared | FLAG | stage2_low_confidence | 0.0080797 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080797 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | NBSP- Inlet Channel High Float. Alarm cleared. Mechanical Bar Screen Fail to Stop. Alarm Cleared | FLAG | stage2_low_confidence | 0.0080797 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080797 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | MTSS - Communication Loss to MTSS alarm. Notified Kyle C. He will investigate. # CMU5 W11722573 05:05 Kyle C called. Communication recovered. Trends OK. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058456 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | NBSP - Harrie R onsite working on scum pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059166 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | KSSSQW - Wet well Ultrasonic and Hydrostatic levels Hi Hi alarms. Duty 3 Just activated. Will monitor. | FLAG | stage2_low_confidence | 0.0074837 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0074837 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NBSP- Inlet Channel High Float. Alarm cleared. Mechanical Bar Screen Fail to Stop. Alarm Cleared. | FLAG | stage2_low_confidence | 0.0081163 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081163 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | NBSSJA - Young J called, contractors cleaning Wet well on site. He disabled LoLo level lockout alarm. | FLAG | stage2_low_confidence | 0.00799 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.00799 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046808 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | EGSSSC- Inlet Channel Level HiHi Alarm. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068551 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | BLSS- Marcus R onsite testing eye wash alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065775 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SUSP - UV Ch. 1 high level, common critical, UV system major fault, multiple lamp fault Ch. 2, 2A major fault. Informed Tyson C onsite, will look into issue | FLAG | stage2_low_confidence | 0.012056 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure] | 0.012056 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | EGSSSC - Sewage pump 2 bypass alarm. Checked site, no obvious issues on site. Alarm was cleared remotely. AUSS - Pump 1 discharge MV2 Fault alarm. Checked site, duty 1 has rotated to pump 5 which is operating normally. Able to clear alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; fault [equipment_failure]; alarm [control_system] | bypass [critical]; fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | SHSP - Marcus R on site to complete a generator test run and JHSC checks. KBSP - Harie R on site to complete an inspection for the RSHW blowers. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062063 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SUSP- UV System Critical Failure. UV Ch. 1,2 high level. Alarms cleared after acknowledging. Known issue on SCADA Report. | FLAG | stage2_low_confidence | 0.015409 | ML: above threshold (no LLM available) — 0.015 | failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.015409 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | QVSSSC- Chris C and Darren B on site to test wetwell floats | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059745 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, -2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | Ethan U signing in Weather -7. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034483 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | KSSSQW- Chris C on site to test hi wet well alarms | FLAG | stage2_low_confidence | 0.0073404 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system]; alarms [control_system] | 0.0073404 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | NBSP, As per Dan H direction, if the back DO drops below 1.25PPM, place on a second blower. Placed Blower 2 Man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062298 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NMSSBP - Placed Pump 3 man/on to pump down wet well before EGSSSC duty will activate. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | SUSP - UV System Critical Failure , Ch 1 High Level, Ch.2 Common critical alarms came in. Checked site. Plant recently activated. Disregard as per shift report. Cleared upon acknowledgement. | FLAG | stage2_low_confidence | 0.020986 | ML: above threshold (no LLM available) — 0.021 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.020986 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 and 2 high level alarm, UV channel 1 and 2 common critical alarm and UV system critical alarm. Checked site, UV channel 2 is active. Trending shows that flow through the UV channel recently started. Shift report states that these alarms are disregards following flow start. Alarm status changed to Normal and alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.021095 | ML: above threshold (no LLM available) — 0.021 | alarm [control_system]; alarms [control_system] | 0.021095 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | AUSS - Terry C onsite requesting to have pump 2 run in duty. Rotated pump 2 to duty 1 KBSP - Harie R onsite inspecting clarifier, may alternate duty on clarifiers | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0065221 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | KSSP - Cam B onsite for monthly disel run | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058547 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | KSSP - Train ZW2,3,4,5 MDF flow inclycle tmp low, transmembrane pressure lo, temp delta high . Informed Mike B. Will let the morning team now, issue due to weather and hi flow Consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071539 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NMSSBP - Kevin S leaving site, 2 pumps running and 2 pumps man/off. Kevin S and Marcos T (back-up) will check system later tonight to return pumps to auto, NMEQBP -Kevin S requested to leave / not to run dewatering pumps until tomorrow morning. | FLAG | stage2_low_confidence | 0.011379 | ML: above threshold (no LLM available) — 0.011 |  | 0.011379 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical and high level alarm and UV system critical alarm. Checked site, UV flow recently started. Disregard as per the shift report. Alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.010027 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010027 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | BLSS - Marcus R testing generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056165 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | KSSP - RAS combined no flow alarm. Checked site, all RAS pumps are manual/off and the WAS pumps are running, indicating that operators are wasting. | FLAG | stage2_low_confidence | 0.010219 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.010219 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | AUSS - Chris R on site to complete a generator test run and the JHSC checks. Chris R stated that maintenance is on site to complete work related to pump 1 and 4 and that these alarms can be disregarded as both pumps are OOS. 09:34 - AUSS - Chris R will not be running the generator. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: 0C and Sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044345 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | SUSP - UV System Critical Failure Alarm, UV Ch.1 High Level and Common Critical alarms came in. Alarms value went normal right away. Checked site. Plant recently started up. Disregard as per shift report | FLAG | stage2_low_confidence | 0.019357 | ML: above threshold (no LLM available) — 0.019 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019357 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in,weather +5C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -3C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SUSSWB - Ventilation H2S OOR alarm. As per shift report disregard alarm after hours. Will notify OP in the morning. 07:20 Value back to normal. Alarm cleared. | FLAG | stage2_low_confidence | 0.0088841 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; h2s [safety] | 0.0088841 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | NBSP - Influent flow hihi and inlet channel high float alarm. Checked site, the Nobleton pumping station currently has two pumps active which is resulting in high influent flows at NBSP. Will monitor situation. | FLAG | stage2_low_confidence | 0.014164 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system] | 0.014164 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | Bayview Steels OCF - Phil R on site to complete maintenance on the mist eliminator filters. Phil will be stopping the fans to complete the work. Will see associated alarm. | FLAG | stage2_low_confidence | 0.018261 | ML: above threshold (no LLM available) — 0.018 | sso [critical]; alarm [control_system] | 0.018261 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KSSSQW - Chris C on site to complete work orders including a dry well flood alarm test, hi/low temperature alarm test and a dialer alarm test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KSSSQW - Chris C heading offsite and will return later. Kevin K is remotely monitoring and has placed three pumps in manual mode to increase the wet well level to increase head pressure to try clear the clogged pumps. | FLAG | stage2_low_confidence | 0.020866 | ML: above threshold (no LLM available) — 0.021 | clog [infrastructure]; clogged [infrastructure] | 0.020866 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | JDSS - Chris C. finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005244 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SHSP - Gavin W on site to complete work on the RAS/WAS pumps. May see associated alarms. | FLAG | stage2_low_confidence | 0.014531 | ML: above threshold (no LLM available) — 0.015 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.014531 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SUSP - UV Ch. 2 Bank 2A Lamp fail alarm came in. Disregarded as per shift report YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0044003 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | KSSP - Generator local mode alarm and Generator fault alarm. Called Niel O who stated that contractors and Brent St C are on site working on the generator. While monitoring SCADA the generator returned to auto mode. 13:39 - KSSP - Brent St C called to inform he was working on the generator, swapping batteries with the contractor. | FLAG | stage2_low_confidence | 0.019371 | ML: above threshold (no LLM available) — 0.019 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.019371 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | HLSSBS- Forcemain pressure hi alarm came in able to reset alarm as trends recovered | FLAG | stage2_low_confidence | 0.0077902 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077902 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NMSSBP - Wet Well 1 and 2 Overflow alarms came in. Placed pumps back to auto and levels went down and alarm cleared. 18:44 - Due to higher levels at AUSS, placed pumps 2-4 at NMSSBP back to man/off. Will continue to monitor | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | SHSP - Lance J on site to test three high level float alarms. NBSP - Marcus R on site to complete maintenance of the head works machines including bar screens, and vortex systems. | FLAG | stage2_low_confidence | 0.009327 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.009327 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | KSSP - Chase J testing headworks alarm | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063892 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SUSP - UV Ch.1 Bank 1A intensity fault. Intensity reading 47.91 and bank 1B UV running as well with strong intensity reading | FLAG | stage2_low_confidence | 0.010364 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.010364 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | SEOC4- Shaft 4 O2 Mon 2 LoLo Alarm. Disregard as per SCADA Report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0054846 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | NBSP - Vortex #1 Water Scour uncommanded close alarm came in. Ack/reset as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0061465 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | SHSP- Power loss on site. Diesel generator running and aeration blower 2 fan overload still running. Notified Dan H. directed to rotate Fan 2 out of D1. Rotated duty but fan would not switch to D5 (OOS). Placed Blower 2 in man/off. All other fans are available if called upon #consult | FLAG | stage2_low_confidence | 0.022831 | ML: above threshold (no LLM available) — 0.023 | oos [equipment_failure] | 0.022831 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | Connor Smith signing in -1C windy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041936 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | BLSS - Marcus R and Lauren S on site to complete work on the barscreen system and test the high wet well level alarm. | FLAG | stage2_low_confidence | 0.0087622 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0087622 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KSSSQW - Wet well Hi alarms, Pump 3 efficiency low, wire to water alarms. Pump running on duty 2 with O flow, Rotated Duty, assigned Pump 2 to Duty 2 and placed P3 man/off. Notified | FLAG | stage2_low_confidence | 0.010631 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010631 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | JDSS - Kevin K finished work and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059661 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | SUSP- Bar Screen Hi Level Alarm. Alarm cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066613 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | GRSSWA- Wetwell 1 Ultrasonic lolo. Not the controlling LIT. Check trends looks like it has dropped out in the past. Will monitor and reset if recovers or email North west wastewater team about outstanding issue | FLAG | stage2_low_confidence | 0.0097381 | ML: above threshold (no LLM available) — 0.01 |  | 0.0097381 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | SUSP- Influent hihi alarm came in as both SUSSHS and SUSSWB were pumping to headworks. Trends recovered and alarm cleared | FLAG | stage2_low_confidence | 0.0093082 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0093082 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | KSSP- Sodium bisulphate containment spill alarm came in. Notified Mike B. Will check SCADA MTSP- Both UV banks running 1a turning on and off. No alarm associated with issue. Notified Terry R to inquire if this was expected. Terry R. it was caused by both high flows and clarifier 1 draining. Will look on SCADA 12:18- KSSP- Mike B. Directed to disregard sodium bisulphate spill alarm #consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; sso [critical]; scada [control_system]; alarm [control_system]; containment [safety] | spill [critical]; sso [critical]; scada [control_system]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | QVSSSC, Diesel Containment Flood Alarm, notified Darren B, directed to disregard at this time, he will be heading to site sometime today | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; containment [safety] | flood [critical]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | SEOC - OCF Fan Room 1 O2 Low alarm. Disregard as per shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055172 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: 10C and sunny | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004454 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | HMSS - Lauren S on site to complete work orders including a generator test and a high level forcemain chamber alarm test. SUSP - UV system critical failure, UV channel 1 level high and UV channel 1 common critical alarm. Checked site, trending shows that UV channel flow recently started. Shift report states that these alarms will trigger when the plant activates and flow begins. All alarm statuses changed to "Normal". Alarms cleared on acknowledgement. RHAMF - Eric S from NAC on site to reset system alarms from last night. Cleared alarms, Eric assured that the system is now operating correctly. | FLAG | stage2_low_confidence | 0.098105 | ML: above threshold (no LLM available) — 0.098 | failure [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.098105 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal MTSP - Final Effluent LoLo alarm came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0053139 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | MAPSN1 SCADA Server Reset, Kingsley M called, will be resetting the server at 09:30 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system] | 0.0057681 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | EGSSSC - Darren B onsite running generator and health and safety alarms | FLAG | stage2_low_confidence | 0.0085593 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0085593 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | MTSP - Clarifier 1 no RAS pump running. Will be off for the weekend and drained Monday | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055396 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | KSSP - Niel O called to inform that they will be completing work on the UV system. Niel directed to disregard all UV associated alarms until the work is complete. | FLAG | stage2_low_confidence | 0.021468 | ML: above threshold (no LLM available) — 0.021 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.021468 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | AUSSYS - Chris R on site to complete a generator test. Will see associated alarms. | FLAG | stage2_low_confidence | 0.013944 | ML: above threshold (no LLM available) — 0.014 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.013944 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | QVSSC - Darren B leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055317 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | Connor Smith signing in -16C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042123 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | KSSP- Sludge Holding Blwr 1 Hi Dif Press Alarm. Both blowers are OOS. Notified Cam B. He will look into it. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | SEOC- OCF Fan1, Fan2 Uncommand Stop. Notified Phil R. He will look into it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050478 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | SEOC4- Shaft 4 Gas High Facility Shutdown Alarm. Disregard as per SCADA Report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0058195 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KSSSQW - Pump 2 Efficiency lolo, Wire-to-water Lowlow, flow lolo alarms. Notified Chris C, Assigned Pump 1 to duty 2 and placed Pump 3 back to auto. Pump 1 and 4 running normal. Chris C on his way to site. | FLAG | stage2_low_confidence | 0.011904 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.011904 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KSSP - UV channel 2 Bank 2 A lamp fail and adjacent lamp fail alarms. Checked site, UV channel 2 is active. These alarms are disregards on the shift report. | FLAG | stage2_low_confidence | 0.0097502 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0097502 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | HLSSBS - Hydrogen Sulphide Sample 1 fault alarm- disregard after hours as per shift report. | FLAG | stage2_low_confidence | 0.011561 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system] | 0.011561 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | KSSP - UV CH1 Bank 1A Low UV intensity Fault alarm. Notified Mike B, he will check SCADA. # Consult 21:34 Mike B called, requested disregard alarm for the night. | FLAG | stage2_low_confidence | 0.011024 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.011024 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | RHAMF - Unit 1 recirculation water flow, odour control system offline . Unit 2 recirculation pump pressure loss. Power blip in area, able to reset alarms and get fans and recirculation pumps back running. Generator remains active, will monitor 10:35 - generator off. No outstanding issue | FLAG | stage2_low_confidence | 0.012428 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012428 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | PVSS - Aaron CM from PCS called to inform he will be completing a reboot of the cellular modem for this location. Aaron stated the work would be best completed with pumps off. Waited until the wet well was pumped down and then informed Aaron he can begin the reboot. | FLAG | stage2_low_confidence | 0.016695 | ML: above threshold (no LLM available) — 0.017 |  | 0.016695 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: 10C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical alarm, UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 2 is active. Trending shows that flow through the UV channel recently started. Shift report states these alarms trigger when flow starts through the UV channel and can be disregarded. Alarm status changed to normal, alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.045254 | ML: above threshold (no LLM available) — 0.045 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.045254 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | AUSS- Placed Pump 6 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041868 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | NMSSBP - Kevin S working on alarms for wet well, temp, & auto dialer test | FLAG | stage2_low_confidence | 0.0086999 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0086999 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS+YNSS normal Adam Button signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046291 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | SUSP - Eric S on site to complete replacement of the lagoon flow meter. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0063521 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-01 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | GRSSWA - Chris C on site to complete work orders including a generator test, JHSC checks and a dry well flood alarm test. KBSP, NBSP, NBSSJA - Kingsley M completing a Hub 5 server restart. No impact to operations affected. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | SUSP, Ian W resetting OIT on site, disregard historian heartbeat alarm from site | FLAG | stage2_low_confidence | 0.0072353 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072353 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | KSSSQW- Wet well 1 hydrostatic level hi alarm came in. Hi flows. D2 active Pumps keeping up will clear when level pumps down | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071975 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | KSSSQW- Channel grinder 2 failed to start alarm and overload alarm came in. was not able to reset alarms and restart grinder. Notified Mike B. will head to site. Created CMU5 W11714748 NMSSBP- Wet well 1/2 ultrasonic and hydrostatic hi, Discharge flow hi, P3 pillow block hi and P4 vibration hi alarms came in D3 active. Able to reset all alarms but discharge flow hi and P4 vibration hi alarm. Will continue to monito P4 vibration hi is a disregard on shift report LSSS- LSSS2 to LSSS4 comm fail able to reset trends okay on site #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; vibration [equipment_failure]; alarm [control_system]; alarms [control_system] | failed [equipment_failure]; vibration [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | SEOC shaft 9 - O2 Monitor lolo alarm. Disregard alarm as per the shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058138 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | SUSP- Dewatering Screw Fault Alarm. Notified Cam B. He will take a look. 01:10- Cam B called back. Can disregard for the night. | FLAG | stage2_low_confidence | 0.0093827 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure]; alarm [control_system] | 0.0093827 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NBSP - Influent Flow HiHi alarm. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066169 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | KBSP - Soda Ash Conveyor E. Stop alarm came in. Called Lance J. who informed he is working on the conveyor and has hit the E. stop | FLAG | stage2_low_confidence | 0.009867 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.009867 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | LSSS, Philip R is on site, running the generator on site and will also be running pump 1 on site. Disregard alarms that come from pump 1 | FLAG | stage2_low_confidence | 0.00831 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.00831 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | NMSSBP - Kevin S. called to inform he will be completing the diesel generator test run | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071725 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | PVSS, Aaron M is finished working on the signal at site, Trends are normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067489 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | JDSS - Chris C on site to complete work orders including generator test run, JHSC checks, dry well flood alarm test, hi/low temperature alarm test and possibly hi/low wet well level alarms. Chris has requested that alarms be disregarded until his work is complete | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | MTSP - Clarifier 2 No RAS pump running alarm and Final Effluent Extended Hi Flow event alarm. Terry R working on site. He will clear alarms. # Consult. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0053578 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | Adam Button signing in 8C clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041579 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | NBSP, UV System Minor Fault Alarm, UV Bank 1A is running. When checking trends, Bank 1B occasionally turns on then off, this seems to be abnormal from Trending. When Dan H calls back at 20:30, RO will notify him of this observation | FLAG | stage2_low_confidence | 0.018389 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.018389 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | KSSSQW - Chris C has returned to site and will be trying to test the alarms stated previously, dry well flood, high/low temp and dialer test, | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | NBSP - Satnam M on site with Martin D to work on RAS valve 4. RAS pump 2 and RAS pump 3 may be OOS when the valve is worked on. Satnam informed that Young J will be on site soon. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | AUSS - Pump1 leakage alarm. Checked site, duty rotated to pump 5 and operations are normal. Contacted Kevin S who is on site with maintenance to check the pump. | FLAG | stage2_low_confidence | 0.013034 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | 0.013034 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in,weather -6C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | BLSS - Lauren S on site to inspect the odour control unit. Lauren stated she will be triggering associated alarms. | FLAG | stage2_low_confidence | 0.0162 | ML: above threshold (no LLM available) — 0.016 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.0162 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | NMSSHS- PAC Communication Failure Alarm. Notified Yash S. He will look into it. | FLAG | stage2_low_confidence | 0.014118 | ML: above threshold (no LLM available) — 0.014 | failure [equipment_failure]; alarm [control_system]; communication failure [control_system] | 0.014118 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | KSSP - Channel Aeration Blower 2 High Differential Pressure alarm came in. Checked site. Aeration blower 1 is running in duty 1. Will send an email to North WW. YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063826 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SUSP - UV System Critical Failure , Ch 1 High Level, Ch.2 Common critical alarms came in. Checked site. Plant recently activated. Disregard as per shift report. Cleared upon acknowledgement. | FLAG | stage2_low_confidence | 0.020986 | ML: above threshold (no LLM available) — 0.021 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.020986 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | AUSS - Wet well high levels. Placed pumps 2, 5, 6 with a manual setpoint of 60% 04:00 - Placed all pump setpoints back to auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038602 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | KSSP- Scum chamber 2 high level disregard on shift report SUSP- UV system critical failure/ CH 1+2 high level/ common critical alarms came in. Cleared upon acknowledgment alarms came in as flow was established to UV channel disregard on shift report | FLAG | stage2_low_confidence | 0.023111 | ML: above threshold (no LLM available) — 0.023 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.023111 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | AUSSYS - Chris R on site and will be testing the emergency eye wash stations and showers. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | SUSP - Tyson C running generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055958 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | GRSSWA- Wetwell 1/2 hihi switch alarm came in. Critical alarm all pumps running at 100 percent. Notified Mike B. Directed to continue to monitor and notify if overflow limit is reached. #consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; alarm [control_system]; overflow [infrastructure] | overflow [critical]; alarm [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | HLSSBS- Force main 1 pressure hi. Reset alarm as trends recovered | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054711 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | HLSSBS - Channel Grinder E stop alarm/ critical alarm. Notified Tyson C, directed disregard alarm until morning. # Consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | KBSP- Sludge Blower 1 motor Temp Hi alarm/ start failed alarm- duty rotated to Sludge Blower 2. Will notify area. | FLAG | stage2_low_confidence | 0.012663 | ML: above threshold (no LLM available) — 0.013 | failed [equipment_failure]; alarm [control_system] | 0.012663 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | HLSSBS - Inlet channel level high switch alarm. Critical level alarm. Checked site, trending shows that the inlet channel level is continually rising, Inlet channel grinder is faulted from earlier in the night. Called Tyson C who directed to disregard the alarm. #consult | FLAG | stage2_low_confidence | 0.024287 | ML: above threshold (no LLM available) — 0.024 | fault [equipment_failure]; faulted [equipment_failure]; alarm [control_system] | 0.024287 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | HLSSBS - Inlet channel switch hihi alarm. Tyson C was contacted earlier and stated to disregard this alarm as well as the inlet channel overflows into the wetwell. | FLAG | stage2_low_confidence | 0.030439 | ML: above threshold (no LLM available) — 0.03 | overflow [critical]; alarm [control_system]; overflow [infrastructure] | 0.030439 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | MTSP - Clarifier 1 No RAS pump running alarm. Disregard as per SCADA reiview. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.005819 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | KSSP - Niel O on site with Chase J to work on the UV system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060552 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | SUSP - UV channel 2 Bank 2A major alarm, UV system major fault and UV channel 2 common major alarm. Checked site, UV channel 2 Bank 2A has been placed in local/off mode by operations. UV channel 1 active. | FLAG | stage2_low_confidence | 0.020078 | ML: above threshold (no LLM available) — 0.02 | fault [equipment_failure]; alarm [control_system] | 0.020078 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | KSSSQW - Wet well Hi and HiHi alarms, Pump 2 wire-to-water /efficiency lo and low/low alarms, Pump 2 Low flow alarm - Rotated Pump 1 to duty 2, Pump 3 to duty3. All alarms cleared. Will monitor Pump 2 next cycle. | FLAG | stage2_low_confidence | 0.010962 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010962 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | SEOC OCF outlet fan O2 hihi alarm - Fans are running. Trend spiked and back to normal range. Disregard as per shift report. Cleared alarm. | FLAG | stage2_low_confidence | 0.0073312 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0073312 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | NBSP- Marcus R onsite. Should not trigger any alarms however maintenance will be onsite later for work on RAS pumps. KBSP- Marcus R informed that will be leaving scum pumps man/off due to high flows. Can disregard HiHi Level alarm. | FLAG | stage2_low_confidence | 0.012536 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012536 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | Connor Smith signing in 3 C Rain | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041948 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046808 | 0 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | Connor Smith signing in 1C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | KSSSQW, Placed pump 1 in D1 and pump 4 in D2 Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034544 | 0 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | NMSSBP - Wet well Hi and discharge flow Hi alarms. 3 pumps active. Alarms cleared in 5 minutes. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-08 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | NBSP - UV system minor fault alarm. Shift report states this alarm is a disregard as long as one UV bank is active. Checked site, UV bank 1B is active. Trending shows the UV duty recently swapped banks. | FLAG | stage2_low_confidence | 0.0197 | ML: above threshold (no LLM available) — 0.02 | fault [equipment_failure]; alarm [control_system] | 0.0197 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS+YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | NBSP - UV Minor fault alarm. Checked site, both UV banks active. Shift report states this alarm is a disregard. Cleared alarm. | FLAG | stage2_low_confidence | 0.017982 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.017982 | 0 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | NBW7 - Jacob M heading to site. Place well 7 man/on | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046294 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | LSSS - Phil R on site to complete a wet well level hi alarm test. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068525 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | RHAMF1- Historian Heartbeat Alarm. Notified Kyle C. He will look into it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055145 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | RHAMF - Marcos T on site to complete testing. Marcos directed to disregard alarms. | FLAG | stage2_low_confidence | 0.0084428 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0084428 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | SHSP - RAS Pump 2 Speed Deviation Alarm. Pump running 90% speed. Notified Dan H. He will investigate. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063626 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | KBSP - Harie R. called to inform that he will be completing a headworks inspection on the bar screen and grit vortex | FLAG | stage2_low_confidence | 0.008341 | ML: above threshold (no LLM available) — 0.008 |  | 0.008341 | 0 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | KSSP - Diesel containment flood alarm. Called Niel O who will check the diesel tanks. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; containment [safety] | flood [critical]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-06 | All Wastewater System ROC General | ROC | SHSP- Marcus R on site to work on air compressors KBSP- Harie R on site to work on WAS pumps | FLAG | stage2_low_confidence | 0.009369 | ML: above threshold (no LLM available) — 0.009 | sso [critical] | 0.009369 | 0 | 0
2026-03 | 2026-03-02 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical and High level alarms, UV system critical alarm. Checked site, UV 2 is running, UV flow recently started. Disregard as per the shift report. Alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.010755 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010755 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | HLSSBS - Channel Grinder E stop alarm came in. Called Darren B. who informed he is headed to site. 11:48 - Darren called back and informed the maintenance team is on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | SEOC4 - Shaft 4 O2 Monitor hi and hihi alarm. Checked site, current value is actually reading lolo. Trending shows a spike of the O2 reading. Shift report states that these O2 Monitor alarms are all disregards. Cleared hi and hihi alarms. | FLAG | stage2_low_confidence | 0.011786 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.011786 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | SEOC 4 - Shaft 4 gas high facility shutdown alarm. Checked site, fan 1 is currently running in duty 1. Operations appear normal, shift report states that this alarm is a disregard after hours. | FLAG | stage2_low_confidence | 0.0094754 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0094754 | 0 | 0
2026-03 | 2026-03-07 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | NMVCBP - Wet well 1 ultrasonic mode alarm. Pumps in local/off to prevent backup mode to start the pumps during high flow event. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; backup [infrastructure] | alarm [control_system]; backup [infrastructure] |  | 1 | 0
2026-03 | 2026-03-10 | All Wastewater System ROC General | ROC | AUSSYS - Generator 1 running status alar. Checked site, Generator ios running in local mode and ATS is pointed to town hydro. Facility logbook indicates that mechanical maintenance is on site to investigate a low oil situation. Terry C is logged into the facility logbook. | FLAG | stage2_low_confidence | 0.012197 | ML: above threshold (no LLM available) — 0.012 |  | 0.012197 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SEOC4 - Shaft 4 high facility shutdown. Disregard as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050111 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, -7D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041867 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | SUSP - Bar screen Hi level alarm. Was able to clear alarm in a few minutes. | FLAG | stage2_low_confidence | 0.0076671 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0076671 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | SUSP - Bar screen Hi level alarms in and out, Tyson C requested disregard alarm until tomorrow. # Consult | FLAG | stage2_low_confidence | 0.0087628 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0087628 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | KCSSKR - Lauren S onsite for wet well cleaning | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059852 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SEOC- OCF FAN Outlet O2 HIHi Alarm. Disregard as per SCADA Report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0054876 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | SUSP- Filters Hi Level Alarm. Notified Tyson C. He will take a look CONSULT | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051051 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-04 | All Wastewater System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | BLSS - Screen 1 emergency stop, wet well 2 and wet well 1 Overflow level alarms - Marcus R called to confirm alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; emergency [critical]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; emergency [critical]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-03 | All Wastewater System ROC General | ROC | KBSP - Gavin W onsite testing both generators | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005949 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NBSP- Inlet Channel High Float. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0066202 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | KSSP - UV bank 1A low UV intensity fault. Still reading intensity with UV1 running | FLAG | stage2_low_confidence | 0.0085387 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure] | 0.0085387 | 0 | 0
2026-03 | 2026-03-09 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NBSP - Auto dialer inlet general alarm, inlet channel high float. flowmeter hi from NMBSSJA | FLAG | stage2_low_confidence | 0.0081787 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0081787 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SUSP- Tyson C called and requested a call if basin levels hit 4.90. FIlters Hi Level Alarm came in while on phone. He will look into it. 22:54- Tyson C cleared alarm. Requested a call if it comes back in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070407 | 0 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | LSSS- Surge Tank 1 Level High Alarm, Quick spike. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0052488 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SUSP - Basin 1 high level, cleared upon Acknowledging alarm. Level within range | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0056168 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical/channel 1 high level alarms and UV system critical failure alarm. UV channel 2 is active, flow through the UV channel recently started. Disregard alarms as per shift report. Alarms cleared when acknowledged. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; alarms [control_system] | failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | KSSP, UV Ch. 1 Bank 1A Low UV Intensity Fault, Not in shift report to disregard, contacted to Tyson C, directed to disregard for the day Consult | FLAG | stage2_low_confidence | 0.0078796 | ML: above threshold (no LLM available) — 0.008 | fault [equipment_failure] | 0.0078796 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | NBSP, UV System Minor Fault, As per shift report, directed to disregard as 1 bank is currently tunning | FLAG | stage2_low_confidence | 0.0092605 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure] | 0.0092605 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 0. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-11 | All Wastewater System ROC General | ROC | NMVCBP - Dan K informed they shut the pumps and left in manual off to slow down flow to NMSSBP, disregard hi level alarms | FLAG | stage2_low_confidence | 0.010906 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.010906 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | Carter Dunn Signing in, 3D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | SEOC OCF outlet fan O2 hihi alarm. Checked site, fans are running. trending shows a spike of the oxygen sensor reading which quickly returned to normal range. These alarms are a disregard on the shift report. cleared alarm. | FLAG | stage2_low_confidence | 0.01093 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.01093 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | SEOC4 - Shaft 4 gas facility shutdown. Disregard as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004991 | 0 | 0
2026-03 | 2026-03-14 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038669 | 0 | 0
2026-03 | 2026-03-15 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 Bank 1B ballast fail alarm along with UV major alarms. Called Tyson C who is on site and will check the system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0070908 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | NMETHW - Kalid from AIM on site with contractors. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056752 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | RHAMF- Jim from NAC onsite to inform of shutting down recirculation pumps 1 and 2. He has confirmed with Daniel K. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062438 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | SECC - Sump 1 level low switch alarm. Checked site, sump pump 1 interlocked on the alarm. trending shows an abnormal dip of the sump 1 pit level. Able to clear alarm, will monitor site. | FLAG | stage2_low_confidence | 0.0096196 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system] | 0.0096196 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | AUSS - Phil R running generator, Alectra on site replacing Hydro meter. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062849 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | NMVCBP- Kevin S on site to complete wet well related work orders. Kevin directed to disregard alarms. | FLAG | stage2_low_confidence | 0.016961 | ML: above threshold (no LLM available) — 0.017 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.016961 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | SEOC- Shaft 6/7 PAC Communication Fail YDOC- PAC Communication Failure Alarm SECC- Shaft 13 to Shaft 6 Comms Failure YDBR- Communication Failure Alarm Notified Chris S. He will look into it. 09:12- Aaron CM called. All alarms have cleared. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system]; comms failure [control_system] | failure [equipment_failure]; alarm [control_system]; alarms [control_system]; communication failure [control_system]; comms failure [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | KBSP- Harie R testing reject hihi alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0064255 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in, weather +4C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043138 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | SUSSWB- Ventilation H2S OOR Alarm. Disregard as per SCADA Report. | FLAG | stage2_low_confidence | 0.0085297 | ML: above threshold (no LLM available) — 0.009 | scada [control_system]; alarm [control_system]; h2s [safety] | 0.0085297 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical/channel 1 high level alarms and UV system critical failure alarm. UV channel 1B is active, flow through the UV channel recently started. Disregard alarms as per shift report. Alarms cleared when acknowledged. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; alarms [control_system] | failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | SHSP - Vortex blower 1 and 2 general alarm. Checked site, both vortex blowers are in local/off mode. Called Gavin W who is working on them | FLAG | stage2_low_confidence | 0.0077292 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077292 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | MTSP - Alum pump containment flood alarm. Notified Phil R, he will check SCADA. # Consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system]; containment [safety] | flood [critical]; scada [control_system]; alarm [control_system]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | NBSP- UV System Minor Fault, UV Bank 1B is running. Disregard alarm as per shift report. | FLAG | stage2_low_confidence | 0.011508 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system] | 0.011508 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | SUSP- UV System Critical/High Level Alarms. Alarms cleared. Known issue on SCADA Report. | FLAG | stage2_low_confidence | 0.0092333 | ML: above threshold (no LLM available) — 0.009 | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0092333 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | MTSP - Terry R. called to inform that they have a VAC truck on site and will be pumping down the chamber. Terry informed he will have the RAS pumps off and everything is diverting to lagoons | FLAG | stage2_low_confidence | 0.011029 | ML: above threshold (no LLM available) — 0.011 |  | 0.011029 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SUSP- UV System Critical Failure, High Level Alarm. Alarms cleared after acknowledging. Known issue on SCADA Report. | FLAG | stage2_low_confidence | 0.017098 | ML: above threshold (no LLM available) — 0.017 | failure [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.017098 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | SEOC - Evgeny S restarting OIT, disregard Historian heartbeat alarm. | FLAG | stage2_low_confidence | 0.0072957 | ML: above threshold (no LLM available) — 0.007 | alarm [control_system] | 0.0072957 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | SUSP- UV System Major Fault, UV Ch. 1 Bank 1B Major Alarm. UV is Local off. Tyson C informed Mike B working on it. | FLAG | stage2_low_confidence | 0.013261 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; alarm [control_system] | 0.013261 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: 3C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | HLSSBS - Site Hydro Power Failure alarm came in along with Channel Grinder E stop, Generator running status, and Sewage pump 2 VFD fault. Checked site. After 10 mins, site is still connected to generator power and Sewage pump 2 VFD fault is outstanding. No outage reported on outage map. 07:27 - Outage has been reported on the outage map and is under investigation. ETA is 09:45. Informed Darren B 09:53 - Site is back to hydro power. KSSSQW - Channel Grinder 1 and 2 overload alarms came in. Unable to clear. Duty is active. Called Darren B. who will attend site. CMU5 created W11750026 #CONSULT #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | MTSP - Grit System 1 and 2 fault and failed to start alarms came in along with Dewatering Screw fault. Checked site. Called Marcos T. who informed he is on site and just cleaned the Mechanical Bar Screen. Marcos will look into these alarms 10:16 - Marcos called back to inform that he has cleared the alarms #CONSULT | FLAG | stage2_low_confidence | 0.012713 | ML: above threshold (no LLM available) — 0.013 | fault [equipment_failure]; failed [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.012713 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | SUSSWB- Brent S onsite for generator maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060465 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | HMSS, Bar Screen 2 Fault, notified Marcus R, he is heading to site 21:32, Marcus R is requesting a second operator as he has to enter the wet well for some valving, Contacted Tyson C, he will give Marcus R a call 21:37, Tyson C is heading to site 22:30, Operators have left site CMU5: W11737262 (Marcus) CMU5: W11737271 (Tyson) | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure] | 0.0044677 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | NBSP- Mech. Bar Screen General Alarm, Mech Bar Screen Out of Service Alarm. Unable to clear alarms. Emailed West Ops. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; alarm [control_system]; alarms [control_system] | out of service [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | NBSP - Mech Bar screen out of service/general alarms. Will monitor Inlet channel levels and notify OP first thing in the morning. 05:30 Lance J requested to start Bar screen continuous override. Not able to reset alarm. Lance J requested disregard for now. # Consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; alarm [control_system]; alarms [control_system] | out of service [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | KCSSKR, Sean P on site, doing a generator load test | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057522 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | MTSP - UV system Major fault alarm. Checked site, UV bank 1 A is active and trending indicates normal operations. UV bank 1B is the bank with the alarm and is in local/off mode. | FLAG | stage2_low_confidence | 0.017581 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system] | 0.017581 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, 0D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | SHSSDK- Gavin W onsite for wet well cleaning with contractor. Disregard low level alarms. | FLAG | stage2_low_confidence | 0.0092775 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0092775 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | AUSS - Martin D on site to complete pump inspections and testing. Martin has requested that pump alarms be disregarded from this site until the work is complete. | FLAG | stage2_low_confidence | 0.012278 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012278 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | LSSS - Noted that LSSS pump 1 is in auto and has faulted on a bearing high temperature alarm. Shift report states this pump should be manual/off and OOS status. Called Phil R to confirm. Placed pump 1 manual/off and OOS status for the weekend. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | Connor Smith signing in 9C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042116 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | KBSP - David D on site with Total Power to complete a generator load bank test. No transfer of station power. | FLAG | stage2_low_confidence | 0.0075345 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075345 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | KBSP- Gen2 REM MODE DI-STS. Lance J. called and requested to disregard as contractors are working on generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060804 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | KSSP - Sludge Holding Tank 2 OOR and Fault alarms came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.011662 | ML: above threshold (no LLM available) — 0.012 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011662 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | NBSP -Young J working on RAS/WAS pumps | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057884 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | NMSSBP- Kevin S testing High wet well level alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00673 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | SUSP - UV Ch.1 Common Critical alarm, High level and UV System Critical alarms came in. All alarms cleared on acknowledgement. Shift report informs that this occurs during plant start up | FLAG | stage2_low_confidence | 0.0095861 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0095861 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | AUSS - Marcos T and Chris R on site for generator 3 testing. Test will be off load. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050788 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | KSSP - Arthur L finished and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.005852 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: 2C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0045807 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal SUSSHS - Sewage Pump 1 No Flow and VFD Fault alarms came in. Unable to clear. Called Chris C. who is heading to site. CMU5 Created W11762134 01:42 - Chris C. called back to inform that he is finished on site and informed that he left sewage pump 1 in auto but manual setpoint at 20% #CONSULT #CMU5 | FLAG | stage2_low_confidence | 0.0090568 | ML: above threshold (no LLM available) — 0.009 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.0090568 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, 3D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | NMSSBP- Mech Screen 2 Overtorque Alarm. Notified Kevin S. He will look into it. 13:59- Terry R called. Maintenance is onsite working on bar screen. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054719 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | RHAMF - Jun Jie from NAC is on site and completing a generator test. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0061982 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 2c | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | SUSP - UV System Critical failure alarm came in. Checked site. Alarms were triggered by plant startup. Alarms cleared upon acknowledgement. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.021892 | ML: above threshold (no LLM available) — 0.022 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.021892 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | SHSP- Marcus R onsite working on aeration, sludge and vortex blowers. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066687 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | MTSP - UV major alarm still outstanding. Called Marcos T who stated that electricians are on site to complete work on the UV system and flow has been diverted to lagoon since before their work started. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | RHAMF - Jun jie from NAC on site and has requested that all fans and pumps be placed into auto mode and the alarms cleared. Made the necessary changes. | FLAG | stage2_low_confidence | 0.01176 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.01176 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | SEOC4- Bill VB Requested to rotate fan duty so that fan 2 is in duty 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051371 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: 0C and cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044604 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | KSSP - ZW2 shutdown due to not all devices in auto. Appears train 2 VFD pump is shown local off. 4 Trains remain in service. Email sent to area. | FLAG | stage2_low_confidence | 0.0072532 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072532 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | Carter D Signing In, 4D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041331 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SEOC OCF - Parth P and Rick L heading to site to replace O2 sensor. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050392 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | RHAMF - Jun Jie from NAC on site to complete vibration testing. Jun Jie requested that the recirculation pump duties be changed so the vibration readings can be taken. Made necessary adjustments. | FLAG | stage2_low_confidence | 0.02048 | ML: above threshold (no LLM available) — 0.02 | vibration [equipment_failure] | 0.02048 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | SEOC Shaft 9 0 O2 Monitor Hi, HiHi and OOR alarm. Alarms are a disregard on the shift report. Alarms cleared on reset. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.007024 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | SHSP - Gavin W on site to complete work on RAS pumps. Gavin will be placing RAS pumps in local mode for inspection and maintenance. Gavin requested the associated alarms be disregarded. | FLAG | stage2_low_confidence | 0.022555 | ML: above threshold (no LLM available) — 0.023 | sso [critical]; alarm [control_system]; alarms [control_system] | 0.022555 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | NBSSJA- Pump1 VFD Fault Alarm. Pump 3 running in auto. Notified Marcus R | FLAG | stage2_low_confidence | 0.010451 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure]; alarm [control_system] | 0.010451 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | AUSS - Kyle B on site to replace a UPS battery. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056909 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | Connor Smith signing in 3C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041757 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | KSSP- Theodore from AB onsite doing some welding. Requested a call if any smoke alarms come in. Phone-289-839-0704 | FLAG | stage2_low_confidence | 0.012479 | ML: above threshold (no LLM available) — 0.012 | smoke [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.012479 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | AUSS- Generator 1,2,3 Not in Auto Alarms. Alarms cleared on their own. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0062206 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | KSSP- Neil O onsite working on membranes. Disregard low levels. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064085 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | SHSP - Aeration blower 1 uncommanded stop and start alarm. Called Gavin W who stated he is working on the blower. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068835 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | LSSS - Phil R working on Surge tanks, directed disregard Hi/low level alarms. | FLAG | stage2_low_confidence | 0.0087776 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0087776 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | Carter D Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052296 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | NMEQBP - Potable water flow HiHi and fault alarms. Called Kevin S who is on site and triggered the alarms. Able to reset once the flow returned to normal range. | FLAG | stage2_low_confidence | 0.019885 | ML: above threshold (no LLM available) — 0.02 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019885 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | SUSSHS - Terry C on site to complete vibration testing. Terry requested that pump 1 be placed into duty 1. | FLAG | stage2_low_confidence | 0.010352 | ML: above threshold (no LLM available) — 0.01 | vibration [equipment_failure] | 0.010352 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | KBSP- David D from maintenance onsite for work on generator 2. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048669 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | KBSP- UV. Ch. 1 Common Major Alarm. Notified Lance J. He was testing onsite and cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058715 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | AUSS, Chris R on site, placed the east force main in isolation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060441 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | NMSSHS- Kevin S onsite for work orders | FLAG | stage2_low_confidence | 0.0096929 | ML: above threshold (no LLM available) — 0.01 | work order [maintenance_action] | 0.0096929 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | SUSP- UV Critical Alarm/High Level Alarm. Alarms cleared after acknowledging | FLAG | stage2_low_confidence | 0.007566 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.007566 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | KSSP - Garric from Ferguson electric turning off power to generators. Replacing batteries. | FLAG | stage2_low_confidence | 0.0073144 | ML: above threshold (no LLM available) — 0.007 |  | 0.0073144 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | SHSP - RAS Pump 2 Speed Deviation Alarm, alarm cleared right away. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055563 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | AUSSYS - Historian Heartbeat alarm, cleared when acknowledged . | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071299 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | HMSS - Lauren S and Marcus R performing drywell and wet well inspections, requested disregard Drywell flood and HiHi alarms. Marcus R testing Hi/Low temp alarm. Confirmed Drywell flood alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SHSP- Aeration Blower 1 Speed Sig Error/High Temperature. Blower is Local off and Marcus R onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058107 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | PVSS - Marcus R. called to inform that he and Lauren S. are on site and will be working on the wet wells. Marcus informed that all LIT and wet well alarms can be disregarded | FLAG | stage2_low_confidence | 0.013068 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.013068 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | QVSSSC - Site hydro power fail, Sewage Pumps 1 and 2 failure, and generator running status alarm came in. Checked site. Site is not connected to generator power but generator is running. Likely a power blip. All alarms have cleared. | FLAG | stage2_low_confidence | 0.022323 | ML: above threshold (no LLM available) — 0.022 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.022323 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | MTSP - Aeration tank 2 DO low alarm - Notified Barry M. He is on site/will check. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00545 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | HLSSBS- Ric L onsite troubleshooting wetwell overflow FIT 14:47- Ric L finished onsite. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; overflow [infrastructure] | overflow [critical]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | NBSP - Vortex 2 air scour uncomamnded close alarm. Disregard in the shift report if it can be reset. Able to reset alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0071472 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical alarm, UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 1 is active. Trending shows flow through the UV system just started. Shift report states these alarms trigger when the UV flow starts. Disregard and clear alarms. | FLAG | stage2_low_confidence | 0.03036 | ML: above threshold (no LLM available) — 0.03 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.03036 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | MTSP, UV System Major Fault, 2 UV systems are running, Bank 1B OOS, Notified Kevin S, directed to disregard for the night consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure] | fault [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal SUSP - Bar Screen Hi alarm came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.00521 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | NBSP - UV System Minor Fault alarm came in. Disregarded as per shift report as there is one bank running | FLAG | stage2_low_confidence | 0.01632 | ML: above threshold (no LLM available) — 0.016 | fault [equipment_failure]; alarm [control_system] | 0.01632 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDOC - Pump 2 failed to start and pump 2 inlet valve failed to open alarm. Checked site, pump 2 is currently manual/off. Pump 1 is active in auto mode. Will monitor site to determine if operations is making changes. 09:23 - YDOC - Called Terry R who is on the way to site and will check operations. | FLAG | stage2_low_confidence | 0.029655 | ML: above threshold (no LLM available) — 0.03 | failed [equipment_failure]; alarm [control_system]; valve failed [infrastructure] | 0.029655 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | wrong book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050742 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | KSSP - Scum Chamber 2 High Level Alarm came in. Disregarded as per shift report | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0058217 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0038978 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047008 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | BLSS - David D finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052476 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | MTSS, Barry M called, Site back to normal operation | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060646 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -7C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003864 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | NMEQBP - Kingsley M restarting OIT. Disregard Historian Heartbeat alarm. 12:05 Kingsley M completed work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0045909 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | NMSSBP- Mech Screen 1 Fault Alarm. Notified Kevin S. He will look into it. | FLAG | stage2_low_confidence | 0.010578 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; alarm [control_system] | 0.010578 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | KBSP - Aaron CM working on the KBSP APN network configuration. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064261 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | AUSS - Marcos T called to inform that Generator 3 will remain out of service for the night. Generator 1 and 2 are available to run if a power failure occurs. Generator 1 and 2 can sustain a maximum of four pumps. SCADA will limit the number of pumps available to four in the event of a power failure. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; out of service [equipment_failure]; scada [control_system] | failure [equipment_failure]; out of service [equipment_failure]; scada [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | BLSS - David D troubleshooting Pump 2. Requested assign Pump 2 to Duty 1 for test. Placed Pump 1 man/off , pump 2 started/running ok. Placed Pump 2 back to auto. | FLAG | stage2_low_confidence | 0.0077649 | ML: above threshold (no LLM available) — 0.008 |  | 0.0077649 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | AUSSYS- Evgeni S restarting OIT. Disregard heartbeat alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0069979 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | LSSS - Pump 4 emergency stop alarm, Phil R and Terry C on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system] | emergency [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | NBSP - Mechanical Bar Screen Failed to Stop and OOS alarms came in multiple times along with Inlet Channel High Float. Checked site. Called Lance J, who directed to place the manual override setpoint to start. This triggered the Mechanical Bar Screen general alarm which placed the bar screen in local. Lance informed he is headed to site to reset these alarms. CMU5 Created W11750066 11:51 - Inlet Channel High float and level hihi alarms came in. This is due to the Mechanical Bar Screen being OOS but Lance informed once the hihi levels hit, will go through the manual bar screen 13:32 - Lance J. called to inform that he has cleared the alarms and the mechanical bar screen is running now. Lance informed that if the fail to stop alarm comes in again, place the manual override setpoint back to start. If the Mechanical Bar Screen General alarm is triggered again, Lance would like a call back. Lance directed to disregard the Sludge Thickener Hi/HiHi alarms #CONSULT #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical/channel 1 high level alarms and UV system critical failure alarm. UV channel 1B is active, flow through the UV channel recently started. Disregard alarms as per shift report. Alarms cleared when acknowledged. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; alarms [control_system] | failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | PVSS - David D. is on site and will be turning off the odour control system for a PM | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006761 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | MTSP - Barry M. called to inform that he is on site at MTSP but will be shutting down MTSS. Barry informed that the high wet well levels can be disregarded | FLAG | stage2_low_confidence | 0.0093551 | ML: above threshold (no LLM available) — 0.009 |  | 0.0093551 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | KBSP - Inlet channel filter bypass pending alarm. Harie R testing alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system] | bypass [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 5. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | KSSP, UV Panel Major Fault/System Major Fault/common major fault/Module Comm fail, nothing in shift report about UV items being disregarded, notified Tyson C, he will look into it 04:40, Tyson C directed to disregard, they will look into it in the morning consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 common critical alarm, UV channel 2 high level alarm, UV system critical failure alarm, UV channel 1 common critical and high level alarm. Checked site, UV channel 1 Bank 1B is active. Trending shows flow to the UV system recently started. Shift report states these alarms will trigger when the plant activates and flow to the UV starts. Cleared alarms. | FLAG | stage2_low_confidence | 0.042884 | ML: above threshold (no LLM available) — 0.043 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.042884 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | NBSP- Young J onsite working on UV's | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056986 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | Connor Smith signing in -12C Windy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042119 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | KSSP- Neil O onsite with contractors for generator work. Will be Local off for the day. | FLAG | stage2_low_confidence | 0.0072367 | ML: above threshold (no LLM available) — 0.007 |  | 0.0072367 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in,weather -11C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043101 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | RHAMF-Assigned recirculation pump 1 to duty 1 for Jim from NAC. 12:12 Recirculation pump 1 for both Train 1 and 2 on duty 1, recirculation pumps 2 OOS (local off) until tomorrow. Jim from NAC leaving site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | RHAMF1 - Jimmy from NAC working on recirculation Pump 2. 14:40 Joe O from CPD requested switch Duty, Unit 1 recirculation Pump 2 to duty 1. Recirculation water low/low, pressure low and low/low. Recirculation pumps interlocked. Jimmy from NAC troubleshooting. 15:00 Man/stopped recirculation Pump1 for Jimmy from NAC, he is running recirculation Pump 1 in Local. 15:14 Switched Unit 2 recirculation Pump 2 to duty 1 for Jimmy from NAC 15:24 Unit 1 Recirculation Pump 1 back to auto, recirculation Pump 2 to Duty 1 as per Jimmy from NAC. 15:30 Unit 1 Recirculation Pump 1 assigned to duty 1 as per Jimmy from NAC. | FLAG | stage2_low_confidence | 0.017754 | ML: above threshold (no LLM available) — 0.018 |  | 0.017754 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | Gluzen Ramos Ong signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054396 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | NBSP - Barscreen out of service and barscreen fail to stop alarms. Checked site, barscreen is in auto but faulted. Attempted to clear alarm. Alarm cleared. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | NMSSBP - Mech screen 2 E-stop. Eqipment OOS and Kevin S onsite | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | Adeela Khan Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | NBSP - Bar Screen Failed to Stop and OOS alarms came in. Checked site. Bar screen is in auto. Alarm cleared. 22:26 - Alarms came back in along with Inlet Channel High float alarm. Would not clear. NBSP - Inlet Works general alarms came in multiple times today. Called Lance J. who directed to select Continuous Override Start on the bar screen setpoint. Alarms were cleared and bar screen is now running. Lance would like a call back if the alarm comes back in. #CONSULT | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] | failed [equipment_failure]; oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | LSSS, David D on site turning off the odour control | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057646 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | KBSP - Lance J working on UV channel 1, disregard alarms for the duration of the work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0070361 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -2C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | BLSS - Screen 1 fault, screen 1 uncommanded stop and mechanical screen system not on. Checked site, barscreen is interlocked. Unable to clear alarms. Contacted Marcus R who will investigate. | FLAG | stage2_low_confidence | 0.018432 | ML: above threshold (no LLM available) — 0.018 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.018432 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | PVSS - Marcus R onsite running generator, drywell inspection, sump alarm, temp, flood, & odour control unit | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | Connor Smith signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052731 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | YDSS + YNSS normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | NMSSYS- Daniel K onsite with contractor troubleshooting Force Main Valve 2. Pumps are in manual and Dan will monitor Wet well levels. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0067805 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | NBSP - Barscreen general alarm. Called Young J who is working on the barscreen system. | FLAG | stage2_low_confidence | 0.0079609 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0079609 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | KBSP- David D onsite for generator work. Lauren S and Lance J also onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0068023 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053605 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | LSSS - Wet Well Screen 1 Differential Level LOE alarm came in. Trends are okay. Alarm cleared | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059831 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | LSSS- Ubah (Student) onsite and requested pump 6 in duty 1 for sampling. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051286 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | SHSP - RAS pump 2 speed deviation alarm. Appears to be just rotated in. Informed Lance J, okay to rotate RAS pump 3 into duty 1. for the night | FLAG | stage2_low_confidence | 0.0080185 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0080185 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | SUSP - UV System Critical Failure, Ch.1 High Level, and Ch.1 and 2 Common Critical alarms came in. Alarms cleared upon acknowledgement. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.018958 | ML: above threshold (no LLM available) — 0.019 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.018958 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | AUSSSR- Line 2 Valve Overtorque Alarm. Two lines are not available. Notified Chris R. He will look into it. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0065195 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | MTSP - UV Systems major Fault alarm came in. Checked site. UV bank 1B is local/off and offline as per shift report. UV Bank 1A is currently running but flashing and permissive status is interlocked. Called Kevin S. who will take a look. 22:40 - Kevin S. called back and informed that he will head to site. Kevin would like to verify that the UV Bank 1A is running even though it is reading interlocked and that there is no tertiary bypass. CMU5 Created W11740941 00:02 - Kevin S. called back to inform that UV Bank 1A was running and there was no bypass. Kevin informed that he was able to clear alarm and will investigate further in the morning. Kevin directed to disregard if the same alarm comes back in but give a call back if the UV does not have a running status 03:25 - UV System Major Fault came back in. UV Bank 1A is running. Disregarded as per Kevin S. #CONSULT #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; fault [equipment_failure]; alarm [control_system] | bypass [critical]; fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | HMSS - Marcus R testing High wet well level alarms. | FLAG | stage2_low_confidence | 0.0078288 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0078288 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 1 is active. Trending shows flow recently started for the UV system. Shift report states these alarms trigger on flow start and can be disregarded. Alarms cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.028117 | ML: above threshold (no LLM available) — 0.028 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.028117 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | MTSP - Alum Pump Containment Flood Alarm outstanding. Checked MTSP logbook and noticed that Phil R. attended site. Called Phil R. who informed that he was able to pump out the chamber but it appears there is no alum leak but there was water in the chamber due to a previous effluent line break. Phil informed that he is unable to clear the alarm due to an issue with the float and directed to disregard alarm until tomorrow. Phil also requests a CMU5. CMU5 Created W11762108 #CONSULT #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; leak [infrastructure]; containment [safety] | flood [critical]; alarm [control_system]; leak [infrastructure]; containment [safety] |  | 1 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | Ethan U signing in Weather 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | MTSP - Terry C running generator not on the load. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060572 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | KSSSQW, Chris C on site, running generator | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054951 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | SUSP - Tyson C called and directed to activate the sludge transfer sequence by hitting the 'Start Transfer" button. | FLAG | stage2_low_confidence | 0.0082577 | ML: above threshold (no LLM available) — 0.008 |  | 0.0082577 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052752 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | KSSP - CIP Cean/Recirc flow hihi/lo. Status went to normal right away. Train 3 going through cool down | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058669 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | Angelica Chepiga signing in,weather -7C | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0042905 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | NBSP - UV Minor Fault alarm. Checked site, UV Bank 1B is active. Trending shows that the UV system duty recently rotated. Shift report states this alarm is a disregard as long as one bank is running. | FLAG | stage2_low_confidence | 0.01936 | ML: above threshold (no LLM available) — 0.019 | fault [equipment_failure]; alarm [control_system] | 0.01936 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | Carter Dunn Signing In, 2D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041681 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | NBSP - UV system minor fault, disregard as per shift report | FLAG | stage2_low_confidence | 0.010017 | ML: above threshold (no LLM available) — 0.01 | fault [equipment_failure] | 0.010017 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | KSSP - Niel O and Chase J on site to complete work on the UV system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00631 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | Christian Van Beek signing in. Weather: -6C and clear. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046011 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | 13:23 SHSP - Power blip. Notified Gavin W, he is on site, will reset/clear alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0052368 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | BSP- Inlet Channel High Float, Mech. Bar Screen Dif. Level HiHi Alarm. Notified Lance J. He will attend site. W11749371 CMU5 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0042932 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | yds + ynss normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049649 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | Connor Smith signing in -3C Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.00423 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | Angelica Chepiga signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053869 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: -2C and Cloudy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044801 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | YDSS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0049575 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046365 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | KSSP - ZW3 High turbidity/ shutdown alarm, notified Chase J, he will investigate. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0057198 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | NMSSBP- Satnam M onsite for generator testing. 14:40- Finished onsite. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0035178 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | KCSSKR, Generator Running Alarm/Pump 3 Fault Alarm, as per interim, notified Lance J, he is heading to site 01:25, Contacted Hydro 1 and spoke with Operator Abby, Informed her of the outages, Abby informed the ROC that this was a planned outage and work is currently being done to their system. Power outage should last from 1AM-4AM. Passed on this new information to Lance J. 01:54, Lance J reset Pump 3 and placed it man/off. Lance J leaving site CMU5: W11756679 | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | SUSP- Tyson C onsite working on UV channel B | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059426 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | SUSP - UV Channel 1 Bank 1A major alarm, common major alarm and UV system major fault alarm. Checked site, UV channel 1 Bank 1 A is in local on. UV channel 1 Bank 1B is also on and in auto mode. System dose and intensitya re normal for the bank in auto. UV intensity and for Bank 1 A is higher than normal. Will monitor site and investigate who is on site. | FLAG | stage2_low_confidence | 0.039001 | ML: above threshold (no LLM available) — 0.039 | fault [equipment_failure]; alarm [control_system] | 0.039001 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | NBSP- Lauren S onsite testing sump pits and working on air compressors. | FLAG | stage2_low_confidence | 0.010673 | ML: above threshold (no LLM available) — 0.011 | sso [critical] | 0.010673 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SEOC- Phil R and Terry S onsite working on biofilters and recirc pumps. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066923 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | BLSS - Pump 3 on duty 6/ OOS. Notified Lauren S, she assigned Pump 3 to duty 1. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-27 | All Wastewater System ROC General | ROC | LSSS - rotated D1 from P4 to P6 for EME sampling | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004596 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | LSSS - Ubah F. from EME is on site for weekly testing and requested pump 6 on. Duty 1 is about to activate and pump 6 is already in duty 1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0066384 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | KSSP - Neil O and Chase J working on UV system. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060289 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal SUSP - UV system critical failure, common critical alarm, high level Ch. 2. Cleared right away. Cleared when UV gates opened | FLAG | stage2_low_confidence | 0.010134 | ML: above threshold (no LLM available) — 0.01 | failure [equipment_failure]; alarm [control_system] | 0.010134 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | LSSS - Wet well screen 1 differential hihi alarm. Checked site, trending shows an abnormal spike of the screen 1 differential level reading. Loss of echo alarms have also been triggering intermittently. Will send email to area ops. Cleared alarms. | FLAG | stage2_low_confidence | 0.012326 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system] | 0.012326 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | RHAMF - Unit 1 Recirculation Pump 1 and 2 fan overload alarms came in. Checked site. Both fans are running and Unit 2 Recirculation Pump 1 is running. Disregarded as per shift report and will call NAC if a fan stops working or a power outage occurs | FLAG | stage2_low_confidence | 0.014894 | ML: above threshold (no LLM available) — 0.015 | alarm [control_system]; alarms [control_system] | 0.014894 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: 8C and raining | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044658 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | SUSP - UV critical failure alarm came in and cleared upon acknowledgement. Plant recently activated. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.018324 | ML: above threshold (no LLM available) — 0.018 | failure [equipment_failure]; alarm [control_system] | 0.018324 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | Adeela Khan signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052508 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDOC - Terry R finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052485 | 0 | 0
2026-03 | 2026-03-22 | All Wastewater System ROC General | ROC | YDSS +YNSS Normal Adeela Khan signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0031998 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | NBSP - Young J, Marcus R and Lauren S are on site to complete maintenance on all blowers on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0071575 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | NBSP - Inlet channel level high float alarm - alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0070779 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | SUSP - Bar screen Hi level alarm. Disregard as per shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0072031 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | PVSS - Brent St C on site with Total Power to complete generator maintenance. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0064839 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | BLSS - Screen Differential Level Hi alarm came in. Disregarded as per shift report | FLAG | stage2_low_confidence | 0.0077612 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0077612 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | SHSP- Gavin W working on Ras pump 2, disregard alarms for the duration of the work. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0069452 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | SHSP - Aeration Blower 1 Fan Overload alarm came in. Checked site. Aeration blower 1 is still running at 51%. Called Marcus R. to receive direction to rotate duties. Rotated blower 2 to duty 1. #consult | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0072116 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | AURSBS, Activated D1 AUW2/3/5, Placed well 2/3/5 in man/on. wrong book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0024184 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | NMSSBP- Satnam S onsite for generator testing. 11:31- Finished on site, all alarms cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0046392 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | KCSSKR- Pump 3 Uncommanded Stop, Fault Alarms. Pump 2 running in duty 1. Notified Marcus R. | FLAG | stage2_low_confidence | 0.011408 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011408 | 0 | 0
2026-03 | 2026-03-16 | All Wastewater System ROC General | ROC | KSSSQW - Pump 2 lo/low- low flow, Wet wells Hi and Hihi alarms, P2 efficiency low/low-low, wire- to - water low/low alarms. Assigned P2 to duty 4/ man/off, Pump 3 to duty 3. Notified Neil O. He will attend site later today to check P2. | FLAG | stage2_low_confidence | 0.013675 | ML: above threshold (no LLM available) — 0.014 | alarm [control_system]; alarms [control_system] | 0.013675 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | Ethan Ullalkar signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053801 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | SHSP- Gavin W onsite diverting to Lagoon for work on filter inlet channel. Disregard related alarms. | FLAG | stage2_low_confidence | 0.0098051 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.0098051 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | Ethan U signing in | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051645 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | AUSSYS - Marcos T testing High Wet well level alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068066 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SUSP - Bar screen Hi level alarm. Disregard as per shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0072031 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | SEOC9 - Shaft 9 O2 Monitor HiHi/OOR alarms, disregard as per SCADA review. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system]; alarms [control_system] | 0.0065793 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SUSSWB- Ventilation H2 S High Alarm. Alarm cleared. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0051217 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | MTSP - Clarifier 1 and 2 no RAS pump running alarm. Checked site, all RAS pumps currently manual/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0062948 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | AUSS - Kyle B finished work and leaving site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059422 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | AUSS - Bill V. working on Generator 3 out: 13:40. cleared outstanding gen 3 alarms | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0038225 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | wrong book | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0050742 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-21 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | SUSP - UV channel 1 high level alarm. UV channel 1 common critical alarm and UV system critical failure alarm. Checked site, UV channel 1 is active. Trending shows flow to the UV channel recently started. Shift report states these alarms trigger when the flow to the UV channel starts and they can be disregarded. Cleared alarms. | FLAG | stage2_low_confidence | 0.035084 | ML: above threshold (no LLM available) — 0.035 | failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.035084 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052967 | 0 | 0
2026-03 | 2026-03-20 | All Wastewater System ROC General | ROC | Connor Smith signing in 0C Snowy | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041992 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | HMSS - Wet well 1 and 2 Metro Overflow alarms. Called Marcus R and Lauren S, no answer. Will call again. 12:58 Called Marcus R. Confirmed Metro Overflow alarms- test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | RHAMF - Jun Jia from NAC on site and has requested that all recirculation pumps, all building air handling fans and AMF Fans be placed manual/off to complete their testing. Called Chris R who is aware of the work and will contact Daniel K to confirm. Placed all pumps and fans manual/off. | FLAG | stage2_low_confidence | 0.017321 | ML: above threshold (no LLM available) — 0.017 |  | 0.017321 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-17 | All Wastewater System ROC General | ROC | KSSSQW - Ernie H on site performing Generators PM's, running generator. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0062932 | 0 | 0
2026-03 | 2026-03-25 | All Wastewater System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-30 | Aurora Henderson Sewage Pumping Station | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked generator and valve room. -All pumps in auto and available. | FLAG | stage2_low_confidence | 0.012005 | ML: above threshold (no LLM available) — 0.012 |  | 0.012005 | 0 | 0
2026-03 | 2026-03-02 | All Water System ROC General | ROC | Christian Van Beek signing in. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054278 | 0 | 0
2026-03 | 2026-03-03 | All Water System ROC General | ROC | QVETQS - drawdown initiated by Ben H. NMETHW isolated. Duty 1 activated for NMETHW. NMETIB duty 1 stop setpoint increased to 85% from 75% and duty activated. | FLAG | stage2_low_confidence | 0.0075922 | ML: above threshold (no LLM available) — 0.008 |  | 0.0075922 | 0 | 0
2026-03 | 2026-03-12 | All Water System ROC General | ROC | MARS - lo level, deactivate AURSBS. Will monitor | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0060031 | 0 | 0
2026-03 | 2026-03-04 | All Water System ROC General | ROC | GWTP - Keswick header fluoride low alarm. Checked site, Keswick system is active and high lift pumps are pushing flow. Trending shows no dip of the fluoride reading below the low alarm setpoint at the time of the alarm. Alarm status changed to Normal, alarm cleared on acknowledgement. | FLAG | stage2_low_confidence | 0.019222 | ML: above threshold (no LLM available) — 0.019 | alarm [control_system] | 0.019222 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | MKRSEM- Called Toronto and requested pumps off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0059819 | 0 | 0
2026-03 | 2026-03-13 | All Water System ROC General | ROC | RHRSTR- Deactivated duty | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053751 | 0 | 0
2026-03 | 2026-03-15 | All Water System ROC General | ROC | SHTP - KMNO Tank 1 and 2 Level Low (info alarm). Tank 2 in duty 1. Jordan B will check SCADA and call back. # Consult 10:15 Jordan B will attend site. # CMU5 W11733473 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | scada [control_system]; alarm [control_system] | 0.0065971 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | YWS + NYWS Normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | VNPS PD7, Placed pump 2 man/off MAPS PD7, Placed pump 2 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034232 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | HLVCMA, Valve Chamber Flood Alarm has come in 2 times but then has cleared, will continue to monitor site, if it comes in a third time, will notify Harsh P 18:32, Alarm came in a third time, notified Harsh P, he is heading to site 21:30, Harsh P is finished on site CMU5: W11760443 | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MAPS PD7, Placed pump 2 in auto VNPS PD7, Placed pump 2 in man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.003475 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | SUETDR- Activated duty Interim Procedure | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040152 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | 13:27 SHTP - Power blip. Plant was running. Notified Jen S , she is on site , will reset alarms. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system]; alarms [control_system] | 0.0056501 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | QVW12 - Chlorine gas leak alarm and valve system emergency closure faults. Called Joe D to return to site for further investigation. Placed wells in manual/off. 16:11 - QVW12 - Joe D contacted Eric S who will attend site to replace the chlorine gas detector. Joe D not attending site. CMU5 already created for Eric S previously. #consult | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; gas leak [critical]; fault [equipment_failure]; alarm [control_system]; leak [infrastructure] | emergency [critical]; gas leak [critical]; fault [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | YWS + NYWS normal Connor Smith signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004684 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | KCETDS- Tim H onsite for filling of tower | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0058362 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | Stouffville: Received call forwarded from Access York from Dave Raymer (647-395-2237, ED of Eastern Gate Village, Seniors Community). He described his issue that testing water from Stouffville Wells 1 and 2 are going onto their property (6985 Main Street, Stouffville) and their pump station that typically pumps that water has failed. He has requested that that flow is turned off until repairs to their pumps are made, currently no estimated time. Notified Jack P. 10:45 - Phil D. and Jack P. attending site. CMU5: W11764329 | FLAG | stage2_low_confidence | 0.081164 | ML: above threshold (no LLM available) — 0.081 | failed [equipment_failure]; repair [maintenance_action] | 0.081164 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | JFPS - Lee F working on site. Man/stop P1 / assigned to D5, Assigned P2 to duty 1 for Lee F. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053255 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | QVW12 - Kyle R on site to complete work on the well 2 starter devices. Kyle has placed well pump 2 local/off. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057663 | 0 | 0
2026-03 | 2026-03-19 | All Wastewater System ROC General | ROC | BLSS - Lauren S. and Lance J. attended screen 1 fault. Screen back in service and all alarms cleared. CMU: 11746738 | FLAG | stage2_low_confidence | 0.011022 | ML: above threshold (no LLM available) — 0.011 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.011022 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | Carter Dunn Signing Out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052772 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MKETFA - Zoran from Metro called, electrical crew working on Milliken brakers. Should not affect the process. | FLAG | stage2_low_confidence | 0.0079867 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079867 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | Connor Smith signing in 3C Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041757 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | YWS + NYWS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | SHETCS, Activated D1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040025 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | STW12 - Place well 1 back in auto STW3 - Place well back in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004151 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054537 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | RHPSPA- Disch. Header Flow 1 LoLo. Duty just deactivated. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054264 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040442 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | Carter D Signing In, 4D/Clear | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041331 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | NMTKKC, Inlet Total Cl2 hihi//Inlet Combined Cl2 hihi, Res currently filling, Currently the header and the outlet are both reading normal, will continue to monitor, if residual continue to rise, will take corrective actions 18:24, After 2 readings, the residual came back down to normal levels. Residuals on the outlet and header analyzers still remained in normal range | FLAG | stage2_low_confidence | 0.011921 | ML: above threshold (no LLM available) — 0.012 |  | 0.011921 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | STETBR - Yash S on site for planned network upgrades. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0057887 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NMETIB - Alex B on site to test the flood alarm and complete the JHSC checks. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | ARPS- OCWA called (Tegbeer) and informed will be rotating Pumps/ from P6 to P5. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0052754 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | MAPS PD7 - Pump 3 man/off, VNPS PD7 Pump 3 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046748 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | EGMCDD - East Gwillimbury pressure lolo alarm. Checked site, valves are cycling between the 100mm line and the 250mm line. After valves rotated the alarms cleared. | FLAG | stage2_low_confidence | 0.0086394 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.0086394 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | KSSP - RAS combined no flow alarm. Checked site, RAS pumps have been placed manual/off by area operations. | FLAG | stage2_low_confidence | 0.0084517 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.0084517 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | QVW34 - Dan B and Kyle R on site to complete maintenance on well pump 4. Dan B will be cutting power to well pump 4 for the assigned work. Dan will eventually be working on well pump 3 but will coordinate with Will M as the pump is currently running manual for additional supply | FLAG | stage2_low_confidence | 0.012722 | ML: above threshold (no LLM available) — 0.013 |  | 0.012722 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | GWTP - ZW 5 membrane tank level lo and level switch lolo alarm. Alarm status quickly changed to normal. Checked site, tank is going through a backwash sequence. Alarms cleared on acknowledgement. Will monitor system. | FLAG | stage2_low_confidence | 0.01098 | ML: above threshold (no LLM available) — 0.011 | alarm [control_system]; alarms [control_system] | 0.01098 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | STW12/STW3 - Place both well 1 & 3 back in auto after zone 1 tower duty finished | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0053306 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | RHRSTR - activated Duty 1 to help with MARS level. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046113 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | BLW3 - Jack P requested pump 3 man/stop, back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0047149 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | VNPS- Noticed PD8 Pump 2 running in manual and duty 1 and duty 2 about to start up. Notified Benson S who is onsite. He will contact maintenance to inquire if they are running in it. Placed pump 4 (duty 2) pump in manual to prevent 3 pumps from running. 13:32- Benson S called back. Requested to place pump 2 back into auto. Also placed pump 4 duty 2 pump back into auto. | FLAG | stage2_low_confidence | 0.014183 | ML: above threshold (no LLM available) — 0.014 |  | 0.014183 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | STRS48 - Chlorinator 1 failed to close alarm on, switched to normal right away, alarm cleared when acknowledged. | FLAG | stage2_low_confidence | 0.012753 | ML: above threshold (no LLM available) — 0.013 | failed [equipment_failure]; alarm [control_system] | 0.012753 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | MKETFA- Miguel from YRP onsite for monthly visit. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.006051 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | NMW12 - Alex B on site for chlorine system inspection. AUPSRR - Donald M on site for chlorine system inspection. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040091 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | RHPSPA - Suction header Pressure Hi alarm, duty just deactivated. Quick spike, back to normal. | FLAG | stage2_low_confidence | 0.008186 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system] | 0.008186 | 0 | 0
2026-03 | 2026-03-18 | All Water System ROC General | ROC | STETBR - Low level alarm. Activated STW3 in manual mode as per the interim procedure. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059979 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | NMETIB - Inlet flow hi alarm. Checked system, NMVCBA is open more than usual and flows are high. Trending shows that flow through the valve slowed and the SCADA system opened the valve more to compensate but opened the valve too much. Monitoring site to ensure the flow returns to the setpoint. | FLAG | stage2_low_confidence | 0.020976 | ML: above threshold (no LLM available) — 0.021 | scada [control_system]; alarm [control_system] | 0.020976 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto mode. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0055122 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NBW5 - Influent Free chlorine residual alarm, quick spike. Alarm cleared in 4 minutes. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0059743 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | BLW34- Jack P called. Finished onsite. Running well in manual STW12- Heading to site for a chlorine cylinder change. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0051744 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | VNPSCD - Benson S completed work on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055033 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | NRETBR, AUETAD- Evgeny S working on OITs. Disregard Heartbeat Alarms. | FLAG | stage2_low_confidence | 0.0084436 | ML: above threshold (no LLM available) — 0.008 | alarm [control_system]; alarms [control_system] | 0.0084436 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | NBW2- Silicate Pump 2 Uncommanded Stop. Cleared alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0050018 | 0 | 0
2026-03 | 2026-03-16 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | Gluzen Ramos Ong signing out | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0054648 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | QVW34 - Eric S working on influent chlorine analyzer. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0046358 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | MAPS PD7 - Pump 2 man/off VNPS PD7 - Pump 1 to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0039271 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SEOC4 - Parth P on site for O2 sensor replacement. 11:58 Parth P and Rick L finished on site | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0037066 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | NMETYS- Alex B onsite filling eyewash. Disregard low pressure alarms that may trigger. | FLAG | stage2_low_confidence | 0.009142 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system]; alarms [control_system] | 0.009142 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | GWTP - GAC 4 flow control valve deviation alarm outstanding. Disregard alarm as per shift report. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0063141 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | STW3 - Placed well 3 pump back to auto. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.004409 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | YWS + NYWS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048829 | 0 | 0
2026-03 | 2026-03-23 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-25 | All Water System ROC General | ROC | JFPS - Cole W called to inform there is a new interim procedure to run JFPS pump 2 for one hour each day from March 26 - April 1. The duty is currently active for this pumping station. Placed pump 3 in manual and shut it down. Activated pump 2 in manual for one hour. | FLAG | stage2_low_confidence | 0.012944 | ML: above threshold (no LLM available) — 0.013 |  | 0.012944 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | YWS + NYWS Normal Christian Van Beek signing out. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0040295 | 0 | 0
2026-03 | 2026-03-22 | All Water System ROC General | ROC | Ethan U signing in Weather 5. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0034337 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NMW15 - Combine Chlorine Low alarm. Donnald M and Alex B working on site. Well 15 pump local/off, no water directed to users. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068085 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | QVW12 - Joe and Eric S finished on site and leaving. Joe D has returned the system to normal operations. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0055434 | 0 | 0
2026-03 | 2026-03-23 | All Water System ROC General | ROC | NMVCBA, Revert flow set point to 40L/sec from 80L/sec NMVCIB, Placed flow set point to 80L/sec from 40L/sec. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041931 | 0 | 0
2026-03 | 2026-03-24 | All Water System ROC General | ROC | NRETBR - Joe D and Christian B finished on site. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0056438 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | SHSP - Marcus R and Gavin W working/inspecting UV system. Disregard alarm for the duration of the work. | FLAG | stage2_low_confidence | 0.0086392 | ML: above threshold (no LLM available) — 0.009 | alarm [control_system] | 0.0086392 | 0 | 0
2026-03 | 2026-03-26 | All Water System ROC General | ROC | AURSBS- Ian W working on OIT. Disregard Heartbeat Alarm. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0068974 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | MAP7 - P3 back in auto VNP7 - P1 man/off | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0036968 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | JFPS - Lee F. doing pump testing on P1 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043949 | 0 | 0
2026-03 | 2026-03-27 | All Water System ROC General | ROC | QVW12 - Chlorine gas leak alarm and chlorine system emergency closure fault. Called Joe D to inform he will head to site. Joe D requested that on call instrumentation be informed. Called Eric S who will speak with Joe D and coordinate a fix. 15:34 - QVW12 - Eric S called and requested a CMU5. created CMU5#W11764578 #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; gas leak [critical]; fault [equipment_failure]; alarm [control_system]; leak [infrastructure] | emergency [critical]; gas leak [critical]; fault [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | KSTP - Conduit level lolo and filter 1 and filter level low alarms. The filters have interlocked on the lolo conduit level alarm. The low lift pump interlock has been cleared and the conduit level is rising. Once the conduit level passed the low alarm setpoint the filter interlock cleared and they initiated production. Called Jason G to inform of these system updates. Jason directed to clear alarms and call if anything else fails or faults. | FLAG | stage2_low_confidence | 0.058993 | ML: above threshold (no LLM available) — 0.059 | fault [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.058993 | 0 | 0
2026-03 | 2026-03-19 | All Water System ROC General | ROC | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA report | FLAG | stage2_low_confidence | 0.013702 | ML: above threshold (no LLM available) — 0.014 | fault [equipment_failure]; scada [control_system]; alarm [control_system] | 0.013702 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | MAPS- Placed PD7 Pump 2 in manual VNPS- Placed PD7 pump 2 in auto | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0041696 | 0 | 0
2026-03 | 2026-03-17 | All Water System ROC General | ROC | KSTP - Low lift Pump 3 uncomm stop alarm, PACL Pump 1 uncomm stop alarm. Duty switched to PACL Pump 2. Duty not active, plant not running. Emailed Central OP team. | FLAG | stage2_low_confidence | 0.016489 | ML: above threshold (no LLM available) — 0.016 | not running [equipment_failure]; alarm [control_system] | 0.016489 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | NBW37- Jacob M onsite working on leak on effluent chlorine analyzer. Disregard related alarms. | FLAG | stage2_low_confidence | 0.011615 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; alarms [control_system]; leak [infrastructure] | 0.011615 | 0 | 0
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | SHSP - Power Failure alarms came in. Checked site. Generator is running but site is still connected to hydro power. Informed Lauren S. SHSSDK - Control Panel Power Failure alarms came in along with pump 1 VFD fault. Control panel alarm cleared but VFD fault is outstanding. Called Lauren S. who is headed to site. CMU5 Created W11769394 #CMU5 #CONSULT | FLAG | stage2_low_confidence | 0.019693 | ML: above threshold (no LLM available) — 0.02 | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | 0.019693 | 0 | 0
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | EGSSSC - recirculation loop flow low and lowlow alarms. Flow control valve fault alarms and recirculation mode failure alarm. Station still operating, wet well cycling. Able to reset valve faults and recirculation flow alarms. Will monitor. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; failure [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-13 | All Wastewater System ROC General | ROC | Adeela Khan signing in. Weather: 0C and snowing | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0044729 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | YDSS+YNSS NORMAL | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048371 | 0 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | NMEQBP - Man/started Dewatering Pump 1. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0043996 | 0 | 0
2026-03 | 2026-03-05 | All Wastewater System ROC General | ROC | LSSS - Pump 1 fault came in. Place pump 1 man/off | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-03 | 2026-03-12 | All Wastewater System ROC General | ROC | KSSSQW - Kevin K has completed work and is leaving site. JDSS - Kevin K is headed to site to complete pump testing. Kevin has requested all alarms be disregarded until the work is complete. | FLAG | stage2_low_confidence | 0.010351 | ML: above threshold (no LLM available) — 0.01 | alarm [control_system]; alarms [control_system] | 0.010351 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal SUSSHS, Sewage Pump 1 no flow/VFD Fault, Notified Chris C, he is heading to site CMU5: W11760566 | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | fault [equipment_failure] | 0.0046102 | 0 | 0
2026-03 | 2026-03-26 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-24 | All Wastewater System ROC General | ROC | YDSS + YNSS Normal | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) |  | 0.0048948 | 0 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | NBSP - Mech Bar Screen oos alarm. Notified Young J. He will check NBSP - Inlet channel HiHi , High float alarms. Bar screen still OOS, Notified Yong J. He will check. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-18 | All Wastewater System ROC General | ROC | SHSP - Aeration blower 1 uncommanded start and stop alarm. Checked site, aeration blower 1 was not active when the alarms triggered. Aeration blower 2 was active when the alarms triggered and is still active and producing air flow. Able to reset alarms. | FLAG | stage2_low_confidence | 0.012729 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system]; alarms [control_system] | 0.012729 | 0 | 0
2026-03 | 2026-03-20 | All Water System ROC General | ROC | STETBR - Low level alarm. Man/started STW12 pump 1 and STW3 pump. | FLAG | stage2_uncertain | 0.45 | ML uncertain — flagged conservatively (no LLM) | alarm [control_system] | 0.0054941 | 0 | 0
2026-03 | 2026-03-13 | Aurora Henderson Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -Housekeeping, cleaned washroom -station okay | FLAG | stage2_low_confidence | 0.010326 | ML: above threshold (no LLM available) — 0.01 | scada [control_system] | 0.010326 | 0 | 0
2026-03 | 2026-03-04 | Aurora Henderson Sewage Pumping Station | WW-CEAST | On site to accommodate day 2 of wet well scum removal by WESSUC. Wet well scum cleaning complete without any issues. All pumps put back in service afterwards. | FLAG | stage2_low_confidence | 0.0079505 | ML: above threshold (no LLM available) — 0.008 |  | 0.0079505 | 0 | 0
2026-03 | 2026-03-12 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Put all 4 pumps in manual to fill the wet well up for running the 4 pumps - informed ROC (Christian) of what I'm up to. Ran each pump - P1= 66.9L/s@ 100% with 366Kpa as pressure, P2= 66.8L/s @ 100% with 352Kpa as pressure, P3= 67.7L/s @ 100% with a pressure of 366Kpa and P4= 63.8L/s @100% with 355Kpa as pressure. Pump actuators where activated when the pump turned on and all 4 check valves are good. Flushed the air valves and also checked the odour control unit - all good. Station back to normal ops - alarms cleared and I informed ROC. | FLAG | stage2_low_confidence | 0.12054 | ML: above threshold (no LLM available) — 0.121 | alarm [control_system]; alarms [control_system] | 0.12054 | 0 | 0
2026-03 | 2026-03-09 | Aurora Henderson Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -maintenance on site to top up oil in generator as oil is low, notified Capital of low oil in generator -station okay | FLAG | stage2_low_confidence | 0.013248 | ML: above threshold (no LLM available) — 0.013 | scada [control_system] | 0.013248 | 0 | 0
2026-03 | 2026-03-09 | Aurora Henderson Sewage Pumping Station | WW-CEAST | On site for generator low oil issues. Oil level show 1/4? under the low mark. We will return with the correct oil | FLAG | stage2_low_confidence | 0.013336 | ML: above threshold (no LLM available) — 0.013 |  | 0.013336 | 0 | 0
2026-03 | 2026-03-06 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station check of site Reviewed SCADA Entered data into SharePoint Inspected site Topped up glycol for heating system Fixed gate, as it was falling off hinges and dragging on ground Oil for generator is low, created WO for Maintenance, as it's a Natural gas generator it takes a different oil then our diesel generators, will hopefully get our contractor from Total Power to do an oil change for this generator, as it's new, it may have not been changed yet. Station okay | FLAG | stage2_low_confidence | 0.034676 | ML: above threshold (no LLM available) — 0.035 | scada [control_system] | 0.034676 | 0 | 0
2026-03 | 2026-03-20 | Aurora Henderson Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | FLAG | stage2_low_confidence | 0.010721 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010721 | 0 | 0
2026-03 | 2026-03-16 | Aurora Henderson Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -valve exercising -station okay | FLAG | stage2_low_confidence | 0.0096853 | ML: above threshold (no LLM available) — 0.01 | scada [control_system] | 0.0096853 | 0 | 0
2026-03 | 2026-03-23 | Aurora Henderson Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | FLAG | stage2_low_confidence | 0.010721 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010721 | 0 | 0
2026-03 | 2026-03-24 | Aurora Henderson Sewage Pumping Station | WW-CEAST | On site with CD/Lexsan/WSP to troubleshoot FM2_MV1. Lexsan confirmed spare wire within the actuator and connected it for SCADA. Tested in both Local/Remote no issues. WSP/CD also inspected surrounding fence and noted significant damages due to snowplow. This issue will be looked at this coming spring/summer. | FLAG | stage2_low_confidence | 0.020257 | ML: above threshold (no LLM available) — 0.02 | scada [control_system] | 0.020257 | 0 | 0
2026-03 | 2026-03-27 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Station check complete and the readings have been entered into the sharepoint | FLAG | stage2_low_confidence | 0.015844 | ML: above threshold (no LLM available) — 0.016 |  | 0.015844 | 0 | 0
2026-03 | 2026-03-17 | Aurora Henderson Sewage Pumping Station | WW-CEAST | On site to complete work orders. Wet well high level alarm test Wet well valve exercise Wet well inspection | FLAG | stage2_low_confidence | 0.020209 | ML: above threshold (no LLM available) — 0.02 | work order [maintenance_action]; alarm [control_system] | 0.020209 | 0 | 0
2026-03 | 2026-03-02 | Aurora Henderson Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -JHSC Inspection -Monthly Generator Test Run -started generator at 10:45, transfer successful, reset alarms on SCADA Generator Start Hours:81.6 Generator Stop Hours:82.8 Run Time:1.2 hrs -fuel cannot be accurately monitored as it's Natural Gas and is used for heating the building as well -generator stopped at 11:53 -test successful, on utility power -tested dry well flood alarm -assisted property services to fix broken gate, gate fixed -work completed -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system]; alarms [control_system] | flood [critical]; scada [control_system]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-03 | 2026-03-10 | Aurora Henderson Sewage Pumping Station | WW-CEAST | Picked up recommended oil for generator Added approximately 15 L of oil to bring to the full mark. Ran generator for one hour. No smoke or other issues noted. Allowed oil to return to oil pan approximately 20 minutes. Oil level is still at full. Complete. | FLAG | stage2_low_confidence | 0.016251 | ML: above threshold (no LLM available) — 0.016 | smoke [equipment_failure] | 0.016251 | 0 | 0
2026-03 | 2026-03-30 | Oak Ridges Air Management Facility | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Both fans running in auto. -All recirc pumps available and in auto. -Nutrient tank batch mixing completed, tank already full. | FLAG | stage2_low_confidence | 0.013071 | ML: above threshold (no LLM available) — 0.013 |  | 0.013071 | 0 | 0
2026-03 | 2026-03-10 | Oak Ridges Air Management Facility | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint) Both fans running in auto. One recirculation pump on duty from each train running in auto. Standby power generator available in auto. Nutrient Tank Batch Mixing - added 1/2 bag nutrient and topped up water from 5/8 to 7/8 level. Also on site, conducted special conditions testing together with contractors (CPD, NAC, AECOM and BIOREM) as part of the 14-day performance test. After the testing, cleared all alarms and put station back to normal operations. | FLAG | stage2_low_confidence | 0.057715 | ML: above threshold (no LLM available) — 0.058 | work order [maintenance_action]; alarm [control_system]; alarms [control_system] | 0.057715 | 0 | 0
2026-03 | 2026-03-20 | Oak Ridges Air Management Facility | WW-CEAST | -on site to assist Kyle Carlen and Jose Oliveira | FLAG | stage2_low_confidence | 0.01291 | ML: above threshold (no LLM available) — 0.013 |  | 0.01291 | 0 | 0
2026-03 | 2026-03-23 | Oak Ridges Air Management Facility | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint) Both fans running in auto. One recirculation pump on duty from each train running in auto. Standby power generator available in auto. Nutrient Tank Batch Mixing tank is full. | FLAG | stage2_low_confidence | 0.023224 | ML: above threshold (no LLM available) — 0.023 | work order [maintenance_action] | 0.023224 | 0 | 0
2026-03 | 2026-03-16 | Oak Ridges Air Management Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | FLAG | stage2_low_confidence | 0.010721 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010721 | 0 | 0
2026-03 | 2026-03-02 | Oak Ridges Air Management Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -NAC electrician's on site, reset faults on recirculation pumps, "current inbalance", pressed reset on panel -reset alarms on SCADA, no alarms present -station okay | FLAG | stage2_low_confidence | 0.026104 | ML: above threshold (no LLM available) — 0.026 | fault [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system] | 0.026104 | 0 | 0
2026-03 | 2025-03-19 | Nobleton WRRF |  | - Checked station and trends, and recorded readings on SharePoint - Reset exhaust fan 307 - Unclogged filter 1 north cell - Found flame failure alarm for the blower room. Notified TL - Smelled of gas near the makeup air unit above the headworks building. Notified TL and to create an Archibus - Reset plant water system - Assisted contractor for the noise study. Notified ROC that the generator will be turned on for the noise study. Turned on the generator at 11:41. Fuel level at 33 inch at start and once done, fuel level at 33 inch. Generator hours from 288.51 hrs to 289.18 hrs - Cleaned fly trap | FLAG | stage2_low_confidence | 0.41773 | ML: above threshold (no LLM available) — 0.418 | failure [equipment_failure]; noise [equipment_failure]; archibus [maintenance_action]; alarm [control_system]; clog [infrastructure]; clogged [infrastructure] | 0.41773 | 0 | 1
2026-03 | 2024-04-19 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - checked station and performed in-house lab, and recorded readings on SharePoint - reset plant water system due to high and low pressure alarm - gave a tour of the plant to the WiFi team - transferred sludge from the sludge thickening tank to the sludge holding tank - GFL picked up a sludge load - wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode. Placed WAS valves back to manual off | FLAG | stage2_low_confidence | 0.089435 | ML: above threshold (no LLM available) — 0.089 | alarm [control_system] | 0.089435 | 0 | 1
2026-03 | 2024-04-19 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - checked station and performed in-house lab, and recorded readings on SharePoint - reset plant water system due to high and low pressure alarm - gave a tour of the plant to the WiFi team - transferred sludge from the sludge thickening tank to the sludge holding tank - GFL picked up a sludge load - wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode. Placed WAS valves back to manual off | FLAG | stage2_low_confidence | 0.089435 | ML: above threshold (no LLM available) — 0.089 | alarm [control_system] | 0.089435 | 0 | 1
2026-03 | 2024-01-31 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - Collected weekly regulatory samples - Decanted then transferred sludge from the sludge thickening tank to the sludge holding tank - Performed station check and in-house lab, and recorded readings on SharePoint. Reset plant water system due to high and low pressure alarm. - Enabled RAS batch wasting mode at 8:13. Turned WAS valve 2 and 3 to auto. Turned WAS pumps 1 and 2 to auto. - Wasted 25m^3 from clarifier 1 and 25m^3 from clarifier 2 then rest RAS batch wasting mode at 12:00. Once done, turned WAS valve 2 and 3 to manual. Turned WAS pumps 1 and 2 to manual off. - Added 1 bag of soda ash each to aeration tank 1 and tank 2 - Performed DO probe maintenance after holding outputs at the aeration tank 1 and tank 2. Cleaned sensor and removed rags. Checked DO readings, all okay. Removed outputs once done - Removed floating solids or debris from aeration tank 1 and tank 2 surfaces - Removed rags from the aeration tank 1 and tank 2 outlet weir - Bled air from the condensation line at the aeration tank 1 and tank 2 | FLAG | stage2_classifier | 0.69182 | ML classifier: high issue probability (0.692) | regulatory [regulatory]; alarm [control_system] | 0.69182 | 0 | 1

## Cleared
source_month | EVENTDATE | DESCRIPTION | PERSONGROUP | LDTEXT | triage_decision | triage_stage | triage_score | triage_reason | matching_keywords | clf_proba | stage1_label | is_issue

## Known Issues
source_month | EVENTDATE | DESCRIPTION | PERSONGROUP | LDTEXT | triage_decision | triage_stage | triage_score | triage_reason | matching_keywords | clf_proba | stage1_label | is_issue
2026-02 | 2026-02-25 | Queensville West Sewage Pumping Station | WW-NORTH | On site to assist with replacement channel grinder, reconnection and testing. Channel grinder back in service. | FLAG | stage2_low_confidence | 0.01725 | ML: above threshold (no LLM available) — 0.017 |  | 0.01725 | 0 | 1
2026-02 | 2026-02-02 | Queensville West Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Equipment OOS: Channel grinder | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-10 | Queensville West Sewage Pumping Station | WW-NORTH | On site responding to Generator fault & LIT 3/4 OOR -Upon arrival, there was no power at the facility but the ATS panel was indicating we were connected to utility power with 600 V on each phase. Switched power to generator power but still the same issue. Although I was able to run a pump in local. -Appears there was a power blip which briefly caused the generator to start. The generator breaker tripped, along with MCC "Panel AA". The tripped MCC Panel AA was the culprit- once breaker was reset, facility power resumed and facility was operating normally. -It was found that the "duct heater"(1, 3, & 5) breaker in "distribution panel AA", was tripped and resetting this caused it to immediately trip again, subsequently tripping MCC "Panel AA". Work order for property services to address this issue will be created. -WWEL_LIT2 (wet well 1 hydrostatic level) began reading OOR once the other issue resolved. Instrumentation will respond to site to correct the issue. Equipment OOS: channel grinder and wet well 1 hydrostatic level | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; work order [maintenance_action] | fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-12 | Queensville West Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint On site to provide operational support for CPD performing pump vibration testing. Placed pumps in manual to increase the wet well level. Ran each pump in local at 52, 56, and 60 Hz separately and running together. Placed facility back to auto and observed normal operation. Equipment OOS: Channel grinder and WW1 hydrostatic transmitter | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; vibration [equipment_failure] | oos [equipment_failure]; vibration [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-09 | Queensville West Sewage Pumping Station | WW-NORTH | on site 1115hrs unable to time in on site, keeps requesting to time out, even though its timed out. station checks health and safety checks. ocu inspection, property services was on site. Heater in OCU room broken, property services looking for a new one to install. channel grinder oos. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-23 | Keswick Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry OCU oos (warranty) | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-12 | Keswick Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry OCU oos (warranty) | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-24 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to install the new limitork on pump 1 discharge valve. Supplier sent the wrong parts and will ship it asap | FLAG | stage2_low_confidence | 0.013449 | ML: above threshold (no LLM available) — 0.013 |  | 0.013449 | 0 | 1
2026-02 | 2026-02-23 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. Pumps 2,5 & 6 available in timed auto duty rotation every 3 hours. Pump #3 discharge valve for east forcemain is tripped. Unable to clear the 'hardware failure' status on the actuator. Maintenance will check this soon. Pumps 1,3 and 4 remain oos. Checked dry well. ok checked bar screens. changed out rag bins. All lines except 1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure] | failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-25 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. checked bar screens. switched out rag bins. All lines except no.1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-27 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Checked screen room. ok. Bypass sampling kit inspection completed. Odour control scrubber system inspection completed. All lines except no.1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; oos [equipment_failure] | bypass [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-02 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Hazardous Waste Collection and Removal Checked dry well. Checked bar screens. switched out rag bin. Added oil on the reservoir tank. All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; hazard [safety] | oos [equipment_failure]; hazard [safety] |  | 1 | 1
2026-02 | 2026-02-17 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to remove pump 4 for service, remove actuator from dump pad line one, and greased pump 3 force main discharge vale | FLAG | stage2_low_confidence | 0.014028 | ML: above threshold (no LLM available) — 0.014 |  | 0.014028 | 0 | 1
2026-02 | 2026-02-17 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to troubleshoot pump 4. Found main fuses blown. Checked motor, wiring, supply and control power. Suspect winding contamination. Removed cable entry lid. Found heavy contamination. Unwired pump so mechanics can remove pump. Pump 4 is out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-20 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bin in screen room -Pump 1 and 4 remain OOS -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-02 | 2026-02-11 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Weather today Snow and -1 Celsius -On site to complete work orders W11587339, W11586377. -Completed station check. -Entered station readings into SharePoint. -Air Compressors inspection. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Unclogged drain lines on screw conveyor 3. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; clog [infrastructure]; clogged [infrastructure] | sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 1
2026-02 | 2026-02-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to complete work orders. -Consolidated wet well inspection work order completed. -Tipping bucket operational checks completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Screw press dewatering compartment and drain line flushed. -Sluice gate valve exercises completed. -Wet well valve exercise completed. -Wet well inspection and cleaning completed. -Wet well high level alarm test completed and confirmed by ROC. -Surge tank inspection consolidated work order completed. -Surge tank and inspection completed. -Surge tank valve and actuator, exercise and inspection completed. -Surge tank drain valve inspection completed. -Transmission line flushing completed on both surge tanks. -Cleared all alarms generated from work orders. -Pumps 1 and 4 remain OOS. -Line 1 at the dump pad OOS for valve replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 1
2026-02 | 2026-02-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -on site at dump pad for line 3 valve overtorque -cleared line, valve was clogged with zip ties, a hauler keeps flushing zip ties and it is an issue -reset alarms on SCADA -line 2 and 3 available, 1 OOS for valve upgrades | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure] | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 1
2026-02 | 2026-02-20 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to work on pump 4. Continued troubleshooting electrical problem. Checked motor cables and power wiring. Sourced replacement fuse. Was able to power up MCC with motor disconnected. Fault history in Eaton Soft Starter indicated SCR shorted fault. Suspect soft starter failure. Need to source replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure]; scr shorted [equipment_failure] | fault [equipment_failure]; failure [equipment_failure]; scr shorted [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-04 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. JHSC Health and Safety Inspection completed. checked bar screens. Bar Screen Bin Removal and Replacement All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-06 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS. Cleared pump 3 E Disc Hdr MV4 alarm on scada. All standby power generators available in auto. Checked dry well. OK. Air dryers inspection and cleaning completed. checked screen room. OK. All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system] | oos [equipment_failure]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-07 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site in response to barscreen 1 overtorque alarm. Both barscreen OOS. Cleared screen 1 overtorque and attempted to run it in auto. Unit faulted out right away. Noticed rake has fallen near bottom sprocket in crooked position. Got ROC to call in Oncall CMS(Lee F) to site. Cleared overtorque for screen 2 and attempted to run it. Found rake is scratching the plate as it is travelling upwards creating loud screeching sound. Stopped the rake at the top. Lee F and I put screen 2 back in service after adjusting the position of the rake. Inlet gate to screen 2 has been open. Inlet gate to screen 1 has been closed. Notified ROC. Screen 1 OOS, screen 2 back in service | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put two bags of soda ash into the aeration tanks and set two up for later,, started de-cant pump and collected the comp samples from yesterdays samples and delivered them to Harry Walker. completed Lab work and wasted 10m3 and added 4 bags of soda ash in total. leaned out post aeration tank and the entry flow gates and also washed down the UV channel. Went through the station sand filters working well, Bar screen just went OOS (flowing through by pass bar screen) I have put in a WO for maintenance. OC unit is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-24 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put two bags in and set two bags up to put in later, and started de-cant pump. Flushed both sand filter reject lines also checked both clarifiers - oil level OK,I did NOT drain the water as I did that 2 weeks ago - same for the greasing. Went through the station - sand filters working good. The OC unit is still OOS put station is running under normal ops. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-23 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Shut off de-cant pump and emptied thickening tank into holding tank. Put two bags of soda ash into the aeration tanks and set up two for later. Pushed bin out for pick up and cleaned around the gates and also the post aeration tank - not much at all in the tank. Checked sand filter operation - all good. Station running under normal ops - no new issues were found , OC is still OOS | FLAG | stage2_low_confidence | 0.13509 | ML: above threshold (no LLM available) — 0.135 | oos [equipment_failure] | 0.13509 | 0 | 1
2026-02 | 2026-02-01 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site for lab analysis and sludge handling work. -Entered lab results into SharePoint. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -OCU remains OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-17 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put 2 bags of soda ash into the aeration tanks and set the next two up,, started the de-cant pump. went through the station - sand filters working good and i washed down the clarifiers scum trough. Cleaned out the post aeration tank and also the gates of the aeration inlet. Station running under normal ops - no issues were observed. Odour Control is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-12 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dropped in 2 bags of soda ash and set up 2 other bags for the aeration tanks also started de-cant pump. Started the Lab and sludge processing and entered results from the Lab into Sharepoint. Wasted 20m3 today and went through the Head works building - greased the travelling bar screen and cleaned out the back plate. Checked the vortex and both are turning. OC unit is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-11 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dumped two bags of soda ash into the aeration tank and set up the next two for later,, started de-cant pump and also collected weekly samples for the Lab,, Delivered samples to Harry Walker after collecting the samples at Mt. Albert PS. Back from drop off of the samples and checked all the cranes - all good and working. Went through the station and just the OC unit is still OOS. Rest of the station is running fine. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-10 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dumped 2 bags of soda ash intro the aeration tanks and set 2 up for later,, also started the de-cant pump. Went through the station - sand filters working great , set up hose and flushed both reject lines. checked blower room - all looks good and the air compressors as well. Station running under normal ops - no issues were found, OC unit is still OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-05 | Mount Albert Water Resource Recovery Facility | WW-CEAST | came to the plant and set up the soda ash and turned the de-cant pump on for Marcos,, went to the pumping station and back at 11,, cleaned out the post aeration tank and also the inlet channel gates as well,, went through the station and everything is running fine. OC unit is still OOS though. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed Lab work and sludge processing,, entered results from the Lab into Sharepoint. Did not waste today and added 4 bags of soda ash. Had Alum delivery today (16000L) and Orlando to pick up the sludge. Went through the station - sand filters are working good and RAZ pumps have good flow. OC unit is still OOS, | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-04 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Set up soda ash - put 2 bags in and 2 set up and waiting,, started de-cant pump and collected weekly samples for the Lab. After dropping off samples cleaned the scum trough - hosed it down till ice was gone. Went through the station and all looks good - Odour Control is still OOS but everything else looks good. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-25 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Placed the bar screen bin outside for removal. Bar screen 2 put back to service after maintenance worked on the over-torque fault. Air compressors inspection and cleaning completed. | FLAG | stage2_low_confidence | 0.039096 | ML: above threshold (no LLM available) — 0.039 | sso [critical]; fault [equipment_failure] | 0.039096 | 0 | 1
2026-02 | 2026-02-23 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Took station readings and entered into Sharepoint - reviewed trends - all good, levelled out bin in the screening room and bar screen 2 is OOS - not sure why (Chris) . Checked pump floor - all good . Emptied all the garbage and swept and mopped out both the office and the washroom. Station running under normal ops - just bar screen 2 OOS - I will find out more tomorrow. | FLAG | stage2_low_confidence | 0.10018 | ML: above threshold (no LLM available) — 0.1 | oos [equipment_failure] | 0.10018 | 0 | 1
2026-02 | 2026-02-25 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | -on site for bar screen 1 overtorque, reset bar screen, watched it travel, no issues, over torque occurs upon flinging rags, bar screen 1 back in service -bar screen 2 overtorque, screen 2 remains OOS with inlet gate closed, cannot be reset, WO created for maintenance | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; wo created [maintenance_action] | oos [equipment_failure]; wo created [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-07 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site in response to mech screen 2 overtorque. Cleared the alarm and ran the screen on hand, noticed rake was slightly to the left touching the plate as it is moving upwards. Called ROC to call in 2nd Ops to close the inlet gate to screen 2 Marcus R on site to assist. Closed inlet gate to screen 2 and put both inlet gates 1 and 2 in remote to be able to operate it remotely without entering wet well. Notified ROC Screen 2 placed OOS, Screen 1 operating as intended. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-27 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | FLAG | stage2_low_confidence | 0.010721 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010721 | 0 | 1
2026-02 | 2026-02-12 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | -On site to complete work orders. -Completed comprehensive housekeeping tasks. -Found outlet air line for OCU has completely torn off unit. Work request created. | FLAG | stage2_low_confidence | 0.02697 | ML: above threshold (no LLM available) — 0.027 | work order [maintenance_action] | 0.02697 | 0 | 1
2026-02 | 2026-02-11 | Vaughan Black Creek Pumping Station | WW-WEST | On site to troubleshoot disconnect switch for South Force Main Valve MV-11. Disconnect switch in internally corroded. Lubricated to allow the disconnect to close again. Tested disconnect function. Ok. Should be replace in the near future. | FLAG | stage2_low_confidence | 0.023682 | ML: above threshold (no LLM available) — 0.024 |  | 0.023682 | 0 | 1
2026-02 | 2026-02-20 | Vaughan Black Creek Pumping Station | WW-WEST | - Checked screen, oil is good. Levelled bin - Pushed bin back in - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 570.2 L/s, pressure 305 kPa Pump 2: 450 L/s at 100%, pressure 267 kPa Pump 3: 132.4 L/s at 100% speed, pressure 214 kPa Pump 4: 466 L/s at 100% speed, pressure 265 kPa - Checked station and recorded readings on SharePoint. Trends okay. Noticed high vibration on pump 1. Will monitor | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; vibration [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; vibration [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-10 | Vaughan Black Creek Pumping Station | WW-WEST | Checked station and trends, and recorded readings on SharePoint. Checked screen, all okay. Levelled bin Mopped floor | FLAG | stage2_low_confidence | 0.0091229 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091229 | 0 | 1
2026-02 | 2026-02-06 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check - no new issues reviewed trends and added data into SharePoint. Completed weekly RS pump run test - no new issues Pump1 -573.1L/s at 297kPa Pump 2 - 453.2 L/s at 100% at 262kPA Pump 3 131.3L/s at 100% and 215kPA Pump4 - 460.3 L/s at 100% at 265kPA Pump 5 -OOS pumps placed back into Auto and put in duty. Pump 5 remains in manual OOS Inspected seal water and cleaned screens - all clear and functioning. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-02 | Kleinburg Water Resource Recovery Facility | WW-WEST | On site for high fuel temperature alarm. Fuel system is cool. Cleared alarm 263. Unplugged sensor to confirm location of sensor. Alarm 263 came back in. Test ran generator okay Fuel was not overheating. Will order a fuel temperature sensor to replace. | FLAG | stage2_low_confidence | 0.012111 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; plugged [infrastructure] | 0.012111 | 0 | 1
2026-02 | 2026-02-23 | Schomberg Water Resource Recovery Facility | WW-WEST | Supernated STT and released to SHT. Completed labs and entered data in ace sheets. Completed station check. UV bank b, rack 7 not lighting up and causing alarm. Problem with power at the socket for rack 7. Created W11693400. Cleaned blower building. Cleaned UV/FE channel. | FLAG | stage2_low_confidence | 0.013464 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.013464 | 0 | 1
2026-02 | 2026-02-02 | Schomberg Water Resource Recovery Facility | WW-WEST | On site to continue work on effluent pump 3. Effluent pump 3 is still out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-08 | All Water System ROC General | ROC | 01:00 - EZ MAX ISSUES 01:35 - MKRSEM - Called Toronto Water (Brett) and requested to stop pumping to reservoir 02:00 - EZMAX Issues resolved | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-02 | 2026-02-26 | Markham Leslie Pumping Station | WW-CEAST | -on site for Housekeeping, cleaning up garbage around site on various floors -running pump 1 in auto duty 1, if it trips on bearing high temp, or another alarm, WO will be created, ongoing issues with pump 1 -completed alarm investigation -W11692845- Leslie Pump 1 High Bearing Temp Alarm created -station okay, only 5 pumps in auto/duty rotation, pump 1 OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: trip [equipment_failure]; oos [equipment_failure]; alarm [control_system] | trip [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-23 | Markham Leslie Pumping Station | WW-CEAST | Station Check completed (See details on SharePoint). Checked drywell. cleaned dry well area Checked screen room, changed out rag bin. Cleaned/hose down screen room. Switched pumps duty to timed mode from all-stop. Pumps 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. pump 1 faulted on 'stack overtemp' alarm. cleared the alarm. pump 2 seal water line has a pinhole leak. created work request W11683392 for maintenance to fix. Pump 1 & 2 taken oos. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; alarm [control_system]; leak [infrastructure] | sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 1
2026-02 | 2026-02-24 | Markham Leslie Pumping Station | WW-CEAST | -ran pump 1 with maintenance, upper bearing on pump is overheating -pump is manual off but available if needed to run -wet well consolidated work order completed -pump 2 was put OOS for the seal water, but back online before end of day -all 6 pumps can run, but pump 1 is manual off for the night, but available if needed -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-10 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Completed consolidated monthly dry well pump floor inspection work order. -Sump pit inspection completed. Tested Sump Level HiHi Alarm and confirmed with ROC. -Dry well flood alarm does not exist at this site, tested sump level HiHi in its place. -High low temp alarm does not exist at this site, temperatures tracked on BAS site. -BAS check completed. -Auto dialer test completed and confirmed with ROC. -Air compressor inspection completed, checked belts, oil, filters. -Seal water strainer checks completed. -Pump 1 OOS. -Pump 6 in auto duty rotation, but discharge valve is leaking, issue already reported to maintenance team. -Bar Screen 2 fault came in at 0928 this morning, reset fault and test ran screen for multiple cycles with no issues. Left bar screen 2 running in auto. Topped up oil on both bar screens. -RS Pump and Motor Inspection completed: -Pump 1 OOS -Pump 2: 1710L/s at 100% speed. -Pump 3: 1300L/s. -Pump 4: 1290L/s. -Pump 5: 1570L/s at 100% speed. -Pump 6: 1190L/s. -Check valve inspections completed. -Air relief valve inspections completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] | sso [critical]; flood [critical]; fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 1
2026-02 | 2026-02-11 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -entered data into sharepoint -inspected site -reviewed SCADA -notified ROC of work being performed -WAJAX on site for generator maintenance -YR maintenance and electrical on site for pump 1 repairs -generators started at 11:58 Generator 1: Start Hours:230.24 Stop Hours:231.42 Generator 2: Start Hours:117.40 Stop Hours:119.35 Generator 3: Start Hours:103.59 Stop Hours:105.54 Bulk Fuel Tank Start: 23,437L Fuel Stop: 22,572L -generator 1 went into shutdown due to low oil level, topped up oil, reset alarms, put generator 1 back to auto, generator started up and ran for remainder of 1 hour test run, sync/load shared with other generators Generator Run Time: 1.95 hrs -generators off at 13:52 -test successful, back on utility power, reset alarms -pump 1 remains OOS -all other pumps in auto and reset -Generator 1-3 Monthly Test Run -Hazard Waste Removal-no hazardous waste -Leslie Scrubber Inspection -bin replacement/screen room inspection -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] | oos [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] |  | 1 | 1
2026-02 | 2026-02-09 | Markham Leslie Pumping Station | WW-CEAST | Weather today Clear and -16 Celsius -On site to complete work orders W11579343. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure]; work order [maintenance_action] | sso [critical]; out of service [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-03 | 2026-03-04 | Sutton Water Resource Recovery Facility | WW-NORTH | Attending site to commission and verify the Lagoon Flowmeter - SUSP_SUSPLG_LGN_FIT1 (W11479921). Configured device, added asset number and verified function. ROC was notified before and after maintenance activities. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-28 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | TESTING NEW MAXIMO SYSTEM NOT REAL ENTRY PLEASE IGNORE REVISION 1 REVISION 2 | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-31 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Elog was down this morning March 31, 2026 Jason Garnett onsite from 7:45 am - 8:15 am Completed station and equipment check and weekly BacT sample W11705420 Took sample and grabs @ 7:55 am Total: 2.70 mg/l Free: 0.02 mg/l Analyzer matched grabs, reagents ok All other readings on PD sheets shared online folder ET Filling @ 20 l/s ET ops normal | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-30 | Queensville Wells No. 3 and 4 | CENTRAL | See photos/paper log book | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-05 | Nobleton Water Resource Recovery Facility | WW-WEST | - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint - Enabled RAS batch wasting mode at 10:08. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 13:47 - Plant water booster pump is cycling too much. This eventually causes pumps to fault on high and low pressure. This issue seems to have been going on for a while. Upon inspection, it seems RT1 and RT2 temperature protection relay faulted and is showing red. In addition, the discharge side fails to maintain adequate pressure while the plant water demand is low (vortex water scour not active at the time, no plant water usage from hydrant, etc). This is causing the pump to cycle on constantly to boost the pressure. The pressure tank seems to be okay with no leaks. Pressure switch differential settings seem okay. The check valve seems to be the culprit. I?ve tried to isolate the lead pump, pump 1, and the hissing sound stopped but the system still loses pressure fast. Therefore, it seems to be leaking on both sides. Created work order for maintenance and notified team - Received soda as delivery at 14:50. Received 250 bags. Signed all papers | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure]; leaking [infrastructure] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 1
2026-03 | 2026-03-06 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, flushed screw press drain lines, replaced bins following pick up. -Monthly JHSC H&S inspection completed, no issues noted. -Consolidated Dry Well Pump Floor Inspection completed. -RS pump & motor inspection completed. -Pump 1: 1310L/s. -Pump 2: 975L/s at 0% speed, 1230L/s at 25%, 1460L/s at 50%, 1860L/s at 100%. -Pump 3: 1310L/s. -Pump 4: 1290L/s. -Pump 5 OOS. -Pump 6: 1165L/s. -Check valve inspections completed. -Sump pit inspection completed. -Dry well flood alarm completed, Sump High High Level Alarm confirmed by ROC. -Air relief valve inspection completed. -Seal water strainer inspection completed. -Air compressor inspection completed. -BAS check completed. -Ran Pump 1 in auto duty 1 again until it failed again on Motor/Bearing High Temp Alarm. -Pumps 1 and 5 remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; failed [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] | sso [critical]; flood [critical]; failed [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-04 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, hosed down floor, repositioned screw press to better align with floor drain. -Bar screen bin removal completed. -Monthly diesel generator test run completed, readings entered into SharePoint. -1058 - Transferred site to generator power. -1241 - Transferred site back to utility power. -Gen. 1: Start hours: 231:42, Stop hours: 233:41, Run time: 1hr, 59min. -Gen. 2: Start hours: 119:35, Stop hours: 121:33, Run time: 1hr, 58min. -Gen. 3: Start hours: 105:54, Stop hours: 107:52, Run time: 1hr, 58min. -Hazardous waste collection and removal completed. -Overflow kit inspection completed. -Ran Pump 1 in auto, duty 1. Pump ran from 12:55-1450 before faulting again on Motor/Bearing High Temp Alarms. Left pump faulted and OOS for the night. -Pump 5 OOS with VFD Fault following generator testing. Work request created for issue. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; fault [equipment_failure]; faulted [equipment_failure]; faulting [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure]; pump fault [infrastructure]; hazard [safety] | overflow [critical]; fault [equipment_failure]; faulted [equipment_failure]; faulting [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure]; pump fault [infrastructure]; hazard [safety] |  | 1 | 1
2026-03 | 2026-03-02 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Reset Earth Fault on AHU1. -Reset Fault 47, Stack Overtemp Fault on Pump 1. -Test ran Pump 1 in auto, duty 1. Pump 1 ran for just under two hours before faulting again. Fault 47, Overtemp Fault back on Pump 1 MCC panel and SCADA is showing Fault Alarm, Motor/Bearing High Temp Alarm, and Motor/Bearing High Temp Trip Alarm. -Left Pump 1 in manual off, OOS for the night. -Hoist inspections completed on site, no issues noted. -Checked screen room, flushed screw press drain lines, replaced bins, cleaned floor in screen room. -Pump 1 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulting [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] | fault [equipment_failure]; faulting [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-27 | Markham Leslie Pumping Station | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Reset fault on Pump 1 and test run pump for maintenance team. -Checked screen room, changed out rag bin for the weekend, replaced bins following pick up, flushed screw press drain lines, bar screen oil topped up. -Assisted maintenance team with pump testing and maintenance activities. -Pump 1 is currently still running, but if it faults again it will remain OOS for the weekend. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure] | fault [equipment_failure]; oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-25 | Markham Leslie Pumping Station | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Ran Pump 1 in auto, duty 1 until pump faulted again. -Pump 1 remains OOS. -Rag bins placed out for pickup. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; pump fault [infrastructure] | sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; pump fault [infrastructure] |  | 1 | 1
2026-03 | 2026-03-10 | Markham Leslie Pumping Station | WW-CEAST | On site to check pump 5 VFD. Found auxiliary power fault. Was able to reset fault. Suspect it happened during power transfer last week. Operations tested pump 5 in manual. Pump is working ok. Pump 5 back in auto duty rotation. Also onsite to check generator 3. Local control panel screen was off. Found loose fuse holder on front of panel. Repaired. Screen is back on. No more issues. | FLAG | stage2_low_confidence | 0.12801 | ML: above threshold (no LLM available) — 0.128 | fault [equipment_failure]; oos [equipment_failure]; repair [maintenance_action] | 0.12801 | 0 | 1
2026-03 | 2026-03-09 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Washed Bayview Steeles OCF mist eliminator filters in screen room and left filters out to dry. -Checked screen room, changed out rag bin, flushed screw press drain lines, hosed down floor. -Odour control scrubber system inspection completed. Inspected filters, greased fan shaft in screen room OCU. -Station check completed, readings entered into SharePoint. -Bypass sampling kit inspection completed. -Ran Pump 1 in auto, duty 1 until Motor/Bearing High Temp Alarms came back in. -At 1132, Generator 3 Warning Alarm and Generator 3 DGC Not in Auto Alarm came in. Inspected Generator 3, found generator screen/panel blank, appears as though their is no power to Gen. 3 panel. Unable to reset alarms locally on generator or at GMCP panel. Work request created for issue. -Pump 1 and 5 OOS, Generator 3 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | bypass [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 1
2026-03 | 2026-03-28 | Ballantrae Well 1 & 2 | EAST | This is my first log entry! And now it's been updated! | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-28 | Ballantrae Well 3 | EAST | Time in: 08:10 On site to support contractor to repair the leak on chlorine solution line #2. Engaged E-Stop for chlorine booster pump 2. Depressurized the chlorine solution line 1&2. Contractor applied coatings on the leaky spot for line #2. I replaced the leaky ball valve on chlorine #1 line. Primed chlorine line #1. Tested chlorinator #1 vacuum, it responds well. Opened cylinders, tested chlorinators in local and remote, no issue. Man/Start well 3. Switched silicate pump to #2 to check it's operation, no issue. Verified chlorinator 1 performance, it is dosing at 50%, 25 ppd, vacuum = -90 mbar. Chlorine booster pump 1 discharge pressure = 210 psi. 09:33 verified chlorine analyzer readings: Grab influent = 2.15 mg/l, analyzer = 2.11 mg/l Grab effluent = 1.48 mg/l, analyzer = 1.51 mg/l. Will place well 3 to auto remotely. Time out: 09:55 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action]; leak [infrastructure] | oos [equipment_failure]; repair [maintenance_action]; leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-31 | Schomberg Elevated Tank | WEST | - on site to complete contingency entry | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-30 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, raked rag bin, bar screen oil topped up, cleaned rags off conveyors and floor. -Pump 4 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-02 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -pump 1 and 4 are OOS, 4 pumps available -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-03 | 2026-03-04 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -rotated bin in screen room -pumps 1 and 4 manual off, duty 7, maintenance working on them -on site for monthly work orders -Air Compressor Inspection -Air Dryer Inspection -JHSC Inspection -bins out for pickup, cleaned screen room -pump 1 back to auto duty 1, running with no issues -5 pumps available in auto, pump 4 OOS -backflushed line 2 at dump pad, cleared alarm, back to available -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] | sso [critical]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-03 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -on site for monthly work orders -Aurora SPS Consolidated Wetwell and Outfall Inspection -Monthly Surge Tank Inspection -Aurora EQ Tipping Bucket Test -outfall is okay, creek is well below duckbill -pump 1 was tested from the request of maintenance, leakage alarm came in, pump 1 is manual off, duty 7 -pump 4 is OOS -4 pumps available -Housekeeping of site, cleaned up garbage on all levels -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 1
2026-03 | 2026-03-18 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to complete work orders. -Alectra on site for hydro meter replacement. Discovered meter due for replacement was for solar power, so no disruption to station power is needed. -0855 - Transferred station to generator power. -Upon transfer to generator power, Generator 3 fuel filter primer cap blew out of the filter causing diesel fuel to spill onto ground. Immediately stopped Generator 3 and used absorbent pads to contain and clean up fuel spill. -0956 - Transferred site back to utility power. -Monthly diesel generator test run completed, readings entered into SharePoint. -Generator 1: Start: 629.3hrs, Stop: 630.4hrs, Run time: 1.1hrs. -Generator 2: Start: 621.5hrs, Stop: 622.6hrs, Run time: 1.1hrs. -Generator 3: Start: 825.3hrs, Stop 825.3hrs. -Generator 3 OOS until repairs can be made. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, changed out rag bin, bar screen oil topped up. -Bar screen rag bin removal completed, bins out for pick up. -Pump 4 OOS, Generator 3 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; sso [critical]; oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; absorbent pads [safety] | spill [critical]; sso [critical]; oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; absorbent pads [safety] |  | 1 | 1
2026-03 | 2026-03-23 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -rotated bin in screen room, cleaned screen room -reset pump 1 for discharge valve fault -pump 4 remains OOS, 5 pumps available -locked out and tagged out East Forcemain for gravity sewer cleaning south of Bloomington: all 6 pumps east discharge valves are in local stop, east surge tanks valve are closed and depowered, East forcemain common discharge valve is local closed, and depowered, ISS east discharge valve is local closed, in local stop -setpoints on SCADA show East is not in service, west forcemain is manually selected as in service -notified ROC and CEWW of East Forcemain OOS -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; scada [control_system] | fault [equipment_failure]; oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-03 | 2026-03-01 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site for sludge handling and lab analysis. -Added two bags of soda ash to each aeration tank. -Unable to decant STT. Hose has multiple holes right above connection to decant pump and is producing no flow. Emptied approximately 2m out of STT to make room for auto wasting tonight. -Raked manual bar screen. -Completed lab analysis and entered results into SharePoint. -Ran RAS pumps at 100% speed for several minutes. -Verified sand filter operation and alum dosing. -Cleaned solids off top of post aeration alum chamber. -Verified clarifier heater are both still running. -OCU and traveling screen remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Added two bags each of Soda Ash into each Aeration Tanks Removed rags from the sluice gates of Aeration Tanks Post Filtration/UV channel hose down. Clarifier #1 taken OOS due to gearbox issue. Emptying clarifier #1 now. Bar screen put back to service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-03 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to complete work orders. -Added two bags of soda ash to each aeration tank. -Raked manual bar screen. -Cleaned out RAS inlet chamber and post aeration alum chamber. Cleaned rags off aeration tank inlet gates and DO probes. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Monthly diesel generator test run completed, readings entered into SharePoint. -1013 - Transferred station to generator power. -1122 - Station transferred back to utility power. -Generator start hours: 492.3, stop hours: 493.5, run time: 1.2hrs. -Switched grit bins following pick up. -Clarifier scum system cleaning completed. Cleaned out clarifier scum troughs, hosed down walls of scum tank and ran Scum Pump 1 in local to pump out tank following cleaning. -Traveling screen and OCU remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-03 | 2026-03-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | put two bags of soda ash into the aeration tanks and set two up for later. Started grabbing samples for the Lab and Daniel had switched WO to Kevin,, went through the station and sand filters working great and started de-cant pump. Clarifier 1 arm stopped turning, got a hold of Bill (maintenance) and he's on his way. Cleaned out the post aeration tank as well as the inlet gates while waiting. There was no Hazardous waste to dispose of and went through the weekly alarm management for EOC and YDOC and there were no changes to either site. Started emptying clarifier #1 due to gear box in motor is broken - Daniel showed up and walked us through switching everything over. Continued draining for two hours and i'll be in on the weekend to complete. Bill and Terry - maintenance got the bar screen working again so we closed off the by-pass and now flow is going through the bar screen. Clarifier 1 is down but the rest of the station is running fine. | FLAG | stage2_low_confidence | 0.57583 | ML: above threshold (no LLM available) — 0.576 | alarm [control_system]; hazard [safety] | 0.57583 | 0 | 1
2026-03 | 2026-03-13 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint). STT decanted, afterwards remaining sludge dumped into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Weekly alarm management - only clarifier 1 no RAS pump running is the alarm due to clarifier 1 out of service. Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system] | out of service [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-19 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put in 2 bags of soda ash and set 2 up for later,, Kevin started de-cant pump and then I worked with Kevin on his Lab work to speed it up and get a lot more organized. Went through the station, UV bank 1 is OOS - sand filters working great. Checked the hoist in the aeration room and the sand filter room - all good. Cleaned out the post aeration tank and the inlet channel gates, Washed down the UV channel and shut down the effluent pumps for the night to make sure we have no breaks again. Hopefully this helped Kevin out with his Lab work, UV 1 is OOS along with clarifier 1 the rest of the station is running fine. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-23 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put 4 bags of soda ash in and started de-cant pump,, Daniel and I isolated the inlet at the headworks and are diverting flow to the lagoon (@ approx. 08:25 ) Put 3 knife gates in place to re-direct flow to the lagoon. Accuworxs here and are pumping down post aeration tank, Retrieved the grating at approx. 14:00 hrs and then put the station back to normal ops by removing gates from the headworks. Station back to normal ops - clarifier 1 and UV bank 1A are still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to complete work orders. -GFL/Accuworx on site for Clarifier 1 cleaning. -Two bags of soda ash added to each aeration tank. -Cleaned out RAS inlet chamber and post aeration alum mixing chamber. -Mechanics and electricians have completed repair work on Clarifier 1. Clarifier 1 locked out at local disconnect with station lock until clarifier cleaning is completed. -Worked on UV room cleaning. Removed old/broken items. Cleaned floors. -UV Bank 1A OOS, Clarifier 1 OOS, RAS Pump 3 OOS, WAS Pump 2 OOS, OCU OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] | oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] |  | 1 | 1
2026-03 | 2026-03-31 | Mount Albert Pumping Station | WW-CEAST | -On site to respond to communications failure alarm reported by ROC. PCS on-call has also been notified and is on route to site. -0405 - Upon arrival to site, swipe card reader not working, local SCADA OIT panel is blank and not working, Pumps both displaying No Communication faults on panels. Wet well level is at 4.08m. Tried resetting pump faults on local panel, but pumps will not run in remote or local. Wet well backup mode is in Auto, but pumps not running. -Called on-call electrician, tried cycling power to pumps, but still not working. Tried disconnecting power for 5-10min, but pumps still not working when turned back on. On-call electrician on route to site. -0431 - Contacted ROC to initiate emergency vac truck procedure and have trucks dispatched to site. -Tried transferring site to generator power, suspecting possible phase loss on site. Unable to get generator to turn on, e-key not working on any locks on site. -Briefly left site to bump e-key at MTA WRRF. When back on site, e-key still not working. Cut lock to generator building. Generator screen is blank and unresponsive. Generator will not run in remote or manual. -0512 - Wessuc confirmed they have vac truck and tanker on route to site. -Electricians and PCS arrived at site and found multiple damaged pieces of equipment due to a suspected lightning strike on the building. They immediately began work to restore functionality of damaged equipment. -0631 - Wessuc informed of delays and that they were still approximately 1.5hrs away. -0645 - Informed SAC of ongoing spill. Spoke with environmental officer Edhilvia Campos and was assigned event# 1QG1QRG. -0655 - Informed York Region local health unit of ongoing spill. Spoke with health officer David Huang. -0700 - Notified LSCRA of ongoing spill. -0815 - Wessuc arrived on site and began setting up hoses to pump down wet well. Began pumping down wet well at approximately 0830. -0830 - Collected spill samples with Chris Rodie, CoC# W11769441. -0925 - Electricians able to get one pump running on site and began pumping down wet well to forcemain along with Wessuc pumping wet well to vac truck. -0957 - Wet well at 3.99m, below the overflow level. Spill has ended. -Kevin Shaji arrived at site to complete weekly sample collection. -When Wessuc had completed their emergency wet well pumping activities, accompanied vac truck to site of spill, which was a local East Gwillimbury manhole between the southeast corner of the Foodland parking lot and the railroad tracks. Wessuc cleaned solids and liquid from surrounding area, as well as removed excess solids from local sewer. While on site, visited by local Public Heath Inspector Darja Montsenko, who also observed spill location during cleanup and afterwards. -Instrumentation team on site to replace damaged flowmeter and level sensor. -Electricians and PCS team able to get both station pumps repaired and operational in auto. -Temporary generator set up on site and tested in manual and in auto, with a full station transfer test. -Composite sampler reset for 0700 April 7, 2026. Sample jug cleaned. -Security system and swipe card reader on site not working. Informed supervisor of issue and work request created. -Station is back running normally. Temporary generator set up on site. Both pumps available and in local. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; spill [critical]; emergency [critical]; lightning strike [critical]; fault [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; not working [equipment_failure]; repair [maintenance_action]; environmental officer [regulatory]; health unit [regulatory]; spill sample [regulatory]; scada [control_system]; alarm [control_system]; no communication [control_system]; overflow [infrastructure]; backup [infrastructure]; pump fault [infrastructure] | overflow [critical]; spill [critical]; emergency [critical]; lightning strike [critical]; fault [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; not working [equipment_failure]; repair [maintenance_action]; environmental officer [regulatory]; health unit [regulatory]; spill sample [regulatory]; scada [control_system]; alarm [control_system]; no communication [control_system]; overflow [infrastructure]; backup [infrastructure]; pump fault [infrastructure] |  | 1 | 1
2026-03 | 2026-03-31 | Mount Albert Pumping Station | WW-CEAST | Attending site to replace wetwell level transmitter and flowmeter (W11769917). Devices were damaged due to electrical storm. Replaced, configured and tested wetwell level transmitter with Art. Parth and Rick replaced and configured discharge flowmeter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-31 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | @8:25 - Placed pumps 1 and 3 OOS in manual off to leave 2 other pumps running in auto and in manual speed of 30% to slow down flow to Aurora SPS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-18 | Kleinburg Water Resource Recovery Facility | WW-WEST | Supernated STT and released to SHT. Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:49. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Autowasting volumes are correct with waste pumps in auto speed. Added 8 bags to soda ash hopper. Completed housekeeping work order for headworks building. Completed DO probe maintenance. Created work order (W11744156) for service water pipe in need of re-securing to wall in headworks. | FLAG | stage2_low_confidence | 0.026213 | ML: above threshold (no LLM available) — 0.026 | work order [maintenance_action] | 0.026213 | 0 | 1
2026-03 | 2026-03-31 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Dropped off Kleinburg WRRF weekly compliance samples -Created contingency entry due to EZmax mobile error. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) | compliance [regulatory] |  | 0 | 1
2026-03 | 2026-03-23 | Schomberg Water Resource Recovery Facility | WW-WEST | On site for blower 1 oil leak. We will return with seals | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-17 | Schomberg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WO. Notified ROC. Completed Consolidated Aer., Sludge and Vortex Blower Inspections. Topped Up Oil Reservoirs and Replaced Air Filters Where Necessary. All Belts OK. Returned to Service and Cleared Associated Alarms. Created Follow-Up WO Regarding Aer. Blower #1 Oil Leak for Maint. ?> W11740816. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; follow-up [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | sso [critical]; follow-up [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-18 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Batch wasted 51m3 overnight Cleaned the DO probes Aeration blower 1 cooling fan faulted and cannot be reset Blower 1 is currently left out of service | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure] | fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-28 | All Water System ROC General | ROC | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, weather: -1C and sun. Please see attached photos of the paper logbooks. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Maximo server down from 10-16:00. Attached are logbook entries | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-31 | All Water System ROC General | ROC | EZ Max Mobile Access Restored Mar/31/2026 04:00 - 06:45 | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, Weather: -1C and sun. Please see attached photos of the paper logbooks. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Maximo down between 10:00 and 16:00. Attached is pictured of logbook entries | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | Contingency Log, March 31, 0400 to 0645, eLogs were down. Attached are the paper logs for that time stamp | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2025-03-19 | Nobleton WRRF |  | - Checked station and trends, and recorded readings on SharePoint - Reset exhaust fan 307 - Unclogged filter 1 north cell - Found flame failure alarm for the blower room. Notified TL - Smelled of gas near the makeup air unit above the headworks building. Notified TL and to create an Archibus - Reset plant water system - Assisted contractor for the noise study. Notified ROC that the generator will be turned on for the noise study. Turned on the generator at 11:41. Fuel level at 33 inch at start and once done, fuel level at 33 inch. Generator hours from 288.51 hrs to 289.18 hrs - Cleaned fly trap | FLAG | stage2_low_confidence | 0.41773 | ML: above threshold (no LLM available) — 0.418 | failure [equipment_failure]; noise [equipment_failure]; archibus [maintenance_action]; alarm [control_system]; clog [infrastructure]; clogged [infrastructure] | 0.41773 | 0 | 1
2026-03 | 2024-04-19 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - checked station and performed in-house lab, and recorded readings on SharePoint - reset plant water system due to high and low pressure alarm - gave a tour of the plant to the WiFi team - transferred sludge from the sludge thickening tank to the sludge holding tank - GFL picked up a sludge load - wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode. Placed WAS valves back to manual off | FLAG | stage2_low_confidence | 0.089435 | ML: above threshold (no LLM available) — 0.089 | alarm [control_system] | 0.089435 | 0 | 1
2026-03 | 2024-04-19 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - checked station and performed in-house lab, and recorded readings on SharePoint - reset plant water system due to high and low pressure alarm - gave a tour of the plant to the WiFi team - transferred sludge from the sludge thickening tank to the sludge holding tank - GFL picked up a sludge load - wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode. Placed WAS valves back to manual off | FLAG | stage2_low_confidence | 0.089435 | ML: above threshold (no LLM available) — 0.089 | alarm [control_system] | 0.089435 | 0 | 1
2026-03 | 2024-01-31 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - Collected weekly regulatory samples - Decanted then transferred sludge from the sludge thickening tank to the sludge holding tank - Performed station check and in-house lab, and recorded readings on SharePoint. Reset plant water system due to high and low pressure alarm. - Enabled RAS batch wasting mode at 8:13. Turned WAS valve 2 and 3 to auto. Turned WAS pumps 1 and 2 to auto. - Wasted 25m^3 from clarifier 1 and 25m^3 from clarifier 2 then rest RAS batch wasting mode at 12:00. Once done, turned WAS valve 2 and 3 to manual. Turned WAS pumps 1 and 2 to manual off. - Added 1 bag of soda ash each to aeration tank 1 and tank 2 - Performed DO probe maintenance after holding outputs at the aeration tank 1 and tank 2. Cleaned sensor and removed rags. Checked DO readings, all okay. Removed outputs once done - Removed floating solids or debris from aeration tank 1 and tank 2 surfaces - Removed rags from the aeration tank 1 and tank 2 outlet weir - Bled air from the condensation line at the aeration tank 1 and tank 2 | FLAG | stage2_classifier | 0.69182 | ML classifier: high issue probability (0.692) | regulatory [regulatory]; alarm [control_system] | 0.69182 | 0 | 1