## Monthly Summary
Month | Set | Total Logs | True Issues | Issue Rate % | Recall | Precision | False Negatives | True Positives | False Positives | FN Rate | Flags to Human | Logs Cleared | Workload Reduction %
2025-10 | TRAIN | 5018 | 50 | 1 | 1 | 0.01 | 0 | 50 | 4968 | 0 | 5018 | 0 | 0
2025-11 | TRAIN | 4560 | 47 | 1.03 | 1 | 0.0103 | 0 | 47 | 4513 | 0 | 4560 | 0 | 0
2025-12 | TRAIN | 4683 | 84 | 1.79 | 1 | 0.0179 | 0 | 84 | 4599 | 0 | 4683 | 0 | 0
2026-01 | TRAIN | 4573 | 53 | 1.16 | 1 | 0.0116 | 0 | 53 | 4520 | 0 | 4573 | 0 | 0
2026-02 | VAL | 4354 | 53 | 1.22 | 1 | 0.0122 | 0 | 53 | 4301 | 0 | 4354 | 0 | 0
2026-03 | TEST | 4962 | 47 | 0.95 | 1 | 0.0095 | 0 | 47 | 4915 | 0 | 4962 | 0 | 0

## Top Issue Terms
Rank | Term | Issue Score
1 | oos | 0.0089
2 | ras | 0.0087
3 | screen | 0.0081
4 | aeration | 0.0073
5 | ras pump | 0.0065
6 | aeration tank | 0.0062
7 | tank | 0.006
8 | bar | 0.0059
9 | clarifier | 0.0058
10 | sludge | 0.0057
11 | bar screen | 0.0055
12 | into sharepoint | 0.0051
13 | lab | 0.0049
14 | uv | 0.0047
15 | pump | 0.0046
16 | channel | 0.0045
17 | sharepoint | 0.0044
18 | order | 0.0044
19 | to each aeration | 0.0044
20 | each aeration | 0.0043
21 | service | 0.0042
22 | added | 0.0042
23 | air | 0.0042
24 | was pump | 0.0041
25 | screen room | 0.004

## Stage Breakdown
Stage | Total | Flagged | Cleared | True Issues in Group
stage1_contingency | 9 | 9 | 0 | 9
stage1_keyword | 1037 | 1037 | 0 | 72
stage2_classifier | 3 | 3 | 0 | 1
stage2_low_confidence | 3150 | 3150 | 0 | 18
stage2_uncertain | 5117 | 5117 | 0 | 0

## Issues Caught (Val+Test)
source_month | EVENTDATE | DESCRIPTION | PERSONGROUP | LDTEXT | triage_decision | triage_stage | triage_score | triage_reason | matching_keywords | clf_proba | stage1_label | is_issue
2026-02 | 2026-02-25 | Queensville West Sewage Pumping Station | WW-NORTH | On site to assist with replacement channel grinder, reconnection and testing. Channel grinder back in service. | FLAG | stage2_low_confidence | 0.01725 | ML: above threshold (no LLM available) — 0.017 |  | 0.01725 | 0 | 1
2026-02 | 2026-02-02 | Queensville West Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Equipment OOS: Channel grinder | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-10 | Queensville West Sewage Pumping Station | WW-NORTH | On site responding to Generator fault & LIT 3/4 OOR -Upon arrival, there was no power at the facility but the ATS panel was indicating we were connected to utility power with 600 V on each phase. Switched power to generator power but still the same issue. Although I was able to run a pump in local. -Appears there was a power blip which briefly caused the generator to start. The generator breaker tripped, along with MCC "Panel AA". The tripped MCC Panel AA was the culprit- once breaker was reset, facility power resumed and facility was operating normally. -It was found that the "duct heater"(1, 3, & 5) breaker in "distribution panel AA", was tripped and resetting this caused it to immediately trip again, subsequently tripping MCC "Panel AA". Work order for property services to address this issue will be created. -WWEL_LIT2 (wet well 1 hydrostatic level) began reading OOR once the other issue resolved. Instrumentation will respond to site to correct the issue. Equipment OOS: channel grinder and wet well 1 hydrostatic level | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; work order [maintenance_action] | fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-12 | Queensville West Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint On site to provide operational support for CPD performing pump vibration testing. Placed pumps in manual to increase the wet well level. Ran each pump in local at 52, 56, and 60 Hz separately and running together. Placed facility back to auto and observed normal operation. Equipment OOS: Channel grinder and WW1 hydrostatic transmitter | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; vibration [equipment_failure] | oos [equipment_failure]; vibration [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-09 | Queensville West Sewage Pumping Station | WW-NORTH | on site 1115hrs unable to time in on site, keeps requesting to time out, even though its timed out. station checks health and safety checks. ocu inspection, property services was on site. Heater in OCU room broken, property services looking for a new one to install. channel grinder oos. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-23 | Keswick Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry OCU oos (warranty) | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-12 | Keswick Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry OCU oos (warranty) | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-24 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to install the new limitork on pump 1 discharge valve. Supplier sent the wrong parts and will ship it asap | FLAG | stage2_low_confidence | 0.013449 | ML: above threshold (no LLM available) — 0.013 |  | 0.013449 | 0 | 1
2026-02 | 2026-02-23 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. Pumps 2,5 & 6 available in timed auto duty rotation every 3 hours. Pump #3 discharge valve for east forcemain is tripped. Unable to clear the 'hardware failure' status on the actuator. Maintenance will check this soon. Pumps 1,3 and 4 remain oos. Checked dry well. ok checked bar screens. changed out rag bins. All lines except 1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure] | failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-25 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. checked bar screens. switched out rag bins. All lines except no.1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-27 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Checked screen room. ok. Bypass sampling kit inspection completed. Odour control scrubber system inspection completed. All lines except no.1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; oos [equipment_failure] | bypass [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-02 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Hazardous Waste Collection and Removal Checked dry well. Checked bar screens. switched out rag bin. Added oil on the reservoir tank. All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; hazard [safety] | oos [equipment_failure]; hazard [safety] |  | 1 | 1
2026-02 | 2026-02-17 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to remove pump 4 for service, remove actuator from dump pad line one, and greased pump 3 force main discharge vale | FLAG | stage2_low_confidence | 0.014028 | ML: above threshold (no LLM available) — 0.014 |  | 0.014028 | 0 | 1
2026-02 | 2026-02-17 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to troubleshoot pump 4. Found main fuses blown. Checked motor, wiring, supply and control power. Suspect winding contamination. Removed cable entry lid. Found heavy contamination. Unwired pump so mechanics can remove pump. Pump 4 is out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-20 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bin in screen room -Pump 1 and 4 remain OOS -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-02 | 2026-02-11 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Weather today Snow and -1 Celsius -On site to complete work orders W11587339, W11586377. -Completed station check. -Entered station readings into SharePoint. -Air Compressors inspection. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Unclogged drain lines on screw conveyor 3. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; clog [infrastructure]; clogged [infrastructure] | sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 1
2026-02 | 2026-02-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to complete work orders. -Consolidated wet well inspection work order completed. -Tipping bucket operational checks completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Screw press dewatering compartment and drain line flushed. -Sluice gate valve exercises completed. -Wet well valve exercise completed. -Wet well inspection and cleaning completed. -Wet well high level alarm test completed and confirmed by ROC. -Surge tank inspection consolidated work order completed. -Surge tank and inspection completed. -Surge tank valve and actuator, exercise and inspection completed. -Surge tank drain valve inspection completed. -Transmission line flushing completed on both surge tanks. -Cleared all alarms generated from work orders. -Pumps 1 and 4 remain OOS. -Line 1 at the dump pad OOS for valve replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 1
2026-02 | 2026-02-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -on site at dump pad for line 3 valve overtorque -cleared line, valve was clogged with zip ties, a hauler keeps flushing zip ties and it is an issue -reset alarms on SCADA -line 2 and 3 available, 1 OOS for valve upgrades | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure] | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 1
2026-02 | 2026-02-20 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to work on pump 4. Continued troubleshooting electrical problem. Checked motor cables and power wiring. Sourced replacement fuse. Was able to power up MCC with motor disconnected. Fault history in Eaton Soft Starter indicated SCR shorted fault. Suspect soft starter failure. Need to source replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure]; scr shorted [equipment_failure] | fault [equipment_failure]; failure [equipment_failure]; scr shorted [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-04 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. JHSC Health and Safety Inspection completed. checked bar screens. Bar Screen Bin Removal and Replacement All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-06 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS. Cleared pump 3 E Disc Hdr MV4 alarm on scada. All standby power generators available in auto. Checked dry well. OK. Air dryers inspection and cleaning completed. checked screen room. OK. All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system] | oos [equipment_failure]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-07 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site in response to barscreen 1 overtorque alarm. Both barscreen OOS. Cleared screen 1 overtorque and attempted to run it in auto. Unit faulted out right away. Noticed rake has fallen near bottom sprocket in crooked position. Got ROC to call in Oncall CMS(Lee F) to site. Cleared overtorque for screen 2 and attempted to run it. Found rake is scratching the plate as it is travelling upwards creating loud screeching sound. Stopped the rake at the top. Lee F and I put screen 2 back in service after adjusting the position of the rake. Inlet gate to screen 2 has been open. Inlet gate to screen 1 has been closed. Notified ROC. Screen 1 OOS, screen 2 back in service | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put two bags of soda ash into the aeration tanks and set two up for later,, started de-cant pump and collected the comp samples from yesterdays samples and delivered them to Harry Walker. completed Lab work and wasted 10m3 and added 4 bags of soda ash in total. leaned out post aeration tank and the entry flow gates and also washed down the UV channel. Went through the station sand filters working well, Bar screen just went OOS (flowing through by pass bar screen) I have put in a WO for maintenance. OC unit is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-24 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put two bags in and set two bags up to put in later, and started de-cant pump. Flushed both sand filter reject lines also checked both clarifiers - oil level OK,I did NOT drain the water as I did that 2 weeks ago - same for the greasing. Went through the station - sand filters working good. The OC unit is still OOS put station is running under normal ops. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-23 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Shut off de-cant pump and emptied thickening tank into holding tank. Put two bags of soda ash into the aeration tanks and set up two for later. Pushed bin out for pick up and cleaned around the gates and also the post aeration tank - not much at all in the tank. Checked sand filter operation - all good. Station running under normal ops - no new issues were found , OC is still OOS | FLAG | stage2_low_confidence | 0.13509 | ML: above threshold (no LLM available) — 0.135 | oos [equipment_failure] | 0.13509 | 0 | 1
2026-02 | 2026-02-01 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site for lab analysis and sludge handling work. -Entered lab results into SharePoint. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -OCU remains OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-17 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put 2 bags of soda ash into the aeration tanks and set the next two up,, started the de-cant pump. went through the station - sand filters working good and i washed down the clarifiers scum trough. Cleaned out the post aeration tank and also the gates of the aeration inlet. Station running under normal ops - no issues were observed. Odour Control is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-12 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dropped in 2 bags of soda ash and set up 2 other bags for the aeration tanks also started de-cant pump. Started the Lab and sludge processing and entered results from the Lab into Sharepoint. Wasted 20m3 today and went through the Head works building - greased the travelling bar screen and cleaned out the back plate. Checked the vortex and both are turning. OC unit is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-11 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dumped two bags of soda ash into the aeration tank and set up the next two for later,, started de-cant pump and also collected weekly samples for the Lab,, Delivered samples to Harry Walker after collecting the samples at Mt. Albert PS. Back from drop off of the samples and checked all the cranes - all good and working. Went through the station and just the OC unit is still OOS. Rest of the station is running fine. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-10 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dumped 2 bags of soda ash intro the aeration tanks and set 2 up for later,, also started the de-cant pump. Went through the station - sand filters working great , set up hose and flushed both reject lines. checked blower room - all looks good and the air compressors as well. Station running under normal ops - no issues were found, OC unit is still OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-05 | Mount Albert Water Resource Recovery Facility | WW-CEAST | came to the plant and set up the soda ash and turned the de-cant pump on for Marcos,, went to the pumping station and back at 11,, cleaned out the post aeration tank and also the inlet channel gates as well,, went through the station and everything is running fine. OC unit is still OOS though. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed Lab work and sludge processing,, entered results from the Lab into Sharepoint. Did not waste today and added 4 bags of soda ash. Had Alum delivery today (16000L) and Orlando to pick up the sludge. Went through the station - sand filters are working good and RAZ pumps have good flow. OC unit is still OOS, | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-04 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Set up soda ash - put 2 bags in and 2 set up and waiting,, started de-cant pump and collected weekly samples for the Lab. After dropping off samples cleaned the scum trough - hosed it down till ice was gone. Went through the station and all looks good - Odour Control is still OOS but everything else looks good. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-25 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Placed the bar screen bin outside for removal. Bar screen 2 put back to service after maintenance worked on the over-torque fault. Air compressors inspection and cleaning completed. | FLAG | stage2_low_confidence | 0.039096 | ML: above threshold (no LLM available) — 0.039 | sso [critical]; fault [equipment_failure] | 0.039096 | 0 | 1
2026-02 | 2026-02-23 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Took station readings and entered into Sharepoint - reviewed trends - all good, levelled out bin in the screening room and bar screen 2 is OOS - not sure why (Chris) . Checked pump floor - all good . Emptied all the garbage and swept and mopped out both the office and the washroom. Station running under normal ops - just bar screen 2 OOS - I will find out more tomorrow. | FLAG | stage2_low_confidence | 0.10018 | ML: above threshold (no LLM available) — 0.1 | oos [equipment_failure] | 0.10018 | 0 | 1
2026-02 | 2026-02-25 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | -on site for bar screen 1 overtorque, reset bar screen, watched it travel, no issues, over torque occurs upon flinging rags, bar screen 1 back in service -bar screen 2 overtorque, screen 2 remains OOS with inlet gate closed, cannot be reset, WO created for maintenance | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; wo created [maintenance_action] | oos [equipment_failure]; wo created [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-07 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site in response to mech screen 2 overtorque. Cleared the alarm and ran the screen on hand, noticed rake was slightly to the left touching the plate as it is moving upwards. Called ROC to call in 2nd Ops to close the inlet gate to screen 2 Marcus R on site to assist. Closed inlet gate to screen 2 and put both inlet gates 1 and 2 in remote to be able to operate it remotely without entering wet well. Notified ROC Screen 2 placed OOS, Screen 1 operating as intended. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-27 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | FLAG | stage2_low_confidence | 0.010721 | ML: above threshold (no LLM available) — 0.011 | scada [control_system] | 0.010721 | 0 | 1
2026-02 | 2026-02-12 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | -On site to complete work orders. -Completed comprehensive housekeeping tasks. -Found outlet air line for OCU has completely torn off unit. Work request created. | FLAG | stage2_low_confidence | 0.02697 | ML: above threshold (no LLM available) — 0.027 | work order [maintenance_action] | 0.02697 | 0 | 1
2026-02 | 2026-02-11 | Vaughan Black Creek Pumping Station | WW-WEST | On site to troubleshoot disconnect switch for South Force Main Valve MV-11. Disconnect switch in internally corroded. Lubricated to allow the disconnect to close again. Tested disconnect function. Ok. Should be replace in the near future. | FLAG | stage2_low_confidence | 0.023682 | ML: above threshold (no LLM available) — 0.024 |  | 0.023682 | 0 | 1
2026-02 | 2026-02-20 | Vaughan Black Creek Pumping Station | WW-WEST | - Checked screen, oil is good. Levelled bin - Pushed bin back in - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 570.2 L/s, pressure 305 kPa Pump 2: 450 L/s at 100%, pressure 267 kPa Pump 3: 132.4 L/s at 100% speed, pressure 214 kPa Pump 4: 466 L/s at 100% speed, pressure 265 kPa - Checked station and recorded readings on SharePoint. Trends okay. Noticed high vibration on pump 1. Will monitor | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; vibration [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; vibration [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-10 | Vaughan Black Creek Pumping Station | WW-WEST | Checked station and trends, and recorded readings on SharePoint. Checked screen, all okay. Levelled bin Mopped floor | FLAG | stage2_low_confidence | 0.0091229 | ML: above threshold (no LLM available) — 0.009 |  | 0.0091229 | 0 | 1
2026-02 | 2026-02-06 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check - no new issues reviewed trends and added data into SharePoint. Completed weekly RS pump run test - no new issues Pump1 -573.1L/s at 297kPa Pump 2 - 453.2 L/s at 100% at 262kPA Pump 3 131.3L/s at 100% and 215kPA Pump4 - 460.3 L/s at 100% at 265kPA Pump 5 -OOS pumps placed back into Auto and put in duty. Pump 5 remains in manual OOS Inspected seal water and cleaned screens - all clear and functioning. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-02 | Kleinburg Water Resource Recovery Facility | WW-WEST | On site for high fuel temperature alarm. Fuel system is cool. Cleared alarm 263. Unplugged sensor to confirm location of sensor. Alarm 263 came back in. Test ran generator okay Fuel was not overheating. Will order a fuel temperature sensor to replace. | FLAG | stage2_low_confidence | 0.012111 | ML: above threshold (no LLM available) — 0.012 | alarm [control_system]; plugged [infrastructure] | 0.012111 | 0 | 1
2026-02 | 2026-02-23 | Schomberg Water Resource Recovery Facility | WW-WEST | Supernated STT and released to SHT. Completed labs and entered data in ace sheets. Completed station check. UV bank b, rack 7 not lighting up and causing alarm. Problem with power at the socket for rack 7. Created W11693400. Cleaned blower building. Cleaned UV/FE channel. | FLAG | stage2_low_confidence | 0.013464 | ML: above threshold (no LLM available) — 0.013 | alarm [control_system] | 0.013464 | 0 | 1
2026-02 | 2026-02-02 | Schomberg Water Resource Recovery Facility | WW-WEST | On site to continue work on effluent pump 3. Effluent pump 3 is still out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-08 | All Water System ROC General | ROC | 01:00 - EZ MAX ISSUES 01:35 - MKRSEM - Called Toronto Water (Brett) and requested to stop pumping to reservoir 02:00 - EZMAX Issues resolved | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-02 | 2026-02-26 | Markham Leslie Pumping Station | WW-CEAST | -on site for Housekeeping, cleaning up garbage around site on various floors -running pump 1 in auto duty 1, if it trips on bearing high temp, or another alarm, WO will be created, ongoing issues with pump 1 -completed alarm investigation -W11692845- Leslie Pump 1 High Bearing Temp Alarm created -station okay, only 5 pumps in auto/duty rotation, pump 1 OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: trip [equipment_failure]; oos [equipment_failure]; alarm [control_system] | trip [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-23 | Markham Leslie Pumping Station | WW-CEAST | Station Check completed (See details on SharePoint). Checked drywell. cleaned dry well area Checked screen room, changed out rag bin. Cleaned/hose down screen room. Switched pumps duty to timed mode from all-stop. Pumps 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. pump 1 faulted on 'stack overtemp' alarm. cleared the alarm. pump 2 seal water line has a pinhole leak. created work request W11683392 for maintenance to fix. Pump 1 & 2 taken oos. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; alarm [control_system]; leak [infrastructure] | sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 1
2026-02 | 2026-02-24 | Markham Leslie Pumping Station | WW-CEAST | -ran pump 1 with maintenance, upper bearing on pump is overheating -pump is manual off but available if needed to run -wet well consolidated work order completed -pump 2 was put OOS for the seal water, but back online before end of day -all 6 pumps can run, but pump 1 is manual off for the night, but available if needed -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-10 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Completed consolidated monthly dry well pump floor inspection work order. -Sump pit inspection completed. Tested Sump Level HiHi Alarm and confirmed with ROC. -Dry well flood alarm does not exist at this site, tested sump level HiHi in its place. -High low temp alarm does not exist at this site, temperatures tracked on BAS site. -BAS check completed. -Auto dialer test completed and confirmed with ROC. -Air compressor inspection completed, checked belts, oil, filters. -Seal water strainer checks completed. -Pump 1 OOS. -Pump 6 in auto duty rotation, but discharge valve is leaking, issue already reported to maintenance team. -Bar Screen 2 fault came in at 0928 this morning, reset fault and test ran screen for multiple cycles with no issues. Left bar screen 2 running in auto. Topped up oil on both bar screens. -RS Pump and Motor Inspection completed: -Pump 1 OOS -Pump 2: 1710L/s at 100% speed. -Pump 3: 1300L/s. -Pump 4: 1290L/s. -Pump 5: 1570L/s at 100% speed. -Pump 6: 1190L/s. -Check valve inspections completed. -Air relief valve inspections completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] | sso [critical]; flood [critical]; fault [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 1
2026-02 | 2026-02-11 | Markham Leslie Pumping Station | WW-CEAST | -station check of site -entered data into sharepoint -inspected site -reviewed SCADA -notified ROC of work being performed -WAJAX on site for generator maintenance -YR maintenance and electrical on site for pump 1 repairs -generators started at 11:58 Generator 1: Start Hours:230.24 Stop Hours:231.42 Generator 2: Start Hours:117.40 Stop Hours:119.35 Generator 3: Start Hours:103.59 Stop Hours:105.54 Bulk Fuel Tank Start: 23,437L Fuel Stop: 22,572L -generator 1 went into shutdown due to low oil level, topped up oil, reset alarms, put generator 1 back to auto, generator started up and ran for remainder of 1 hour test run, sync/load shared with other generators Generator Run Time: 1.95 hrs -generators off at 13:52 -test successful, back on utility power, reset alarms -pump 1 remains OOS -all other pumps in auto and reset -Generator 1-3 Monthly Test Run -Hazard Waste Removal-no hazardous waste -Leslie Scrubber Inspection -bin replacement/screen room inspection -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] | oos [equipment_failure]; repair [maintenance_action]; scada [control_system]; alarm [control_system]; alarms [control_system]; hazard [safety] |  | 1 | 1
2026-02 | 2026-02-09 | Markham Leslie Pumping Station | WW-CEAST | Weather today Clear and -16 Celsius -On site to complete work orders W11579343. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure]; work order [maintenance_action] | sso [critical]; out of service [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-03 | 2026-03-04 | Sutton Water Resource Recovery Facility | WW-NORTH | Attending site to commission and verify the Lagoon Flowmeter - SUSP_SUSPLG_LGN_FIT1 (W11479921). Configured device, added asset number and verified function. ROC was notified before and after maintenance activities. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-28 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | TESTING NEW MAXIMO SYSTEM NOT REAL ENTRY PLEASE IGNORE REVISION 1 REVISION 2 | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-31 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Elog was down this morning March 31, 2026 Jason Garnett onsite from 7:45 am - 8:15 am Completed station and equipment check and weekly BacT sample W11705420 Took sample and grabs @ 7:55 am Total: 2.70 mg/l Free: 0.02 mg/l Analyzer matched grabs, reagents ok All other readings on PD sheets shared online folder ET Filling @ 20 l/s ET ops normal | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-30 | Queensville Wells No. 3 and 4 | CENTRAL | See photos/paper log book | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-05 | Nobleton Water Resource Recovery Facility | WW-WEST | - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint - Enabled RAS batch wasting mode at 10:08. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 13:47 - Plant water booster pump is cycling too much. This eventually causes pumps to fault on high and low pressure. This issue seems to have been going on for a while. Upon inspection, it seems RT1 and RT2 temperature protection relay faulted and is showing red. In addition, the discharge side fails to maintain adequate pressure while the plant water demand is low (vortex water scour not active at the time, no plant water usage from hydrant, etc). This is causing the pump to cycle on constantly to boost the pressure. The pressure tank seems to be okay with no leaks. Pressure switch differential settings seem okay. The check valve seems to be the culprit. I?ve tried to isolate the lead pump, pump 1, and the hissing sound stopped but the system still loses pressure fast. Therefore, it seems to be leaking on both sides. Created work order for maintenance and notified team - Received soda as delivery at 14:50. Received 250 bags. Signed all papers | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure]; leaking [infrastructure] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; leak [infrastructure]; leaking [infrastructure] |  | 1 | 1
2026-03 | 2026-03-06 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, flushed screw press drain lines, replaced bins following pick up. -Monthly JHSC H&S inspection completed, no issues noted. -Consolidated Dry Well Pump Floor Inspection completed. -RS pump & motor inspection completed. -Pump 1: 1310L/s. -Pump 2: 975L/s at 0% speed, 1230L/s at 25%, 1460L/s at 50%, 1860L/s at 100%. -Pump 3: 1310L/s. -Pump 4: 1290L/s. -Pump 5 OOS. -Pump 6: 1165L/s. -Check valve inspections completed. -Sump pit inspection completed. -Dry well flood alarm completed, Sump High High Level Alarm confirmed by ROC. -Air relief valve inspection completed. -Seal water strainer inspection completed. -Air compressor inspection completed. -BAS check completed. -Ran Pump 1 in auto duty 1 again until it failed again on Motor/Bearing High Temp Alarm. -Pumps 1 and 5 remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; failed [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] | sso [critical]; flood [critical]; failed [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-04 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, hosed down floor, repositioned screw press to better align with floor drain. -Bar screen bin removal completed. -Monthly diesel generator test run completed, readings entered into SharePoint. -1058 - Transferred site to generator power. -1241 - Transferred site back to utility power. -Gen. 1: Start hours: 231:42, Stop hours: 233:41, Run time: 1hr, 59min. -Gen. 2: Start hours: 119:35, Stop hours: 121:33, Run time: 1hr, 58min. -Gen. 3: Start hours: 105:54, Stop hours: 107:52, Run time: 1hr, 58min. -Hazardous waste collection and removal completed. -Overflow kit inspection completed. -Ran Pump 1 in auto, duty 1. Pump ran from 12:55-1450 before faulting again on Motor/Bearing High Temp Alarms. Left pump faulted and OOS for the night. -Pump 5 OOS with VFD Fault following generator testing. Work request created for issue. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; fault [equipment_failure]; faulted [equipment_failure]; faulting [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure]; pump fault [infrastructure]; hazard [safety] | overflow [critical]; fault [equipment_failure]; faulted [equipment_failure]; faulting [equipment_failure]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure]; pump fault [infrastructure]; hazard [safety] |  | 1 | 1
2026-03 | 2026-03-02 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Reset Earth Fault on AHU1. -Reset Fault 47, Stack Overtemp Fault on Pump 1. -Test ran Pump 1 in auto, duty 1. Pump 1 ran for just under two hours before faulting again. Fault 47, Overtemp Fault back on Pump 1 MCC panel and SCADA is showing Fault Alarm, Motor/Bearing High Temp Alarm, and Motor/Bearing High Temp Trip Alarm. -Left Pump 1 in manual off, OOS for the night. -Hoist inspections completed on site, no issues noted. -Checked screen room, flushed screw press drain lines, replaced bins, cleaned floor in screen room. -Pump 1 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulting [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] | fault [equipment_failure]; faulting [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-27 | Markham Leslie Pumping Station | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Reset fault on Pump 1 and test run pump for maintenance team. -Checked screen room, changed out rag bin for the weekend, replaced bins following pick up, flushed screw press drain lines, bar screen oil topped up. -Assisted maintenance team with pump testing and maintenance activities. -Pump 1 is currently still running, but if it faults again it will remain OOS for the weekend. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure] | fault [equipment_failure]; oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-25 | Markham Leslie Pumping Station | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Ran Pump 1 in auto, duty 1 until pump faulted again. -Pump 1 remains OOS. -Rag bins placed out for pickup. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; pump fault [infrastructure] | sso [critical]; fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; pump fault [infrastructure] |  | 1 | 1
2026-03 | 2026-03-10 | Markham Leslie Pumping Station | WW-CEAST | On site to check pump 5 VFD. Found auxiliary power fault. Was able to reset fault. Suspect it happened during power transfer last week. Operations tested pump 5 in manual. Pump is working ok. Pump 5 back in auto duty rotation. Also onsite to check generator 3. Local control panel screen was off. Found loose fuse holder on front of panel. Repaired. Screen is back on. No more issues. | FLAG | stage2_low_confidence | 0.12801 | ML: above threshold (no LLM available) — 0.128 | fault [equipment_failure]; oos [equipment_failure]; repair [maintenance_action] | 0.12801 | 0 | 1
2026-03 | 2026-03-09 | Markham Leslie Pumping Station | WW-CEAST | -On site to complete work orders. -Washed Bayview Steeles OCF mist eliminator filters in screen room and left filters out to dry. -Checked screen room, changed out rag bin, flushed screw press drain lines, hosed down floor. -Odour control scrubber system inspection completed. Inspected filters, greased fan shaft in screen room OCU. -Station check completed, readings entered into SharePoint. -Bypass sampling kit inspection completed. -Ran Pump 1 in auto, duty 1 until Motor/Bearing High Temp Alarms came back in. -At 1132, Generator 3 Warning Alarm and Generator 3 DGC Not in Auto Alarm came in. Inspected Generator 3, found generator screen/panel blank, appears as though their is no power to Gen. 3 panel. Unable to reset alarms locally on generator or at GMCP panel. Work request created for issue. -Pump 1 and 5 OOS, Generator 3 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | bypass [critical]; oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 1
2026-03 | 2026-03-28 | Ballantrae Well 1 & 2 | EAST | This is my first log entry! And now it's been updated! | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-28 | Ballantrae Well 3 | EAST | Time in: 08:10 On site to support contractor to repair the leak on chlorine solution line #2. Engaged E-Stop for chlorine booster pump 2. Depressurized the chlorine solution line 1&2. Contractor applied coatings on the leaky spot for line #2. I replaced the leaky ball valve on chlorine #1 line. Primed chlorine line #1. Tested chlorinator #1 vacuum, it responds well. Opened cylinders, tested chlorinators in local and remote, no issue. Man/Start well 3. Switched silicate pump to #2 to check it's operation, no issue. Verified chlorinator 1 performance, it is dosing at 50%, 25 ppd, vacuum = -90 mbar. Chlorine booster pump 1 discharge pressure = 210 psi. 09:33 verified chlorine analyzer readings: Grab influent = 2.15 mg/l, analyzer = 2.11 mg/l Grab effluent = 1.48 mg/l, analyzer = 1.51 mg/l. Will place well 3 to auto remotely. Time out: 09:55 | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action]; leak [infrastructure] | oos [equipment_failure]; repair [maintenance_action]; leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-31 | Schomberg Elevated Tank | WEST | - on site to complete contingency entry | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-30 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, raked rag bin, bar screen oil topped up, cleaned rags off conveyors and floor. -Pump 4 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-02 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -pump 1 and 4 are OOS, 4 pumps available -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-03 | 2026-03-04 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -rotated bin in screen room -pumps 1 and 4 manual off, duty 7, maintenance working on them -on site for monthly work orders -Air Compressor Inspection -Air Dryer Inspection -JHSC Inspection -bins out for pickup, cleaned screen room -pump 1 back to auto duty 1, running with no issues -5 pumps available in auto, pump 4 OOS -backflushed line 2 at dump pad, cleared alarm, back to available -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] | sso [critical]; oos [equipment_failure]; work order [maintenance_action]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-03 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -on site for monthly work orders -Aurora SPS Consolidated Wetwell and Outfall Inspection -Monthly Surge Tank Inspection -Aurora EQ Tipping Bucket Test -outfall is okay, creek is well below duckbill -pump 1 was tested from the request of maintenance, leakage alarm came in, pump 1 is manual off, duty 7 -pump 4 is OOS -4 pumps available -Housekeeping of site, cleaned up garbage on all levels -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 1
2026-03 | 2026-03-18 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to complete work orders. -Alectra on site for hydro meter replacement. Discovered meter due for replacement was for solar power, so no disruption to station power is needed. -0855 - Transferred station to generator power. -Upon transfer to generator power, Generator 3 fuel filter primer cap blew out of the filter causing diesel fuel to spill onto ground. Immediately stopped Generator 3 and used absorbent pads to contain and clean up fuel spill. -0956 - Transferred site back to utility power. -Monthly diesel generator test run completed, readings entered into SharePoint. -Generator 1: Start: 629.3hrs, Stop: 630.4hrs, Run time: 1.1hrs. -Generator 2: Start: 621.5hrs, Stop: 622.6hrs, Run time: 1.1hrs. -Generator 3: Start: 825.3hrs, Stop 825.3hrs. -Generator 3 OOS until repairs can be made. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, changed out rag bin, bar screen oil topped up. -Bar screen rag bin removal completed, bins out for pick up. -Pump 4 OOS, Generator 3 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: spill [critical]; sso [critical]; oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; absorbent pads [safety] | spill [critical]; sso [critical]; oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; absorbent pads [safety] |  | 1 | 1
2026-03 | 2026-03-23 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -rotated bin in screen room, cleaned screen room -reset pump 1 for discharge valve fault -pump 4 remains OOS, 5 pumps available -locked out and tagged out East Forcemain for gravity sewer cleaning south of Bloomington: all 6 pumps east discharge valves are in local stop, east surge tanks valve are closed and depowered, East forcemain common discharge valve is local closed, and depowered, ISS east discharge valve is local closed, in local stop -setpoints on SCADA show East is not in service, west forcemain is manually selected as in service -notified ROC and CEWW of East Forcemain OOS -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; scada [control_system] | fault [equipment_failure]; oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-03 | 2026-03-01 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site for sludge handling and lab analysis. -Added two bags of soda ash to each aeration tank. -Unable to decant STT. Hose has multiple holes right above connection to decant pump and is producing no flow. Emptied approximately 2m out of STT to make room for auto wasting tonight. -Raked manual bar screen. -Completed lab analysis and entered results into SharePoint. -Ran RAS pumps at 100% speed for several minutes. -Verified sand filter operation and alum dosing. -Cleaned solids off top of post aeration alum chamber. -Verified clarifier heater are both still running. -OCU and traveling screen remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Added two bags each of Soda Ash into each Aeration Tanks Removed rags from the sluice gates of Aeration Tanks Post Filtration/UV channel hose down. Clarifier #1 taken OOS due to gearbox issue. Emptying clarifier #1 now. Bar screen put back to service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-03 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to complete work orders. -Added two bags of soda ash to each aeration tank. -Raked manual bar screen. -Cleaned out RAS inlet chamber and post aeration alum chamber. Cleaned rags off aeration tank inlet gates and DO probes. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Monthly diesel generator test run completed, readings entered into SharePoint. -1013 - Transferred station to generator power. -1122 - Station transferred back to utility power. -Generator start hours: 492.3, stop hours: 493.5, run time: 1.2hrs. -Switched grit bins following pick up. -Clarifier scum system cleaning completed. Cleaned out clarifier scum troughs, hosed down walls of scum tank and ran Scum Pump 1 in local to pump out tank following cleaning. -Traveling screen and OCU remain OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-03 | 2026-03-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | put two bags of soda ash into the aeration tanks and set two up for later. Started grabbing samples for the Lab and Daniel had switched WO to Kevin,, went through the station and sand filters working great and started de-cant pump. Clarifier 1 arm stopped turning, got a hold of Bill (maintenance) and he's on his way. Cleaned out the post aeration tank as well as the inlet gates while waiting. There was no Hazardous waste to dispose of and went through the weekly alarm management for EOC and YDOC and there were no changes to either site. Started emptying clarifier #1 due to gear box in motor is broken - Daniel showed up and walked us through switching everything over. Continued draining for two hours and i'll be in on the weekend to complete. Bill and Terry - maintenance got the bar screen working again so we closed off the by-pass and now flow is going through the bar screen. Clarifier 1 is down but the rest of the station is running fine. | FLAG | stage2_low_confidence | 0.57583 | ML: above threshold (no LLM available) — 0.576 | alarm [control_system]; hazard [safety] | 0.57583 | 0 | 1
2026-03 | 2026-03-13 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. Station Check (See details on SharePoint). STT decanted, afterwards remaining sludge dumped into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Weekly alarm management - only clarifier 1 no RAS pump running is the alarm due to clarifier 1 out of service. Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system] | out of service [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system] |  | 1 | 1
2026-03 | 2026-03-19 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put in 2 bags of soda ash and set 2 up for later,, Kevin started de-cant pump and then I worked with Kevin on his Lab work to speed it up and get a lot more organized. Went through the station, UV bank 1 is OOS - sand filters working great. Checked the hoist in the aeration room and the sand filter room - all good. Cleaned out the post aeration tank and the inlet channel gates, Washed down the UV channel and shut down the effluent pumps for the night to make sure we have no breaks again. Hopefully this helped Kevin out with his Lab work, UV 1 is OOS along with clarifier 1 the rest of the station is running fine. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-23 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put 4 bags of soda ash in and started de-cant pump,, Daniel and I isolated the inlet at the headworks and are diverting flow to the lagoon (@ approx. 08:25 ) Put 3 knife gates in place to re-direct flow to the lagoon. Accuworxs here and are pumping down post aeration tank, Retrieved the grating at approx. 14:00 hrs and then put the station back to normal ops by removing gates from the headworks. Station back to normal ops - clarifier 1 and UV bank 1A are still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site to complete work orders. -GFL/Accuworx on site for Clarifier 1 cleaning. -Two bags of soda ash added to each aeration tank. -Cleaned out RAS inlet chamber and post aeration alum mixing chamber. -Mechanics and electricians have completed repair work on Clarifier 1. Clarifier 1 locked out at local disconnect with station lock until clarifier cleaning is completed. -Worked on UV room cleaning. Removed old/broken items. Cleaned floors. -UV Bank 1A OOS, Clarifier 1 OOS, RAS Pump 3 OOS, WAS Pump 2 OOS, OCU OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] | oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action] |  | 1 | 1
2026-03 | 2026-03-31 | Mount Albert Pumping Station | WW-CEAST | -On site to respond to communications failure alarm reported by ROC. PCS on-call has also been notified and is on route to site. -0405 - Upon arrival to site, swipe card reader not working, local SCADA OIT panel is blank and not working, Pumps both displaying No Communication faults on panels. Wet well level is at 4.08m. Tried resetting pump faults on local panel, but pumps will not run in remote or local. Wet well backup mode is in Auto, but pumps not running. -Called on-call electrician, tried cycling power to pumps, but still not working. Tried disconnecting power for 5-10min, but pumps still not working when turned back on. On-call electrician on route to site. -0431 - Contacted ROC to initiate emergency vac truck procedure and have trucks dispatched to site. -Tried transferring site to generator power, suspecting possible phase loss on site. Unable to get generator to turn on, e-key not working on any locks on site. -Briefly left site to bump e-key at MTA WRRF. When back on site, e-key still not working. Cut lock to generator building. Generator screen is blank and unresponsive. Generator will not run in remote or manual. -0512 - Wessuc confirmed they have vac truck and tanker on route to site. -Electricians and PCS arrived at site and found multiple damaged pieces of equipment due to a suspected lightning strike on the building. They immediately began work to restore functionality of damaged equipment. -0631 - Wessuc informed of delays and that they were still approximately 1.5hrs away. -0645 - Informed SAC of ongoing spill. Spoke with environmental officer Edhilvia Campos and was assigned event# 1QG1QRG. -0655 - Informed York Region local health unit of ongoing spill. Spoke with health officer David Huang. -0700 - Notified LSCRA of ongoing spill. -0815 - Wessuc arrived on site and began setting up hoses to pump down wet well. Began pumping down wet well at approximately 0830. -0830 - Collected spill samples with Chris Rodie, CoC# W11769441. -0925 - Electricians able to get one pump running on site and began pumping down wet well to forcemain along with Wessuc pumping wet well to vac truck. -0957 - Wet well at 3.99m, below the overflow level. Spill has ended. -Kevin Shaji arrived at site to complete weekly sample collection. -When Wessuc had completed their emergency wet well pumping activities, accompanied vac truck to site of spill, which was a local East Gwillimbury manhole between the southeast corner of the Foodland parking lot and the railroad tracks. Wessuc cleaned solids and liquid from surrounding area, as well as removed excess solids from local sewer. While on site, visited by local Public Heath Inspector Darja Montsenko, who also observed spill location during cleanup and afterwards. -Instrumentation team on site to replace damaged flowmeter and level sensor. -Electricians and PCS team able to get both station pumps repaired and operational in auto. -Temporary generator set up on site and tested in manual and in auto, with a full station transfer test. -Composite sampler reset for 0700 April 7, 2026. Sample jug cleaned. -Security system and swipe card reader on site not working. Informed supervisor of issue and work request created. -Station is back running normally. Temporary generator set up on site. Both pumps available and in local. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; spill [critical]; emergency [critical]; lightning strike [critical]; fault [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; not working [equipment_failure]; repair [maintenance_action]; environmental officer [regulatory]; health unit [regulatory]; spill sample [regulatory]; scada [control_system]; alarm [control_system]; no communication [control_system]; overflow [infrastructure]; backup [infrastructure]; pump fault [infrastructure] | overflow [critical]; spill [critical]; emergency [critical]; lightning strike [critical]; fault [equipment_failure]; failure [equipment_failure]; not running [equipment_failure]; not working [equipment_failure]; repair [maintenance_action]; environmental officer [regulatory]; health unit [regulatory]; spill sample [regulatory]; scada [control_system]; alarm [control_system]; no communication [control_system]; overflow [infrastructure]; backup [infrastructure]; pump fault [infrastructure] |  | 1 | 1
2026-03 | 2026-03-31 | Mount Albert Pumping Station | WW-CEAST | Attending site to replace wetwell level transmitter and flowmeter (W11769917). Devices were damaged due to electrical storm. Replaced, configured and tested wetwell level transmitter with Art. Parth and Rick replaced and configured discharge flowmeter. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-31 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | @8:25 - Placed pumps 1 and 3 OOS in manual off to leave 2 other pumps running in auto and in manual speed of 30% to slow down flow to Aurora SPS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-18 | Kleinburg Water Resource Recovery Facility | WW-WEST | Supernated STT and released to SHT. Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:49. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Autowasting volumes are correct with waste pumps in auto speed. Added 8 bags to soda ash hopper. Completed housekeeping work order for headworks building. Completed DO probe maintenance. Created work order (W11744156) for service water pipe in need of re-securing to wall in headworks. | FLAG | stage2_low_confidence | 0.026213 | ML: above threshold (no LLM available) — 0.026 | work order [maintenance_action] | 0.026213 | 0 | 1
2026-03 | 2026-03-31 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Dropped off Kleinburg WRRF weekly compliance samples -Created contingency entry due to EZmax mobile error. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) | compliance [regulatory] |  | 0 | 1
2026-03 | 2026-03-23 | Schomberg Water Resource Recovery Facility | WW-WEST | On site for blower 1 oil leak. We will return with seals | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-17 | Schomberg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WO. Notified ROC. Completed Consolidated Aer., Sludge and Vortex Blower Inspections. Topped Up Oil Reservoirs and Replaced Air Filters Where Necessary. All Belts OK. Returned to Service and Cleared Associated Alarms. Created Follow-Up WO Regarding Aer. Blower #1 Oil Leak for Maint. ?> W11740816. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; follow-up [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | sso [critical]; follow-up [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 1
2026-03 | 2026-03-18 | Schomberg Water Resource Recovery Facility | WW-WEST | Completed the station check and daily lab work Batch wasted 51m3 overnight Cleaned the DO probes Aeration blower 1 cooling fan faulted and cannot be reset Blower 1 is currently left out of service | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure] | fault [equipment_failure]; faulted [equipment_failure]; out of service [equipment_failure] |  | 1 | 1
2026-03 | 2026-03-28 | All Water System ROC General | ROC | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, weather: -1C and sun. Please see attached photos of the paper logbooks. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-30 | All Water System ROC General | ROC | Maximo server down from 10-16:00. Attached are logbook entries | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-31 | All Water System ROC General | ROC | EZ Max Mobile Access Restored Mar/31/2026 04:00 - 06:45 | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, Weather: -1C and sun. Please see attached photos of the paper logbooks. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-30 | All Wastewater System ROC General | ROC | Maximo down between 10:00 and 16:00. Attached is pictured of logbook entries | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2026-03-31 | All Wastewater System ROC General | ROC | Contingency Log, March 31, 0400 to 0645, eLogs were down. Attached are the paper logs for that time stamp | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 1
2026-03 | 2025-03-19 | Nobleton WRRF |  | - Checked station and trends, and recorded readings on SharePoint - Reset exhaust fan 307 - Unclogged filter 1 north cell - Found flame failure alarm for the blower room. Notified TL - Smelled of gas near the makeup air unit above the headworks building. Notified TL and to create an Archibus - Reset plant water system - Assisted contractor for the noise study. Notified ROC that the generator will be turned on for the noise study. Turned on the generator at 11:41. Fuel level at 33 inch at start and once done, fuel level at 33 inch. Generator hours from 288.51 hrs to 289.18 hrs - Cleaned fly trap | FLAG | stage2_low_confidence | 0.41773 | ML: above threshold (no LLM available) — 0.418 | failure [equipment_failure]; noise [equipment_failure]; archibus [maintenance_action]; alarm [control_system]; clog [infrastructure]; clogged [infrastructure] | 0.41773 | 0 | 1
2026-03 | 2024-04-19 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - checked station and performed in-house lab, and recorded readings on SharePoint - reset plant water system due to high and low pressure alarm - gave a tour of the plant to the WiFi team - transferred sludge from the sludge thickening tank to the sludge holding tank - GFL picked up a sludge load - wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode. Placed WAS valves back to manual off | FLAG | stage2_low_confidence | 0.089435 | ML: above threshold (no LLM available) — 0.089 | alarm [control_system] | 0.089435 | 0 | 1
2026-03 | 2024-04-19 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - checked station and performed in-house lab, and recorded readings on SharePoint - reset plant water system due to high and low pressure alarm - gave a tour of the plant to the WiFi team - transferred sludge from the sludge thickening tank to the sludge holding tank - GFL picked up a sludge load - wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode. Placed WAS valves back to manual off | FLAG | stage2_low_confidence | 0.089435 | ML: above threshold (no LLM available) — 0.089 | alarm [control_system] | 0.089435 | 0 | 1
2026-03 | 2024-01-31 | Nobleton WRRF |  | Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - Collected weekly regulatory samples - Decanted then transferred sludge from the sludge thickening tank to the sludge holding tank - Performed station check and in-house lab, and recorded readings on SharePoint. Reset plant water system due to high and low pressure alarm. - Enabled RAS batch wasting mode at 8:13. Turned WAS valve 2 and 3 to auto. Turned WAS pumps 1 and 2 to auto. - Wasted 25m^3 from clarifier 1 and 25m^3 from clarifier 2 then rest RAS batch wasting mode at 12:00. Once done, turned WAS valve 2 and 3 to manual. Turned WAS pumps 1 and 2 to manual off. - Added 1 bag of soda ash each to aeration tank 1 and tank 2 - Performed DO probe maintenance after holding outputs at the aeration tank 1 and tank 2. Cleaned sensor and removed rags. Checked DO readings, all okay. Removed outputs once done - Removed floating solids or debris from aeration tank 1 and tank 2 surfaces - Removed rags from the aeration tank 1 and tank 2 outlet weir - Bled air from the condensation line at the aeration tank 1 and tank 2 | FLAG | stage2_classifier | 0.69182 | ML classifier: high issue probability (0.692) | regulatory [regulatory]; alarm [control_system] | 0.69182 | 0 | 1

## Top 200 Flags
source_month | EVENTDATE | DESCRIPTION | PERSONGROUP | LDTEXT | triage_decision | triage_stage | triage_score | triage_reason | matching_keywords | clf_proba | stage1_label | is_issue
2026-02 | 2026-02-08 | All Water System ROC General | ROC | 01:00 - EZ MAX ISSUES 01:35 - MKRSEM - Called Toronto Water (Brett) and requested to stop pumping to reservoir 02:00 - EZMAX Issues resolved | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-28 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | CENTRAL | TESTING NEW MAXIMO SYSTEM NOT REAL ENTRY PLEASE IGNORE REVISION 1 REVISION 2 | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-31 | Newmarket (East) Harry Walker Elevated Tank | CENTRAL | Elog was down this morning March 31, 2026 Jason Garnett onsite from 7:45 am - 8:15 am Completed station and equipment check and weekly BacT sample W11705420 Took sample and grabs @ 7:55 am Total: 2.70 mg/l Free: 0.02 mg/l Analyzer matched grabs, reagents ok All other readings on PD sheets shared online folder ET Filling @ 20 l/s ET ops normal | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-28 | Ballantrae Well 1 & 2 | EAST | This is my first log entry! And now it's been updated! | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-31 | Schomberg Elevated Tank | WEST | - on site to complete contingency entry | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-31 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Dropped off Kleinburg WRRF weekly compliance samples -Created contingency entry due to EZmax mobile error. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) | compliance [regulatory] |  | 0 | 1
2026-03 | 2026-03-28 | All Water System ROC General | ROC | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, weather: -1C and sun. Please see attached photos of the paper logbooks. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-31 | All Water System ROC General | ROC | EZ Max Mobile Access Restored Mar/31/2026 04:00 - 06:45 | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-03 | 2026-03-28 | All Wastewater System ROC General | ROC | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, Weather: -1C and sun. Please see attached photos of the paper logbooks. | FLAG | stage1_contingency | 1 | LOGENTRY_CONTINGENCY=1 (operator-marked event) |  |  | 0 | 1
2026-02 | 2026-02-01 | Keswick Water Resource Recovery Facility | WW-NORTH | Attended for sludge handling Decanted/transferred sludge thickening tanks Switched WAS feed to sludge thickening tank 2 Cleaned bar screen and raked bin Reset channel blower #2 alarm Cleared blockage from microscreeen discharge. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; blockage [infrastructure] | alarm [control_system]; blockage [infrastructure] |  | 1 | 0
2026-02 | 2026-02-02 | Holland Landing Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Checked diesel containment pit Equipment OOS: none | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; containment [safety] | oos [equipment_failure]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-12 | Holland Landing Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Equipment OOS: none | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Checked diesel containment pit; dry Equipment OOS: none | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; containment [safety] | oos [equipment_failure]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-12 | East Gwillimbury 2nd Concession Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Equipment OOS: none | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-02 | Queensville West Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint Equipment OOS: Channel grinder | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-20 | Queensville West Sewage Pumping Station | WW-NORTH | Onsite to wrap up annual calibrations and to replace Wetwell 1 LIT2 Informed ROC Used cal mode on scada during the work Created CSE permit Completed force main 1 FIT, force main 1 PIT, H2S gas detectors Entered wetwell and replaced hydrostatic LIT2 Completed configuration and calibration Cleared associated alarms Closed CSE permit Informed ROC, armed building and left site No issues | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; h2s [safety] | sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; h2s [safety] |  | 1 | 0
2026-02 | 2026-02-19 | Queensville West Sewage Pumping Station | WW-NORTH | Onsite for annual calibrations Informed ROC Used cal mode on scada during calibration Instruments calibrated: Discharge FIT #2, LIT 1, 3 and 4, overflow FIT, channel LIT. Issues calibrating LIT2, Discharge FIT #1 and Discharge PIT2. Will return tomorrow to address the issues. Cleared associated alarms Informed ROC, armed building and left site | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; sso [critical]; scada [control_system]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-19 | Queensville West Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry channel grinder oos | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-10 | Queensville West Sewage Pumping Station | WW-NORTH | On site responding to Generator fault & LIT 3/4 OOR -Upon arrival, there was no power at the facility but the ATS panel was indicating we were connected to utility power with 600 V on each phase. Switched power to generator power but still the same issue. Although I was able to run a pump in local. -Appears there was a power blip which briefly caused the generator to start. The generator breaker tripped, along with MCC "Panel AA". The tripped MCC Panel AA was the culprit- once breaker was reset, facility power resumed and facility was operating normally. -It was found that the "duct heater"(1, 3, & 5) breaker in "distribution panel AA", was tripped and resetting this caused it to immediately trip again, subsequently tripping MCC "Panel AA". Work order for property services to address this issue will be created. -WWEL_LIT2 (wet well 1 hydrostatic level) began reading OOR once the other issue resolved. Instrumentation will respond to site to correct the issue. Equipment OOS: channel grinder and wet well 1 hydrostatic level | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; work order [maintenance_action] | fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-12 | Queensville West Sewage Pumping Station | WW-NORTH | Performed facility station check Data in sharepoint On site to provide operational support for CPD performing pump vibration testing. Placed pumps in manual to increase the wet well level. Ran each pump in local at 52, 56, and 60 Hz separately and running together. Placed facility back to auto and observed normal operation. Equipment OOS: Channel grinder and WW1 hydrostatic transmitter | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; vibration [equipment_failure] | oos [equipment_failure]; vibration [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-05 | Queensville West Sewage Pumping Station | WW-NORTH | station checks sharepopint data entry grinder oos | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-09 | Queensville West Sewage Pumping Station | WW-NORTH | on site 1115hrs unable to time in on site, keeps requesting to time out, even though its timed out. station checks health and safety checks. ocu inspection, property services was on site. Heater in OCU room broken, property services looking for a new one to install. channel grinder oos. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-08 | Sutton Water Resource Recovery Facility | WW-NORTH | Decant sludge holding and thickening tanks Transfer and put air back on after decant Rag hopper was plugged - ran in hand and raked and cleared material Put aeration blower one in manual off position blower was jumping around will look into it Monday | FLAG | stage1_keyword | 0.95 | Critical keyword match: plugged [infrastructure] | plugged [infrastructure] |  | 1 | 0
2026-02 | 2026-02-23 | Keswick Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry OCU oos (warranty) | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-10 | Keswick Sewage Pumping Station | WW-NORTH | on site 0900hrs. issue with e-log, notified lead and supervisor. Log entry done under remotely while on site. Generator test run. health and safety check ocu oos, GHD and CPD are aware and looking into it?. channel communitor inspection Drywell and hoist inspections. Heat trace inspection generator lolo temp alarm test on scada @1005hrs | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system] | oos [equipment_failure]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-12 | Keswick Sewage Pumping Station | WW-NORTH | station checks sharepoint data entry OCU oos (warranty) | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-02 | Keswick Joe Dales Sewage Pumping Station | WW-NORTH | Performed facility station check Data in SharePoint Equipment OOS: none | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-03 | Georgina No. 4 Sewage Pumping Station | WW-NORTH | generator test run Hi/Low temp alarm test, on scada @1004hrs drywell flood alarm test, on dialer 1010hrs sump pit inspection drywell valve exercise. hoist inspection ocu inspection | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; scada [control_system]; alarm [control_system] | flood [critical]; scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-24 | Woodbridge East Booster Pumping Station | WEST | #11583073 jhs #11582177 dehumidifier #11582224 sump pit #11583744 flood #11583765 lo temp #11582349 Depolox maint. 9:40 Verified (mg/l) Free: Grab 0.04, A 0.04 Total: Grab 1.55, A 1.50 | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-02 | 2026-02-04 | Woodbridge East Elevated Tank | WEST | On site to replace network switch with network analyst Aaron Magsakay. Comm failure alarm was triggered due to this. Removed Old switch from VNETAG NAC panel. Wired 24 VDC power to the new switch and plugged in the Cat6 cable to correct ports. Powered up new IE3300 layer 3 switch and checked the comms. Removed unused cat6 cables. Checked with ROC to make sure comms are back and trends are good. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; alarm [control_system]; plugged [infrastructure] | failure [equipment_failure]; alarm [control_system]; plugged [infrastructure] |  | 1 | 0
2026-02 | 2026-02-19 | Woodbridge West Elevated Tank | WEST | On site for the following work orders. Informed ROC about the works being done W11621618 VNETFD, JHSC Health and Safety Inspection, W11621605 VNETFD, Sump Pit System Inspection, W11621908 VNETFD, Low Temperature Alarm, Test, W11622354 VNETFD, Inspection Form, W11622293 VNETFD, Flood Alarm, Test, W11622283 VNETFD, West Woodbridge ET, Air Relief Valve, Inspection W11622341 VNETFD, Sensing Line Heat Trace System, Inspection, PM W11622415 VNETFD, Portable Gasoline Generator, Test, Woodbridge | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-19 | Woodbridge West Elevated Tank | WEST | -on site to perform following orders: -chamber flood alarm: all ok -chamber inspection: all ok -sump pit tested: all o -temp alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-23 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. Pumps 2,5 & 6 available in timed auto duty rotation every 3 hours. Pump #3 discharge valve for east forcemain is tripped. Unable to clear the 'hardware failure' status on the actuator. Maintenance will check this soon. Pumps 1,3 and 4 remain oos. Checked dry well. ok checked bar screens. changed out rag bins. All lines except 1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure] | failure [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-25 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. checked bar screens. switched out rag bins. All lines except no.1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-27 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Checked screen room. ok. Bypass sampling kit inspection completed. Odour control scrubber system inspection completed. All lines except no.1 available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; oos [equipment_failure] | bypass [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-02 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Hazardous Waste Collection and Removal Checked dry well. Checked bar screens. switched out rag bin. Added oil on the reservoir tank. All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; hazard [safety] | oos [equipment_failure]; hazard [safety] |  | 1 | 1
2026-02 | 2026-02-17 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to troubleshoot pump 4. Found main fuses blown. Checked motor, wiring, supply and control power. Suspect winding contamination. Removed cable entry lid. Found heavy contamination. Unwired pump so mechanics can remove pump. Pump 4 is out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to prep cables for pump 4 replacement. Mechanics installed replacement pump. Wired pump and tried to test rotation. Breaker tripped and 3rd phase fuse blew on startup. Electrical problem needs further investigation. Pump 4 remains out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: tripped [equipment_failure]; trip [equipment_failure]; out of service [equipment_failure] | tripped [equipment_failure]; trip [equipment_failure]; out of service [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site in response to pump 4 alarms(leakage/estop/fault). Upon arrival, found pump 4 mcc main switch in tripped position on B1. Reset the switch put still no power to Pump 4 MCC. Checked all the estops for the pump and confirmed non are active. Talked to CMS and created CMU4 for this issue | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leakage [infrastructure] | fault [equipment_failure]; tripped [equipment_failure]; trip [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 0
2026-02 | 2026-02-20 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bin in screen room -Pump 1 and 4 remain OOS -station okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system] | oos [equipment_failure]; scada [control_system] |  | 1 | 1
2026-02 | 2026-02-11 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Weather today Snow and -1 Celsius -On site to complete work orders W11587339, W11586377. -Completed station check. -Entered station readings into SharePoint. -Air Compressors inspection. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Unclogged drain lines on screw conveyor 3. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; clog [infrastructure]; clogged [infrastructure] | sso [critical]; out of service [equipment_failure]; work order [maintenance_action]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 1
2026-02 | 2026-02-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -On site to complete work orders. -Consolidated wet well inspection work order completed. -Tipping bucket operational checks completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Screw press dewatering compartment and drain line flushed. -Sluice gate valve exercises completed. -Wet well valve exercise completed. -Wet well inspection and cleaning completed. -Wet well high level alarm test completed and confirmed by ROC. -Surge tank inspection consolidated work order completed. -Surge tank and inspection completed. -Surge tank valve and actuator, exercise and inspection completed. -Surge tank drain valve inspection completed. -Transmission line flushing completed on both surge tanks. -Cleared all alarms generated from work orders. -Pumps 1 and 4 remain OOS. -Line 1 at the dump pad OOS for valve replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 1
2026-02 | 2026-02-19 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | -on site at dump pad for line 3 valve overtorque -cleared line, valve was clogged with zip ties, a hauler keeps flushing zip ties and it is an issue -reset alarms on SCADA -line 2 and 3 available, 1 OOS for valve upgrades | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure] | oos [equipment_failure]; scada [control_system]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure] |  | 1 | 1
2026-02 | 2026-02-20 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site to work on pump 4. Continued troubleshooting electrical problem. Checked motor cables and power wiring. Sourced replacement fuse. Was able to power up MCC with motor disconnected. Fault history in Eaton Soft Starter indicated SCR shorted fault. Suspect soft starter failure. Need to source replacement. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure]; scr shorted [equipment_failure] | fault [equipment_failure]; failure [equipment_failure]; scr shorted [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-04 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. JHSC Health and Safety Inspection completed. checked bar screens. Bar Screen Bin Removal and Replacement All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-06 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS. Cleared pump 3 E Disc Hdr MV4 alarm on scada. All standby power generators available in auto. Checked dry well. OK. Air dryers inspection and cleaning completed. checked screen room. OK. All lines available at the dump pad for haulers to use. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; scada [control_system]; alarm [control_system] | oos [equipment_failure]; scada [control_system]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-09 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site for bar screen 1 oos found the rake at the bottom and the rollers out of alinement. Repaired the rollers and aligned the rake and it is back in service | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; repair [maintenance_action] | oos [equipment_failure]; repair [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-07 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | On site in response to barscreen 1 overtorque alarm. Both barscreen OOS. Cleared screen 1 overtorque and attempted to run it in auto. Unit faulted out right away. Noticed rake has fallen near bottom sprocket in crooked position. Got ROC to call in Oncall CMS(Lee F) to site. Cleared overtorque for screen 2 and attempted to run it. Found rake is scratching the plate as it is travelling upwards creating loud screeching sound. Stopped the rake at the top. Lee F and I put screen 2 back in service after adjusting the position of the rake. Inlet gate to screen 2 has been open. Inlet gate to screen 1 has been closed. Notified ROC. Screen 1 OOS, screen 2 back in service | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] | fault [equipment_failure]; faulted [equipment_failure]; oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-03 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | WW-CEAST | on site to complete Consolidated Monthly Dry Well Pump Floor Inspection WO Auto Dialer Alarm Test - received by ROC. High Low Temperature Alarm Test - received by ROC. Dry Well Flood Alarm Test - received by ROC. Sump Pit Inspection and operation Raw Sewage Pump and Motor Inspection Pump 1 (VFD) - out of service Pump 2 (VFD) - @ 0% speed, 267 L/s, 771 kPa, 354 A, 518 V, 54 Hz, 1077 Rpm; 60% speed, 404 L/s, 783 kPa, 470 A, 541 V, 57 Hz, 1136 Rpm Pump 3 (Constant) - 429 L/s, 810 kPa, 454 A, 598 V, 60 Hz Pump 4 (Constant) - 451 L/s, 782 kPa, 454 A, 606 V, 60 Hz Pump 5 (VFD) - @ 0% speed, 299 L/s, 777 kPa, 379 A, 515 V, 54 Hz, 1077 Rpm; 60% speed, 420 L/s, 798 kPa, 499 A, 549 V, 57 Hz, 1136 Rpm Pump 6 (VFD) - @ 0% speed, 277 L/s, 743 kPa, 370 A, 513 V, 54 Hz, 1077 Rpm; 60% speed, 408 L/s, 748 kPa, 493 A, 545 V, 57 Hz, 1136 Rpm Check Valves Inspection Air Compressors Inspection Cleared/reset all alarms Station back to normal operations | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; out of service [equipment_failure]; alarm [control_system]; alarms [control_system] | sso [critical]; flood [critical]; out of service [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put two bags of soda ash into the aeration tanks and set two up for later,, started de-cant pump and collected the comp samples from yesterdays samples and delivered them to Harry Walker. completed Lab work and wasted 10m3 and added 4 bags of soda ash in total. leaned out post aeration tank and the entry flow gates and also washed down the UV channel. Went through the station sand filters working well, Bar screen just went OOS (flowing through by pass bar screen) I have put in a WO for maintenance. OC unit is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-24 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put two bags in and set two bags up to put in later, and started de-cant pump. Flushed both sand filter reject lines also checked both clarifiers - oil level OK,I did NOT drain the water as I did that 2 weeks ago - same for the greasing. Went through the station - sand filters working good. The OC unit is still OOS put station is running under normal ops. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-22 | Mount Albert Water Resource Recovery Facility | WW-CEAST | February 22, 2026 -09:15 - was on site to do sludge handling and weekend lab -started decant pump for sludge thickening tank upon arriving to site -received call, had to leave site for family emergency, ending my on-call and weekend work -notified ROC operator Ethan, who called the on-call manager to get another operator on site to finish weekend work - told Ethan to notify me of whatever operator is covering the work so I can let them know the status of site -was notified by ROC operator Ethan that Terry Reed was covering my on-call -11:28 called Terry Reed to give him a status update for the area, he did not pickup, left him a text message/iMessage explaining 'the decant pump is running, lab had not been started yet, no other work at the WRRF was started', text message said 'delivered', did not hear back from Terry Reed | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-02 | 2026-02-01 | Mount Albert Water Resource Recovery Facility | WW-CEAST | -On site for lab analysis and sludge handling work. -Entered lab results into SharePoint. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -OCU remains OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-17 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Put 2 bags of soda ash into the aeration tanks and set the next two up,, started the de-cant pump. went through the station - sand filters working good and i washed down the clarifiers scum trough. Cleaned out the post aeration tank and also the gates of the aeration inlet. Station running under normal ops - no issues were observed. Odour Control is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-12 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dropped in 2 bags of soda ash and set up 2 other bags for the aeration tanks also started de-cant pump. Started the Lab and sludge processing and entered results from the Lab into Sharepoint. Wasted 20m3 today and went through the Head works building - greased the travelling bar screen and cleaned out the back plate. Checked the vortex and both are turning. OC unit is still OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-11 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dumped two bags of soda ash into the aeration tank and set up the next two for later,, started de-cant pump and also collected weekly samples for the Lab,, Delivered samples to Harry Walker after collecting the samples at Mt. Albert PS. Back from drop off of the samples and checked all the cranes - all good and working. Went through the station and just the OC unit is still OOS. Rest of the station is running fine. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-10 | Mount Albert Water Resource Recovery Facility | WW-CEAST | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing. Decanted STT. Dumped remaining sludge into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Batch wasted 10 m3. Aeration, sludge and vortex blower belts, oil filters and oil levels checked. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action] | work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-10 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Dumped 2 bags of soda ash intro the aeration tanks and set 2 up for later,, also started the de-cant pump. Went through the station - sand filters working great , set up hose and flushed both reject lines. checked blower room - all looks good and the air compressors as well. Station running under normal ops - no issues were found, OC unit is still OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-05 | Mount Albert Water Resource Recovery Facility | WW-CEAST | came to the plant and set up the soda ash and turned the de-cant pump on for Marcos,, went to the pumping station and back at 11,, cleaned out the post aeration tank and also the inlet channel gates as well,, went through the station and everything is running fine. OC unit is still OOS though. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-06 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Completed Lab work and sludge processing,, entered results from the Lab into Sharepoint. Did not waste today and added 4 bags of soda ash. Had Alum delivery today (16000L) and Orlando to pick up the sludge. Went through the station - sand filters are working good and RAZ pumps have good flow. OC unit is still OOS, | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-04 | Mount Albert Water Resource Recovery Facility | WW-CEAST | Set up soda ash - put 2 bags in and 2 set up and waiting,, started de-cant pump and collected weekly samples for the Lab. After dropping off samples cleaned the scum trough - hosed it down till ice was gone. Went through the station and all looks good - Odour Control is still OOS but everything else looks good. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-13 | Mount Albert Pumping Station | WW-CEAST | Here to complete station check - entered readings into Share point,, verified the Hi wet well alarm with ROC and also verified Dialer alarm through the dry well flood alarm. Greased both pumps and activated the sump pumps to verify operation and checked the hoist down stairs - the hoist on the main floor is LOTO by maintenance. Checked both check valves and I could not find the building temp alarm - I will ask if there is a way to check Temp alarm. Station running under normal ops - no issues at all. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-21 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Feb 21 18:30 - inlet gate on bar screen 2 closed, bar screen 2 overtorque alarm, ongoing issue, will investigate when on site, bar screen 1 still in service Feb 25 6:00 - W11688345 created for bar screen 2, unable to reset alarm or run screen, need maintenance to investigate, bar screen 1 tripped too on overtorque, but was reset, and available | FLAG | stage1_keyword | 0.95 | Critical keyword match: tripped [equipment_failure]; trip [equipment_failure]; alarm [control_system] | tripped [equipment_failure]; trip [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | -on site for bar screen 1 overtorque, reset bar screen, watched it travel, no issues, over torque occurs upon flinging rags, bar screen 1 back in service -bar screen 2 overtorque, screen 2 remains OOS with inlet gate closed, cannot be reset, WO created for maintenance | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; wo created [maintenance_action] | oos [equipment_failure]; wo created [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-12 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Weather today Partly Cloudy and -7 Celsius -On site to complete work orders W11650108, W11593563, W11585171, W11560628. - Comprehensive Housekeeping. - 2026 IMS Emergency Procedure Quiz. - Odour Complaint Digital Forms Training ? Virtual. - Consolidated Monthly Surge Tank Inspection. - Surge tank and system inspection. - Surge tank valve and actuator exercise and inspection. - Surge tank drain valve inspection. - Transmission Line Flushing. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; work order [maintenance_action] | emergency [critical]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-19 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Weather today Partly cloudy and -2 Celsius -On site to complete work orders W11658045, W11658670. - Equalization Tank, Tipping Bucket Operational Check - Consolidated Wet Well Inspection, Overflow. - Bar Screen Cleaning/Lubrication. - Screw conveyor clean/lubrication. - Sluice gate valve/actuator exercise. - Wet well inspection and cleaning. - Wet well valve exercise. - High level alarm test. - Tipping bucket operational check. - Facility overflow inspection/clean. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; work order [maintenance_action]; alarm [control_system]; overflow [infrastructure] | overflow [critical]; work order [maintenance_action]; alarm [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-05 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | Weather today Mostly cloudy and -11 Celsius -On site to complete work order W11585114, W11639140, W11562343. - Check valve inspection. - Dry well flood alarm test. - Sump pit inspection. - High low temp alarm test. - Autodialer test. - Air Compressor Inspection. -Hoist Inspection. -All pumps available in timed auto duty rotation every 3 hours. -Standby power generator available in auto. -Checked dry well. -Checked bar screens room. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. - RS pump & motor inspection. Pump 1 - @ 0% speed 118.8 L/s, 135 kPa, 106 A, 622 V, 39 Hz; @ 25% speed 215.5 L/s, 145 kPa, 144 A, 622 V, 44 Hz; @ 35% speed 279 L/s, 166 kPa, 170 A, 624 V, 46 Hz Pump 2 - @ 0% speed 188.6 L/s, 147 kPa, 121 A, 384 V, 798 RPM, 40 Hz; @ 25% speed 332.6 L/s, 128 kPa, 152 A, 431 V, 895 RPM, 45 Hz; @ 100% speed 528.8 L/s, 181 kPa, 250 A, 574 V, 1193 RPM, 60 Hz Pump 3 - @ 0% speed 163.3 L/s, 139 kPa, 115 A, 371 V, 769 RPM, 39 Hz; @ 25% speed 232.4 L/s, 153 kPa, 153 A, 423 V, 877 RPM, 44 Hz; @ 35% speed 264.2 L/s, 152 kPa, 165 A, 445 V, 921 RPM, 46 Hz. Pump 4 - @ 0% speed 172.1 L/s, 149 kPa, 123 A, 623 V, 39 Hz; @ 25% speed 326.7 L/s, 144 kPa, 177 A, 622 V, 44 Hz; @ 35% speed 360.5 L/s, 154 kPa, 196 A, 622 V, 46 Hz. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; flood [critical]; work order [maintenance_action]; alarm [control_system] | sso [critical]; flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-07 | Newmarket Sewage Pumping Station & Equalization Tank | WW-CEAST | On site in response to mech screen 2 overtorque. Cleared the alarm and ran the screen on hand, noticed rake was slightly to the left touching the plate as it is moving upwards. Called ROC to call in 2nd Ops to close the inlet gate to screen 2 Marcus R on site to assist. Closed inlet gate to screen 2 and put both inlet gates 1 and 2 in remote to be able to operate it remotely without entering wet well. Notified ROC Screen 2 placed OOS, Screen 1 operating as intended. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 1
2026-02 | 2026-02-10 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | Weather today Light Snow and -5 Celsius -On site to complete work orders W11584817, W11578953. -Completed station check. -Entered station readings into SharePoint. -Consolidated Dry Well & Hoist System Inspection. - Hoist System Inspection. - Check valve inspection. - Dry well flood alarm test. - Sump pit inspection. - RS pump inspection. - RS pump motor / inspection. - Air relief valve inspection. - High low temp alarm test. - Autodialer test. -Pumps 1-4 RS pump motor / inspection. Pump 1 -15% - 80.7 L/s Pump 2 constant speed ? 194.1 L/s Pump 3 - 15% - 97.2 L/s Pump 4 - 15% - 82.9 L/s -All pumps available in timed-auto duty rotation every 4 hours. -Standby power generator available in auto. -Checked dry well, ok. -No outstanding alarms. -Station operations normal. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-13 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | Weather today Partly Cloudy and -13 Celsius -On site to complete work order W11594271, W11582123, W11582137. -Completed station check. -Entered station readings into SharePoint. - Ran pump 2 in local for a few minutes with a flow of 198.5 L/s at 114 kPa. -RS Pump Discharge valve actuator inspection and exercise the ones that would work. -Manual valve inspection and exercise. -All pumps available in timed-auto duty rotation every 4 hours. -Standby power generator available in auto. -Checked dry well, ok. - Meter Chamber 2 Flood Alarm shelved will pump out groundwater from chamber next week with warmer weather. -Station operations normal. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-03 | Newmarket Bogart Creek Sewage Pumping Station | WW-CEAST | Weather today Light snow and -5 Celsius -On site to complete work orders W11579572, W11570187. -Odour control scrubber system inspection. -at 8:30 Wessuc onsite complete Wet well scum removal. -Wet well backup control mode in pac while work is being completed. -Wet well backup control mode back in auto now. -Wet well scum removal work is completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; backup [infrastructure] | work order [maintenance_action]; backup [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | SEC Boxgove Corrosion Control Facility | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Chemical Tank 1 filled with water, Chemical Tank filled with H2O2 and OOS. -Comprehensive housekeeping tasks completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-20 | SEC Boxgove Corrosion Control Facility | WW-CEAST | -On site to complete work orders. -Turned off water to Chemical Tank 1, water at overflow level with HiHi level alarm in. -Ventilation system inspection completed. -Chemical tanks maintenance completed. -Sump pit system inspections completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; work order [maintenance_action]; alarm [control_system]; overflow [infrastructure] | overflow [critical]; work order [maintenance_action]; alarm [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | SEC Markham Odour Control Facility | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Fans impeller bearing lubrication completed. -Nutrient tanks batch mixing completed. -Comprehensive housekeeping tasks completed. -Fan 3 OOS with outlet gate fault. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; impeller [equipment_failure]; work order [maintenance_action] | fault [equipment_failure]; oos [equipment_failure]; impeller [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-17 | SEC Markham Odour Control Facility | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Fans impeller bearing lubrication completed. -Nutrient tank batch mixing completed - Nutrient pumps currently OOS. -Sump pump test and maintenance completed. Functionally tested sump pump and floats. -Water supply pumps, actuators exercise and inspection completed. Fully exercised all valves. -Hoist system inspections completed. -Fan 3 OOS with Outlet MV2 Fault. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; impeller [equipment_failure]; work order [maintenance_action] | fault [equipment_failure]; oos [equipment_failure]; impeller [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-13 | SEC Markham Odour Control Facility | WW-CEAST | -On site to complete comprehensive housekeeping tasks. -Inspected fault on Fan 3 Outlet MV2 Gate. Tried to exercise valve locally, but valve is continually faulting both opening and closing. Appears to be metal shavings around stem, possibly rubbing on metal frame. Will create a work request for maintenance team to investigate further. -Fan 3 OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; faulting [equipment_failure]; oos [equipment_failure] | fault [equipment_failure]; faulting [equipment_failure]; oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-05 | SEC Markham Odour Control Facility | WW-CEAST | -On site to complete work orders -Monthly diesel generator test run completed, readings entered into SharePoint. -1006 - Transferred station to generator power. -1106 - Transferred station back to utility power. -Generator start hours: 255.4, stop hours: 256.6, run time: 1.2hrs. -Damper and Knife Gate Sets 1-3, exercise and inspection completed. -Recirculation pump and strainer inspections completed. Currently Filter 2, Recirc Pump 2 is the only recirc pump in service. The rest of the recirc pumps are OOS with work request made for repairs/replacement. -OCF Damper Station GO2 Low and O2 Monitor 4 Alarms outstanding, work requests made to have sensors replaced. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | SEC Altona Air Handling Facility (Shaft 6/7) | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked fan room and generator. -Found small fluid leak below generator. Leak appears to be coming from fuel filter. Work request created for maintenance team to investigate issue. -Monthly JHSC H&S inspection completed, fire extinguisher in electrical room needs to be recharged. Supervisor notified to created work request for Property Services. -MAU fan found to not be running. Control panel display is blank and fan will not run locally as well. Property Services work request submitted by supervisor. -Heat trace system inspection completed. -Manually rotated fan duties while on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; work order [maintenance_action]; leak [infrastructure] | fire [critical]; work order [maintenance_action]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-27 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | -On site to complete work orders. -Reenabled BioFilter 2 BioScrubber Media DP Lo Alarm following repairs made to sensor. -Booster pump, solenoid valve, media spray checks completed on Filter 2 side. Fan 1/BioFilter 1 OOS. -Recirculation pump and strainer inspection completed. BioFilter 2, Recirc Pump 2 OOS. -Blower inspection completed. Fan 1 OOS. -Comprehensive housekeeping tasks completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system] | oos [equipment_failure]; work order [maintenance_action]; repair [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Fan 1 OOS, panel showing "14 Overtemp" fault after fan ran for less than two hours. Will create work request. -Nutrient tanks and pumps OOS. -Filter 2 BioScrubber Media DP and Drain pH sensors OOS, work requests created. -Comprehensive housekeeping tasks completed. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; work order [maintenance_action] | fault [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-18 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | -On site to perform a station check. -Station check completed, readings entered into SharePoint. -Fan 1 OOS, panel showing "14 Overtemp" fault after fan ran for less than two hours. Will create work request. -Nutrient tanks and pumps OOS. -Filter 2 BioScrubber Media DP and Drain pH sensors OOS, work requests created. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure] | fault [equipment_failure]; oos [equipment_failure]; overtemp [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Nutrient pumps and tanks OOS. -Monthly diesel generator test run completed, readings entered into SharePoint. -0916 - Transferred station to generator power. -1026 - Transferred station back to utility power. -Generator start hours: 262:48, stop hours: 264:03, run time: 1hr, 15min. -Monthly JHSC H&S inspection completed, no issues noted. -Fan 1 remains OOS. -Fan 2 running in auto with bypass knife gate open. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; oos [equipment_failure]; work order [maintenance_action] | bypass [critical]; oos [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-11 | SEC Pickering Odour Control Facility (York/Durham) | WW-CEAST | -On site to perform a station check. -Entered station readings into SharePoint. -Placed Fan 1 back in service following previous repairs. -Several low temperature alarms on the Fan 1/BioFilter 1 side of the station are outstanding. Checked instruments, no faults, all readings appear legitimate. All readings also appear to be slowly rising as well. F1 BioFilter Media Temp LoLo, CAU1 Outlet Temp Lo, and BFILT1 Outlet Temp Lo all oustanding. -F2 BioFilter Drain pH HiHi Alarm also outstanding, will create work request for instrumentation team. Sensor is displaying a "Sensor no communication" fault. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; repair [maintenance_action]; alarm [control_system]; alarms [control_system]; no communication [control_system] | fault [equipment_failure]; repair [maintenance_action]; alarm [control_system]; alarms [control_system]; no communication [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Craig Hendry arrived with the lockbox at 05:32. Wet well reached 4.98. Turned forcemain 2 back on. Opened force main 2. Removed LOTO on pump 4 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 4. Re engaged estop and reestablished LOTO. Closed forcemain 2 and turned it off Key and lockbox sent with Craig Hendry at 05:57 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-25 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Craig Hendry arrived with the lockbox at 00:57. Wet well reached 4.47 m. Turned forcemain 2 back on. Opened force main 2. Removed LOTO on pump 4 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 4. Re engaged estop and reestablished LOTO. Closed forcemain 2 and turned it off Key and lockbox sent with Craig Hendry at 01:22 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-23 | Vaughan Black Creek Pumping Station | WW-WEST | Arrived on site at 21:48 to meet with capital sewer and capital delivery for shut down of pumps, foremain valves and to stop all flow through forcemain while work is being performed Notified ROC of the work being performed Performed tailgate meeting with Craig Hendry and reviewed LOTO procedure Placed all pumps to manual at 22:00. Placed pumps 1, 4 and 5 into local off, estop engaged and LOTO three pumps. Disabled low level lockout Daniel Lemieux arrived at Black Creek to view all pipes due to not being able to find chamber 93-04. Accessed all pipes and gave him the coordinates to 93-04 and 93-05. Once Daniel Lemieux gave the okay, manually stopped pump 3. Started pumping down wet well from 3.74 m at 23:33 using VFD pump 2. While pumping down wet well, placed pump 3 into local off, estop engaged, and LOTO pump 3. Once wet well reached 0.80 m at 23:47 manually stopped pump 2. Placed it in local, estop engaged, and LOTO. Placed forcemain 1 into manual off. Placed both forcemain valves into local off from manaul. Capital delivery onsite to witness lockout procedure Once done, keys and lockbox sent with capital sewer at 23:50 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-24 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux. Craig Hendry arrived with the lockbox at 05:06. Capital sewer is done with the work and is letting it cure. Wet well at 3.8 m when Craig arrived. Allowed enough time to cure. Worked on forcemain 1 actuator valve with electrician on call (Satnam Mann) but could not get the valve to open. Will need to be investigated further. Work order created and at priority 4. Forcemain 1 OOS. Opened interconnect valve between forcemain 1 and 2 to allow pumps 1-3 to push flow into forcemain 2 (north forcemain). Opened forcemain 2. All pumps feeding forcemain 2. Removed LOTO on pump 2 and estop disengaged. At 6:03, when wet well level reached 4.98 m, began pumping the wet well down. Once wet well level reached normal operating parameters, shut off pump 2. Removed LOTO on pumps 1, 3, 4, Disengaged estop and placed the pumps to remote. Manually turned on pump 3 and placed it into auto, and in auto speed Placed pump 1, 3, 4 back into auto, and in auto speed. Kept pump 5 locked out due to it being OOS due to pump seal leak (WO created). Reenabled low level lockout Cleared all active alarms. Reset alarms on wet well backup panel. Reset dialer Checked once again that the plant is back to normal operation Inspected dry well before leaving. No issues | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action]; work order created [maintenance_action]; wo created [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; backup [infrastructure] | oos [equipment_failure]; work order [maintenance_action]; work order created [maintenance_action]; wo created [maintenance_action]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; backup [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Daniel mentioned that guys are out and Craig Hendry is on his way back with the lockbox. Craig Hendry arrived with the lockbox at 01:12. Wet well reached 5.11 m. Turned forcemain 1 back on. Opened force main 1. Removed LOTO on pump 2 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 2. Re engaged estop and reestablished LOTO. Closed forcemain 1 and turned it off Key and lockbox sent with Craig Hendry at 01:37 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-24 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Daniel mentioned that guys are out and Craig Hendry is on his way back with the lockbox. Craig Hendry arrived with the lockbox at 23:22. Wet well reached 4.95 m. Turned forcemain 2 back on. Opened force main 2. Removed LOTO on pump 4 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 4. Re engaged estop and reestablished LOTO. Closed forcemain 2 and turned it off Key and lockbox sent with Craig Hendry at 23:52 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-24 | Vaughan Black Creek Pumping Station | WW-WEST | Arrived on site at 21:52 to meet with capital sewer for shut down of pumps, foremain valves and to stop all flow through forcemain while work is being performed Notified ROC of the work being performed Performed tailgate meeting with Craig Hendry and reviewed LOTO procedure Placed all pumps to manual at 22:00. Placed pumps 1, 2 and 5 into local off, estop engaged and LOTO three pumps. Disabled low level lockout Once Daniel Lemieux gave the okay, manually stopped pump 3. Started pumping down wet well from 3.72 m at 22:02 using VFD pump 4. While pumping down wet well, placed pump 3 into local off, estop engaged, and LOTO pump 3. Closed forcemain 1. Once wet well reached 0.80 m at 22:16 manually stopped pump 4. Placed it in local, estop engaged, and LOTO. Closed forcemain 2. Turned breakers off for forcemain 1 and 2 Once done, keys and lockbox sent with capital sewer at 22:20 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-24 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Requested Daniel to recall guys and send lockbox back at 03:17 Craig Hendry arrived with the lockbox at 3:27. Wet well reached 5.48 m due to forcemain 1 valve over torque. Could not reset the over torque. Turned on breaker for forcemain 2. Opened forcemain 2. Removed LOTO and disengaged estop on pump 4. Used pump 4 to pump down wet well. Once wet well reached 0.8 m, shut off pump 4. Reengaged e stop and reestablished LOTO. Requested maintenance on call to troubleshoot south forcemain valve over torque Closed forcemain 2. Powered off Key and lockbox sent with Craig Hendry at 4:07 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-27 | Vaughan Black Creek Pumping Station | WW-WEST | - Checked screen, oil is good. Levelled bin - Performed housekeeping. Cleaned toilet and took garbage out - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 589.8 L/s, pressure 300 kPa Pump 2: 453 L/s at 100%, pressure 265 kPa Pump 3: 134.8 L/s at 100% speed, pressure 215 kPa Pump 4: 475 L/s at 100% speed, pressure 264 kPa - Checked station and recorded readings on SharePoint. Trends okay. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-25 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Craig Hendry arrived with the lockbox at 03:03. Wet well reached 5.20 m. Turned forcemain 2 back on. Opened force main 2. Removed LOTO on pump 4 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 4. Re engaged estop and reestablished LOTO. Closed forcemain 2 and turned it off Key and lockbox sent with Craig Hendry at 03:32 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-25 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux. Craig Hendry arrived with the lockbox at 07:07. Capital sewer is done with the work and letting the epoxy cure. Wet well at 4.15 m when Craig arrived. Removed LOTO on pump 4 and estop disengaged. Opened forcemain 2. At 7:34, when wet well level reached 5.14 m, began pumping the wet well down. Once wet well level reached normal operating parameters, shut off pump 4 Removed LOTO on pumps 1, 2, 3, Disengaged estop and placed the pumps to remote. Opened forcemain 1. Manually turned on pump 3 and placed it into auto, and in auto speed Placed pump 1, 2, 4 back into auto, and in auto speed for VFD pumps. Removed loto and disengaged estop for pump 5. Kept pump 5 in local off due to pump 5 being OOS (pump seal leak, WO already created). Reenabled low level lockout Cleared all active alarms. Reset alarms on wet well backup panel. Reset dialer Checked once again that the plant is back to normal operation Inspected dry well before leaving. No issues | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; backup [infrastructure] | oos [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure]; backup [infrastructure] |  | 1 | 0
2026-02 | 2026-02-13 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux. Craig Hendry arrived with the lockbox at 02:40. Capital sewer is done with the work and is letting it cure. Wet well at 4.25 m when Craig arrived. Allowed enough time to cure. Turned forcemain 1 into manual. Opened force main 1. Removed LOTO on pump 2 and estop disengaged. At 3:18, when wet well level reached 5.10 m, began pumping the wet well down. Once wet well level reached normal operating parameters, shut off pump 2. Turned forcemain 2 back to open. Removed LOTO on the remaining pumps 1, 3, 4. Disengaged estop and placed the pumps to remote. Manually turned on pump 3 and placed it into auto, and in auto speed. Placed pump 1, 3, 4 back into auto, and in auto speed. Kept pump 5 in manual due to it being OOS. Reenabled low level lockout Cleared all active alarms. Reset alarms on wet well backup panel. Reset dialer Checked once again that the plant is back to normal operation Inspected dry well before leaving. No issues Update: removed loto on pump 5 and disengaged estop. Left the pump in local. Cleared e stop alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system]; backup [infrastructure] | oos [equipment_failure]; alarm [control_system]; alarms [control_system]; backup [infrastructure] |  | 1 | 0
2026-02 | 2026-02-13 | Vaughan Black Creek Pumping Station | WW-WEST | Monitored wet well level and kept communication with Daniel Lemieux. Daniel notified he will be recalling guys and sending the lockbox back at 00:48 before doing concrete work Craig Hendry arrived with the lockbox at 01:00. Wet well reached 4.49 m, peak. Turned forcemain 1 into remote. Opened force main 1. Removed LOTO on pump 2 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 2. Re engaged estop and reestablished LOTO. Closed forcemain 1 and turned it off Key and lockbox sent with Craig Hendry at 01:25 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-13 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check and weekly pump run test Station check ok - no new issues. Bar screen oil levels good and leveled bin. Pump run test: Pump1 562.7L/s at 297kpa Pump 2 - 448.4L/s at 265kpa at 100% Pump 3 132.9L/s at 214kpa at 100% Pump4 - 471.7L/s at 263kpa at 100% Pump 5 -OOS | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-20 | Vaughan Black Creek Pumping Station | WW-WEST | - Checked screen, oil is good. Levelled bin - Pushed bin back in - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 570.2 L/s, pressure 305 kPa Pump 2: 450 L/s at 100%, pressure 267 kPa Pump 3: 132.4 L/s at 100% speed, pressure 214 kPa Pump 4: 466 L/s at 100% speed, pressure 265 kPa - Checked station and recorded readings on SharePoint. Trends okay. Noticed high vibration on pump 1. Will monitor | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; vibration [equipment_failure]; work order [maintenance_action] | oos [equipment_failure]; vibration [equipment_failure]; work order [maintenance_action] |  | 1 | 1
2026-02 | 2026-02-12 | Vaughan Black Creek Pumping Station | WW-WEST | Arrived on site at 21:50 to meet with capital sewer and capital delivery for shut down of pumps, foremain valves and to stop all flow through forcemain while work is being performed Notified ROC of the work being performed Performed tailgate meeting with Craig Hendry and reviewed LOTO procedure Placed all pumps to manual at 22:08. Placed pumps 1, 4 and 5 into local off, estop engaged and LOTO three pumps. Closed forcemain 2, manual off Once Craig Hendry gave the okay, manually stopped pump 3. Disabled low level lock out. Started pumping down wet well from 3.74 m at 22:13 using VFD pump 2. While pumping down wet well, placed pump 3 into local off, estop engaged, and LOTO pump 3. Once wet well reached 0.80 m at 22:31. manually stopped pump 2. Placed it in local, estop engaged, and LOTO. Placed forcemain 1 into manual off. Placed both forcemain valves into local off from manaul off Capital delivery onsite to witness LOTO procedure Once done, keys and lockbox sent with capital sewer at 22:35 Monitored wet well level and kept communication with Daniel Lemieux, foreman onsite. Notified Daniel to recall guys and send lockbox back at 23:14 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-12 | Vaughan Black Creek Pumping Station | WW-WEST | Craig Hendry arrived with the lockbox at 23:28. Wet well reached 4.30 m. Turned forcemain 1 into remote. Opened force main 1. Removed LOTO on pump 2 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 2. Re engaged estop and reestablished LOTO. Closed forcemain 1 and turned it off Key and lockbox sent with Craig Hendry at 23:52 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-06 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite for station check - no new issues reviewed trends and added data into SharePoint. Completed weekly RS pump run test - no new issues Pump1 -573.1L/s at 297kPa Pump 2 - 453.2 L/s at 100% at 262kPA Pump 3 131.3L/s at 100% and 215kPA Pump4 - 460.3 L/s at 100% at 265kPA Pump 5 -OOS pumps placed back into Auto and put in duty. Pump 5 remains in manual OOS Inspected seal water and cleaned screens - all clear and functioning. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-09 | Vaughan Black Creek Pumping Station | WW-WEST | Onsite with Young Jung for work orders. ROC notified of work being done. Completed consolidated dry well inspection - Triggered hi/lo temperature alarm and dry well flood alarms. Tested dry well sump pit with floats, no issues. Inspected Check valves - no new issues. Placed pumps 1,2,4 and 5 into manual off to Exercise suction valves on pumps 1,2,4 and 5. Pumps placed back into auto. Pump 5 left in manual off Flushed air relief valves. Completed consolidated wet well work order. Greased and inspected bar screen - no new issues. Manually exercised valves in wetwell. Trigger wetwell overflow alarm 1 and 2. Hosed down and cleaned debris in wetwell | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-04 | Vaughan Humber Pumping Station | WW-WEST | - On site for wet well inspection and cleaning - Tested the wet well high level alarm. Alarm received. No issues - Tested the metro overflow alarm by tripping the float. Alarm received. - Overflow to Toronto maintenance hole also tested. alarm received - Exercised wet well valves. Greased fittings. The isolation gate after the screen is very stiff - Cleaned wet well - Inspected the bar screen and checked oil. No issues. Greased fittings - Levelled bin and pushed bin back in | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; trip [equipment_failure]; alarm [control_system]; overflow [infrastructure] | overflow [critical]; trip [equipment_failure]; alarm [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | Kleinburg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:30. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Scum Tank Flushing Complete. Returned to Auto and Service. Lowered Sludge Thickening Tank #2 Decant Slip Tube. Found Filter Air Lift Clogged. Cleared Obstruction and Returned to Service. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Flushed Bar-screen Dewatering Press Drainage Line with No Issues. Returned to Service. Topped Up Soda Ash Hopper ?> 8 Bags. Reject Sump Pump #1 Fault Alarm Outstanding. Reset Fault and Cleared Alarm. Returned Pump to Service. Known Issue, WO Made and Pending for Maintenance. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Clarifier #1 and 13 m3 from Clarifier #2. Inspected and Flushed Filter Reject Wash Boxes, Weirs and Air Lifts with No Issues. Completed Biorem Odour Control Unit Inspection. All Equipment Operational, All Parameters within Optimal Rates. Recirculation Water pH Analysis: 2.79. Greased Blower Driveshaft Bearings. No New Issues Found. Completed Filter Bypass and Alum Containment Float Alarm Tests with No Issues. Confirmed Reception by the ROC. Cleared Associated Alarms and Returned to Service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; sso [critical]; fault [equipment_failure]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure]; containment [safety] | bypass [critical]; sso [critical]; fault [equipment_failure]; alarm [control_system]; alarms [control_system]; clog [infrastructure]; clogged [infrastructure]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-12 | Kleinburg Water Resource Recovery Facility | WW-WEST | Onsite for consolidated headworks work order Greased vortex 1 and 2 while running. Placed both vortex 1 and 2 into off and E stop. Check oil levels - both good. Cleaned rags from blades of both vortex 1 and 2. Both operate normally. Greased traveling bar screen while in operation. Then placed in off and E stop. Placed auger into off and E stop. Checked oil levels in both gear boxes - both ok. Cleaned rags from bar screen and flushed auger. Placed back into operation Greased grit declassify screw and checked oil levels - oil levels ok. | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action] | work order [maintenance_action] |  | 1 | 0
2026-02 | 2026-02-17 | Kleinburg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:25. Lowered Sludge Thickening Tank #2 Decant Slip Tube. Reject Sump Pump #1 Fault Alarm Outstanding. Reset Fault and Cleared Alarm. Returned Pump to Service. Known Issue, WO Made and Pending for Maintenance. Topped Up Soda Ash Hopper ?> 14 Bags. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Rotated RAS Pump Duties. Pumps #2 and 4 Manual Off, Pumps #1 and 3 in Auto. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Completed Biorem Odour Control Unit Inspection. All Equipment Operational, All Parameters within Optimal Rates. Recirculation Water pH Analysis: 2.43. No New Issues Found. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 15 m3 from Each Clarifier. Received Alum Delivery. Reviewed and Signed Documentation. Alum Tank Level: 0.95 ?> 3.58m. Alum Tank Hi and HiHi Alarms Remain Outstanding Until Tank is Gradually Drawn Down. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; alarms [control_system] | fault [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | Kleinburg Water Resource Recovery Facility | WW-WEST | Onsite for consolidated blower inspection work order. Notified ROC of work being done. Placed sludge holding tank blower 1 in manual off and LOTO generating E stop alarms - checked belts, filter and oil levels all ok. Placed back into auto and swapped duties to place sludge blower 2 into manual and LOTO generating e stop alarm. checked belts, filter and oil levels all ok. Placed back into auto. Both blowers operating normally. Place vortex blower 1 into off and checked belts, filter and oil levels. All ok. Placed back into auto Placed vortex blower 2 into off and checked belts, filter and oil level. All ok placed back in auto. Both blowers operating normally. Placed diversion tank blowers 1 and 2 into local off generating E stop alarms checked belts, filters and oil levels. All ok. Placed aeration tank blower 2 into off manual and LOTO generating e stop alarms. Checked belts, filter and oil levels all ok. Placed back into auto and rotated duties to place aerating tank blower 1 into manual off and LOTO generating e stop alarms. Checked belts, filter and oil level - all ok. Placed back into auto. Manually exercised aeration tank butterfly valves. Assisted Marcus with clarifier inspection WO | FLAG | stage1_keyword | 0.95 | Critical keyword match: work order [maintenance_action]; alarm [control_system]; alarms [control_system] | work order [maintenance_action]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-06 | Kleinburg Water Resource Recovery Facility | WW-WEST | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 9:00. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 12 m3 from Clarifier #1 and 15 m3 Clarifier #2. Topped Up Soda Ash Hopper ?> 9 Bags. Inspected Filters and Compressors. Flushed Reject Wash Boxes, Weirs and Air Lifts. Tested Compressor Condensation Flushing Solenoids with No Issues. Completed Circular Plant Clarifier and Drive Inspection. Did Not Test Run Unit due to Ice within Clarifier. No Issues Found. Unit Remains OOS. | FLAG | stage1_keyword | 0.95 | Critical keyword match: sso [critical]; oos [equipment_failure] | sso [critical]; oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-17 | King City Pumping Station | WW-WEST | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Rotated manual OOS pump from pump 2 to pump 3. Bar screen flushed and functioning normally. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-05 | King City Pumping Station | WW-WEST | Onsite for work orders. Called ROC to inform of generator run test, and alarms being tested. Transferred power from hydro to generator at 9:07am. Recorded data to SharePoint. Transferred power from generator back to hydro at 10:15am. Transferred smoothly. Maintenance onsite for RS pump inspection PMs Completed dry well inspection - all pumps run ok, check valves operating properly Triggered hi-Lo temp alarm. Triggered dry well flood alarm and tested dry well sump pit. Triggered diesel containment flood alarm. Completed JHSC inspection and checked plant for hazardous waste. Flushed and checked bar screen - no issues. Bin placed out for pick up | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; hazard [safety]; containment [safety] | flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; hazard [safety]; containment [safety] |  | 1 | 0
2026-02 | 2026-02-04 | King City Pumping Station | WW-WEST | Onsite with Young Jung for consolidated wetwell work order. Notified ROC of work being done. Cleaned and inspected bar screen - greased bar screen and flushed. Triggered wetwell overflow alarms. Exercised wetwell valves Cleaned debris from wetwell. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-06 | Nobleton Janet St. Sewage Pumping Station | WW-WEST | Attending site to replace failing diesel tank level transmitter (W11475801). Replace, configured and verified diesel tank level. ROC was notified before and after maintenance activities. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-03 | Vaughan Pine Valley Pumping Station | WW-WEST | Onsite for station check and work orders. Called ROC to inform of generator run test Completed station check - no new issues reviewed trends and added data into SharePoint. Transferred power from hydro to generator at 12:28pm. Transferred power back to at 1:30pm. Transferred no issues. Completed consolidated dry well inspection - all ok. Tested sump pit floats and dry well flood alarm - triggered alarm Tested hi Lo temperature alarms. Inspected odour control unit - no new issues. At 0.4inches of water. Completed JHSC inspection and checked station for hazardous waste | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; hazard [safety] | flood [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; hazard [safety] |  | 1 | 0
2026-02 | 2026-02-02 | Schomberg Water Resource Recovery Facility | WW-WEST | On site to continue work on effluent pump 3. Effluent pump 3 is still out of service. | FLAG | stage1_keyword | 0.95 | Critical keyword match: out of service [equipment_failure] | out of service [equipment_failure] |  | 1 | 1
2026-02 | 2026-02-05 | Schomberg Water Resource Recovery Facility | WW-WEST | In Responding to Filter Room Smoke Alarm Communicated by the ROC. No Signs of Fire Evident. Ventilated Filter Room, Cleaned and Inspected Smoke Detector. Returned to Service. Alarm Acknowledged and Reset. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; smoke [equipment_failure]; alarm [control_system] | fire [critical]; smoke [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-05 | Schomberg Water Resource Recovery Facility | WW-WEST | Installed stop logs in headworks to divert all incoming flow to lagoon at 7:54 am. Ran effluent pumps manually to pump out effluent tank. Shut off plant service water system. Shut off filter reject pumps. Shut off plant sewer pumps. Shut off filter sump pumps. Pumped uv/effluent channel in to lagoon overflow. Shut off UV banks. Completed station check. No issues found. Completed labs and entered data in ace sheets. Completed consolidated blower inspection work order. Added oil to aeration blower 1. Otherwise, all good. GFL entered effluent tank to suck out sludge and pressure wash walls. GFL sprayed walls down with sodium hypochlorite. 11:08 turned UV banks back to auto/on. Removed stop logs from headworks to return flow to plant. Set filter sump pumps to auto. Set filter reject pumps to auto. Set plant sewer pumps in auto. Set plant service water system to auto. Effluent tank full and overflowing to lagoon at 13:23. Added dechlorination pucks to effluent tank at 13:23. Turned effluent pumps to auto at 14:43. Tested effluent pumps. All three make appropriate flow. Reset duties for filter reject and effluent pumps. Reset all alarms. Plant back to normal, but with clean effluent tank. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-09 | Schomberg Water Resource Recovery Facility | WW-WEST | Supernated STT and released to SHT. Completed labs and entered data in ACE sheets. Completed station check. No issues found. Exercised SHT overflow valve. Test SHT high level float. ROC received alarm. Completed consolidated headworks work order. ROC received alarms. | FLAG | stage1_keyword | 0.95 | Critical keyword match: overflow [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] | overflow [critical]; work order [maintenance_action]; alarm [control_system]; alarms [control_system]; overflow [infrastructure] |  | 1 | 0
2026-02 | 2026-02-26 | ROC General | ROC | KSSP, Ian W testing a new UV Bypass alarm at KSSP. Please disregard until further notice | FLAG | stage1_keyword | 0.95 | Critical keyword match: bypass [critical]; alarm [control_system] | bypass [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | ROC General | ROC | SECC - Jonathan from Property services on site for fire alarm testing. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | ROC General | ROC | MAPS- Chris from Property Service onsite for fire test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical] | fire [critical] |  | 1 | 0
2026-02 | 2026-02-20 | ROC General | ROC | NMSSBP - Pat B. from Property services is on site for fire alarm testing 08:18 - Pat is finished on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | ROC General | ROC | YDOC - Jonathan from Property services testing fire alarm will attend SEOC OCF next. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | ROC General | ROC | SEOC67 - Jonathan from Property services on site for fire alarm testing. 11:20 Off site | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | ROC General | ROC | AUSS - Pat B. from Property Services is on site and will be testing the fire alarm 10: 19 - Pat is finished on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical]; alarm [control_system] | fire [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-04 | ROC General | ROC | SEOC4 - Donald (Magnum Fire, 4167861418) on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical] | fire [critical] |  | 1 | 0
2026-02 | 2026-02-04 | ROC General | ROC | SEOC OCF - Donald from Magnum fire leaving site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical] | fire [critical] |  | 1 | 0
2026-02 | 2026-02-04 | ROC General | ROC | SEOC OCF - Donald from Magnum Fire protection on site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fire [critical] | fire [critical] |  | 1 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | GWTP- Sutton header turbidity hi alarm came in D1 not active. UV 1 minor fault and lo UV irradiance. Notified Jack P will take a look at both issues on site KSTP- Post Cl2 lo vacuum alarm came in. Notified Jerry Z Post Cl2 1 working okay and Fluoride res stil low. Jerry Z aware and directed to disregard and give it time to recover | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | KSETDP - Chris S on site, working on altitude valve programming, requested disregard PAC commfail alarm. ET offline, Dan Z on site to assist . | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | KCETDS- PAC comm fail on site. Trends okay. cleared upon acknowledgment | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AUPSWS, Jerry Z on site, testing temp/flood and running generator | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical] | flood [critical] |  | 1 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | NMW15- Placed well man/on for Dan B MAPS PD7- Chris I done on site P4 OOS KSTKWP- Tower level hihi alarm came in. Patrikc F still making adjustments to help KSETDP fill AUETFC- Kyle C on site STETTL- Lane from town of Stouffville is flushing in system | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | MTW12- Silicate P1/2 OOS. Notified Phil D will investigate on site | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SUETDR - Jackie S on site. Building Flood Alarm cleared. Jackie S leaving site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SUETDR - Building flood alarm. Notifies Jackie S. She will attend site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | MKMCLA- Comm Fail. Alarm cleared after about 45 minutes. Gap in trends. Will inform PCS and Linear. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | KSTKWP - Jerry Z on site for a chlorine leak test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | AUW57 - Joe D working on site, testing chlorine leak. Directed Well 5 pump man/off for the duration of the work. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | VNPSAP - Joe W on site to complete a temperature alarm test and a flood alarm test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NMPSKC, Dan B on site, Working on pumps 5 and 6. Dan B will have to cut the power to the site. Power loss at NMPSKC will last for 30 minutes. Once power is restored, Pumps 5 and 6 will be OOS while pumps 1-4 will be available if needed | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-23 | All Water System ROC General | ROC | Hub 1/Hub 2 Server/HLW12/HLETYS/STETTL/NMSSHS/STW12, Comm Fail alarms, contacted Yash S, he will look into it 09:24, Comms/Trends have been restored | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | SUETDR, Building Flood Alarm, notified Jackie S, she will head to site to investigate the issue CMU5: W11694960 | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-24 | All Water System ROC General | ROC | NMW12 - Alex B on site to complete work orders including JHSC checks, ammonia system inspection, chlorin system inspection, flood alarm test, chlorine leak detection test, chlorine analyzer maintenance and if there is time a silicate system inspection. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] | flood [critical]; work order [maintenance_action]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-26 | All Water System ROC General | ROC | AUW57, Joe D finished on site, will be placing the well back to auto once the cycle is done. Cl2 Pump 2/Booster 2 will be OOS for the night on site. If Cl2 Pump 1/Booster 1 has issues, contact on call | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-27 | All Water System ROC General | ROC | NMW15- Treated free hihi alarm came in. Well not active no water directed to users. Continue to monitor trends did not recover. Placed well in man/off emailed Central water team | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-25 | All Water System ROC General | ROC | AUW14- Building flood alarm came in. Notified Joe D on site will investigate | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-01 | All Water System ROC General | ROC | STRS48 - High lift pump 1 fail to stop alarm. Checked site, SCADA shows the pump as active but no flow is registered on the flow meter. While monitoring the pump showed as deactivated. Able to clear alarm. Pump was re-assigned duty 1 automatically. | FLAG | stage1_keyword | 0.95 | Critical keyword match: scada [control_system]; alarm [control_system] | scada [control_system]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | SHTP- KMNO Pump 1 Leakage Alarm. Pump 1 Fault Alarm. Pump 2 rotating in and out of duty 1. Notified Cole W. He will take a look. 05:00- Cole W will attend site W11664772 CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] | fault [equipment_failure]; alarm [control_system]; leak [infrastructure]; leakage [infrastructure] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | QVW34- P4 VFD fault and Estop. Called Will M. Maintenance Ops on site replacing motor on P4 | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCPSDS- Comm fail. Ack/reset. Alarm cleared right away. Trends okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | AUPSRR - Donald M performing w/o on site including: Chlorine analyzers maintenance, chem scan maintenance, testing ammonia flood alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-11 | All Water System ROC General | ROC | JFPS- Lee F finished onsite. Requested to leave pump 2 man/off. Can run in emergency. | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical] | emergency [critical] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | VNRSKS - Dave T on site for flood alarm test and health and safety inspection. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | AUW14 - Ammonia pump 1 fault alarm at duty stop. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | HLW2 - Treated total chlorine , combine chlorine residual low alarms. Well 2 duty not active, no water directed to users. Chlorine residual value recovered, alarms cleared. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | MKRSEM- Called Metro spoke with Pouran to start 2 pumps RHPSPA- Travis W on site to Gen test run, surge valve test and perform valve exercises AURSBS- CL2 iso valve1/2 failed to open. ack reset aalrms. Found Post total and free Cl2 analyzers in calibration mode. Notified Donald M. Directed to disable calibration mode on both analyzers. KSTP- Artour L on site to commission diesel tank LITs QVETQS- Jay G on site to clean outlet analyzer. Taking grab on site while working on analyzer. NMETIB- Deactivated at 72% NMETHW- Activated D1 at 48% AURSBS- Post injection free hihi switch alarm came in. Notified Donald M. Will attend site to 0 analyzer. Created CMU5 W11676555 SHTP-Jake M returned planet to normal Ops #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: failed [equipment_failure]; alarm [control_system] | failed [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | KCETDS- Comm fail. Alarm cleared upon acknowledgement. Trends okay | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | HLW2- Ammonia Pump 1 Fault Alarm. Ammonia Pump 2 took over in duty 1. Cleared alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | NMTKKC - Jason G testing flood alarm and performing chlorine and ammonia systems maintenance. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | MARS- Dave T on site for Cl2 analyzer maintenance, JHS inspections and to test flood alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMTKKC - Header ammonia LoLo, outlet total amonia LoLo alarms, Historian heartbeat alarm, called Jason G( running gen at NMPSKC). Jason G will check. NMW12 - interlocked on NMTKKC to NMW12 commfail. Alarm cleared. NMTKKC - Historian Heartbeat alarm. Notified Ian W, he will check. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-21 | All Water System ROC General | ROC | NBW5- Influent Free CL2 Lo Alarm. Value recovered. Effluent Free CL2D Lo Alarm and Effluent Free Chlorine LoLo Switch alarm came in shortly after. Well interlocked. Notified Tim H. He will attend site. Tim H requested to change Influent Lo Alarm from 1.0 to 1.5 and Effluent Lo Alarm from 0.65 to 1.0 16:54- Tim H finished onsite. He will leave well man/off for the weekend. Requested a call if needed to run in emergency. W11679721 CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: emergency [critical]; alarm [control_system] | emergency [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | MKPSSA, Travis W on site, Running generator/Testing pumps and testing flood alarms. notified Toronto of this work as well, they shouldn't be impacted | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | HLW2 - Ammonia Pump 1 fault alarm, Cole W will attend site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | BVPS- Dan Z on site to work on analyzers and testing flood alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-12 | All Water System ROC General | ROC | QVW12 - William M on site for turbidity meter maintenance and chlorine leak test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: leak [infrastructure] | leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-15 | All Water System ROC General | ROC | BLW3 - Patrick F finished at site. Leaving chlorinator 1 OOS for the weekend, disregard well 3 percent decline alarm. Will bring it up to team start of week | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system] | oos [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | MTW3 - Chlorine gas leak, scrubber running. Informed Patrick F, will head to site CMU = 11670914 | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; leak [infrastructure] | gas leak [critical]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-14 | All Water System ROC General | ROC | VNRSKS to COTFA Comm Alarm COTFA to MARS Comm Fail COTFA to RHRSWA Comm Fail COTFA to ROYKS Comm Fail COTFA to VNETAG Comm Fail COTFA to VNPS7 Comm Fail COTFA to VNPS8 Comm Fail JFPS to COTFA Comm Fail NRETBR to COTFA Comm Fail RHPSWA to COTFA Comm Fail All alarms Cleared | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-18 | All Water System ROC General | ROC | STPSMR - Travis W working on site, deactivating duty , testing chlorine leak alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | RHRSWA- Pac Panel died on site lossing comms. RHPSPA interlocked due to comm fail/ Notified Tim H. Time H req consult with Ian W to troubleshoot. Notified Ian W to call Tim H. MKRSMR- Called Metro spoke with Pouria activated D1 | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | GWTP- Patrick F on site to test chemical leak alarms and flood alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | flood [critical]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NMW15 - PAC commfail. PCS working on NMETYS to NMW15 communication as per Alex B. | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-13 | All Water System ROC General | ROC | QVW12 - Jerry Z on site, requested to disregard chlorine room gas leak alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | HLW2 - Ammonia pump 1 fault. Pump 2 able to run. Able to clear pump 1 fault | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure] | fault [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | VNETFD- Angelica C and Tim H on site to test hi lo temp and flood alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-22 | All Water System ROC General | ROC | MTW3 - Chlorine Gas Leak alarm came in. Well was not running. Called Dan Z. who will attend site. CMU5 Created W11679951 23:26 - Dan Z. called back to inform that MTW3 will be OOS for the night as a minor leak has been identified. Both cylinders are now closed. #CONSULT #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; oos [equipment_failure]; not running [equipment_failure]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; oos [equipment_failure]; not running [equipment_failure]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-20 | All Water System ROC General | ROC | MTW3 - Chlorine Gas Leak alarm came in. Called Phil D. who will head to site. CMU5 Created W11679209 #CMU5 | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; alarm [control_system]; leak [infrastructure] | gas leak [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | HLW2 - Stephen B leaving site to grab supplies from HLW1 and will be back to change cylinders at HLW2 with Jacob M STPS48- Lee F on site to work on high lift P2 NMTKKC- Ian W and Jay G done on site. Jay G will activate D1 with chem system off and place back in auto once flow stabilizes. NMPSKC- Pac Comm fail came in on site. Notified Jay G who will consult with Ian W | FLAG | stage1_keyword | 0.95 | Critical keyword match: |  |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | JFPS- WPS P2 failed to start and MV2 failed to close alarms came in as power transferred back to utility cleared alarms KSETDP- Jackie P on site to test lo temp, Cl2 leak alarms and perform JHS inspections AUW57- Joe D on site to get well back on line. MAPS- Dave T on site to test lo temp, Gas leak alarms and perform JHS HVAC inspections BLW3- Phil D on site to work on silicate and Cl2 systems. Dan Z also on site to test alarms on site and directed to disregard all alarms on site until done | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; failed [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] | gas leak [critical]; failed [equipment_failure]; alarm [control_system]; alarms [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-10 | All Water System ROC General | ROC | NBW56 - Jordan B on site, cleaning chlorine analyzers and testing chlorine leak alarm. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-16 | All Water System ROC General | ROC | HLW2- Treated Total and Combined Cl2 lo alarms came in. Well not active no water directed to users and alarm cleared after 3 mins | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; alarms [control_system] | alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-19 | All Water System ROC General | ROC | RHPSWPA, Travis W on site, testing flood alarms | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-17 | All Water System ROC General | ROC | VNP8 - Proc sump pump 1 & 2 fault, able to clear RHRSTR - Site power failure, able to clear as site continuous to run on generator | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; failure [equipment_failure] | fault [equipment_failure]; failure [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-04 | All Water System ROC General | ROC | JFPS - David T. testing flood alarm ANW23 - Stephen B. working on NTU analyzer | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system] | flood [critical]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | NMTKKC- Jason G onsite for work orders. May receive hi sanitary pit, flood alarm, hi/low temp, process room flood. Will also be working on chlorine analyzers later on | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; work order [maintenance_action]; alarm [control_system] | flood [critical]; work order [maintenance_action]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | KSETWB - Jackie S on site performing w/o, including - Chlorine gas leak test, chlorine analyzer maintenance, recirculation pump run, valves exercising. | FLAG | stage1_keyword | 0.95 | Critical keyword match: gas leak [critical]; leak [infrastructure] | gas leak [critical]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | HLW1 - Stephen B on site for chlorine leak alarm test, chlorine analyzers maintenance. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | SHTP - Jacob M working on chlorine system, testing chlorine leak alarm and running generator. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | NMW136 - Well 16 pump fault alarm. Checked site, unable to clear alarm. Rotated duty 1 to pump 16. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system]; pump fault [infrastructure] | fault [equipment_failure]; alarm [control_system]; pump fault [infrastructure] |  | 1 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | SHTP, KMNO Pump 2 Leak/Fault, Notified Jacob M, he will look into it | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; leak [infrastructure] | fault [equipment_failure]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | VNPS - Tim H running generator , will attend re- chlor after for chlorine analyzers maintenance and chlorine leak alarm test. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | JFPS- Tyler S called. Pump 1 will remain OOS Local off RHPSWA- Tyler S also notified that Pump 1 will remain Local off | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure] | oos [equipment_failure] |  | 1 | 0
2026-02 | 2026-02-03 | All Water System ROC General | ROC | GWTP Low lift Patrick F cleaning turbidity meter, chlorine analyzers, testing chlorine leak alarm and Health and Safety check. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system]; leak [infrastructure] | alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMTKKC - Commfail alarm, not able to deactivate Duty 1. Notified Jason G. NMTKKC - Ian W will call Jason G . | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-05 | All Water System ROC General | ROC | MKRSMR - Travis W testing flood alarm, Hi/low level alarms, chlorine analyzers maintenance and performing Health and safety inspection. | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; alarms [control_system] | flood [critical]; alarm [control_system]; alarms [control_system] |  | 1 | 0
2026-02 | 2026-02-07 | All Water System ROC General | ROC | MTW3 - SIlicate pump 1 fault alarm. Checked site, well has been running for several hours. Silicate pump duty rotated to silicate pump 2 and normal operations resumed. Unable to clear alarm. Sent mail to OCO. NBW5 - Turbidity high alarm. Checked site, well recently activated. Trending shows a pattern of turbidity spikes on well start. Will monitor site. | FLAG | stage1_keyword | 0.95 | Critical keyword match: fault [equipment_failure]; alarm [control_system] | fault [equipment_failure]; alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-09 | All Water System ROC General | ROC | NMTKKC - Sanitary pump fail to stop alarm, notified Jason G. He is on site. Contractor cut a power cable. No power on site. NMW12, NMW136, NMW15 Commfail alarm . Jason G requested all wells place man/off. TK at 73%, Jason G investigating on site, will call back. | FLAG | stage1_keyword | 0.95 | Critical keyword match: alarm [control_system] | alarm [control_system] |  | 1 | 0
2026-02 | 2026-02-24 | All Wastewater System ROC General | ROC | KBSP, Marcus R on site, testing the Filter Inlet Flood/Alum Leak-Flood alarm | FLAG | stage1_keyword | 0.95 | Critical keyword match: flood [critical]; alarm [control_system]; leak [infrastructure] | flood [critical]; alarm [control_system]; leak [infrastructure] |  | 1 | 0
2026-02 | 2026-02-28 | All Wastewater System ROC General | ROC | NBSP - Inlet channel Hi alarm, Mech Bar screen fail to stop and OOS alarms. All alarms cleared in a few minutes. Will monitor. | FLAG | stage1_keyword | 0.95 | Critical keyword match: oos [equipment_failure]; alarm [control_system]; alarms [control_system] | oos [equipment_failure]; alarm [control_system]; alarms [control_system] |  | 1 | 0

## Cleared Logs
source_month | EVENTDATE | DESCRIPTION | PERSONGROUP | LDTEXT | triage_decision | triage_stage | triage_score | triage_reason | matching_keywords | clf_proba | stage1_label | is_issue